## TechItemDoc
ItemCode | Item Name | UOM | Qty | Unit Price | Remarks
26 | 26G sheet | sq.m | 5
29 | 24G sheet | sq.m | 3.5
31 | Supplying fixing of opposed blade volume control dampers in supply air duct collars as per approved drawings and specifications. Volume control damper shall be provided at the junction of each branch duct with main duct. Dampers shall be 2 gauge heavier than the gauge of large duct but should not be less than 20 gauge, and shall be rigid in construction so as not to flutter with the passage of air. | SQMT | 1
47 | 12.7 mm OD soft copper (Insulation 13 mm) | RM | 1
48 | 15.9 mm OD soft copper (Insulation 19 mm) | RM | 1
49 | 19.1 mm OD hard copper (Insulation 19 mm) | RM | 22
50 | 22.2 mm OD hard copper (Insulation 19 mm) | RM | 51
54 | 32 mm dia | RM | 15
55 | 25 mm dia | RM | 10
57 | 2C x 1.5 mm2 (control wiring for IDU to ODU) | RM | 46
6 | SITC of conventional type microprocessor based Remote Annunciator panel of following zones for wall mounting type fabricated out of 16 SWG CRCA sheet steel incorporating audio visual indication for each zone without battery bank and battery charger . | Nos. | 2
8 | 2 x 1.5 sq mm | Mtr | 20
2 | 25 mm dia | Mtr. | 11
4 | 50 mm dia | Mtr. | 6
10 | Pendant type 68° C Temprature | Each | 1
1 | Supply, Installation, Testing, and Commissioning of Addressable Type (Optical Smoke ) Smoke Detector Conforming to EN54, with standard detector mounting base, IP30 Ingress Protection, Area Coverage of 50 sq. mm (subject to local standard), 360° Angle Visibility, Operating Temperature (-10°C to +50°C), approved by LPCB, of approved make along with suitable size 2 core cable clipped to structure/wall/ceiling / through GI or Heavy Duty PVC Conduits with suitable cable clips/saddles with all necessary mounting and fixing arrangements. (Above & Below Ceiling) Make Fire Alarm Devices: Johnson or as directed by the Airport. Make: PVC Conduits: Sudhakar, Shakti or equivalent | Nos | 10
2 | Supply, Installation, Testing, and Commissioning of Addressable Type Monitor Module along with suitable size 2 core cable clipped to structure/wall/ceiling / through GI or Heavy Duty PVC Conduits with suitable cable clips/saddles. Make Fire Alarm Devices: Johnson or as directed by the Airport. Make: PVC Conduits: Sudhakar, Shakti or equivalent | Nos | 2
3 | Supply, Installation, Testing, and Commissioning of Addressable Type control Module along with suitable size 2 core cable clipped to structure/wall/ceiling / through GI or Heavy Duty PVC Conduits with suitable cable clips/saddles. Make Fire Alarm Devices: Johnson or as directed by the Airport. Make: PVC Conduits: Sudhakar, Shakti or equivalent | Nos | 2
4 | Supply & Installation of Isolation Module | Nos | 1
5 | Supply, Installation, Testing & Commissioning of Flow Switch on Sprinkler distribution header pipe with a working pressure of 31 Bar (450 PSI) and a flow sensitivity range of 4-10 GPM (15 - 38 LPM) on each floor / zone / inside proposed demise area tap of point, shall be connected to fire alarm panel through cable. (Make: Potter/ System Sensor or equivalent with airport approval) 80mm dai | Nos | 1
6 | Supply & Installation of Drain Valve 25MM with fitting | Nos | 1
7 | Supply & Installation of Ball Valve 15MM for pressure gauge as per requirment | Nos | 1
8 | Supply & Installation of Pressure Guage 16kg as per site requirment | Nos | 1
10 | 300 mm width X 50 mm depth X 2 mm thickness | RM | 108
11 | Suplly and installtion of out door stand as per site condition 1000x500x700mm , with plat and fitting etc | nos | 1