## High Side CHW AHU
High Side CHW AHU BOQ
Sr. No. | Description | Unit | Qty | Rates | Amount
1.1 | Ceiling suspended Air Handling Unit - CHW Type
Supply of double skin ceiling suspended air handling units complete with 25mm thick insulated panels, Forward curved DIDW Blower, cooling coil section with 6 Row CHW coil, filter section with filters, fan motor, drive set, mounting base damper etc.as per below specifications: a. Chilled water temperature entering 7 deg C & exit 12 deg C b. Fan Outlet Velocity should not exceed 1800 FPM c. Coil face velocity should not exceed 500 FPM d. Filter velocity should not exceed 400 FPM
a | 3400 CFM, 8.5 TR (Pipe Connections at LHS from filter) | Nos. | 1 |  | 0
1.2 | Starter Panel
Supply of Direct online starters suitable for motors of Air handling units of below mentioned capacities (KW/HP).The starter shall comprise of all necessary power and control equipments including, Auto/manual selector switch, start/stop push button, LED indicators.
a | 2.25KW (3HP) | Nos. | 1 |  | 0
1.3 | Chilled Water pipe
Supply of chilled water pipes in MS class C with necessary clamps, vibration isolator and fittings such as bends, tees etc. but excluding valves, strainers, gauges etc. Adequately supported on rigid supports duly painted as per specification and as requirements
a | 40 mm dia. | Rmt | 13 |  | 0
1.4 | Chilled Water pipe Insulation
Supply of Providing and fixing insulation by applying adhesive as per specifications and drawings.
a | 40 mm dia. | Rmt | 13 |  | 0
2 | CHW AHU Valve Station package
Supply of following valve station for air handling Unit. It shall include following Item: 1. Ball Valve - 2 nos. 2. Y-Strainer - 2 nos. 3. PICV Valve - 2 nos. 4. Temperature gauge - 2 nos. 5. Pressure gauge - 2 nos. 6. Drain Valve - 2 nos.
a | 40 mm dia. | Lot | 1 |  | 0
3 | Electrostatic Air Cleaners
MAKE : RYDAIR
a | AIRFLOW : 2500 CFM (L)620 x (W)1243 x (H)540 | Nos. | 1 |  | 0
| Total |  |  |  | 0
| GST 28% |  |  |  | 0
| TOTAL AMOUNT |  |  |  | 0

## Low Side CHW AHU
Low Side CHW AHU BOQ
Sr. No. | Description | Unit | Qty | Rates | Amount
1.1 | Ceiling suspended Air Handling Unit - CHW Type
Installation, testing and comissioning of double skin ceiling suspended air handling units complete with 25mm thick insulated panels, Forward curved DIDW Blower, cooling coil section with 6 Row CHW coil, filter section with filters, fan motor, drive set, mounting base damper etc.as per below: a. Chilled water temperature entering 7 deg C & exit 12 deg C b. Fan Outlet Velocity should not exceed 1800 FPM c. Coil face velocity should not exceed 500 FPM d. Filter velocity should not exceed 400 FPM
a | 3400 CFM, 8.5 TR | Nos. | 1 |  | 0
1.2 | Starter Panel
Installation, testing and comissioning of Direct online starters suitable for motors of Air handling units of below mentioned capacities (KW/HP).The starter shall comprise of all necessary power and control equipments including, Auto/manual selector switch.
i | 2.25KW (3HP) | Nos. | 1 |  | 0
1.3 | Chilled Water pipe
Installation, testing and comissioning of chilled water pipes in MS class C with necessary clamps, vibration isolator and fittings such as bends, tees etc. but excluding valves, strainers, gauges etc. Adequately supported on rigid supports duly painted.
a | 40 mm dia. | Rmt | 13 |  | 0
1.4 | Chilled Water pipe Insulation
Installation, testing and comissioning of Providing and fixing insulation by applying adhesive as per specifications and drawings.
a | 40 mm dia. | Rmt | 13 |  | 0
2 | CHW AHU Unit Valve Station
Installation, testing and comissioning of following valve station for air handling Unit . It shall include following Item: 1. Ball Valve - 2 nos. 2. Y-Strainer - 2 nos. 3. PICV Valve - 2 nos. 4. Temperature gauge - 2 nos. 5. Pressure gauge - 2 nos. 6. Drain Valve - 2 nos. 7. Necessary Insulated copper Pipe - as per site condition
a | 40 mm dia. | Lot | 1 |  | 0
3 | Electrostatic Air Cleaners
Installation, testing and comissioning
a | AIRFLOW : 2500 CFM (L)620 x (W)1243 x (H)540 | Nos. | 1 |  | 0
| Total |  |  |  | 0
| GST 18% |  |  |  | 0
| TOTAL AMOUNT |  |  |  | 0

## Low Side BOQ
Low Side HVAC BOQ
Sr. No. | Description | Unit | Qty | Rates | Amount
1 | AIR DISTRIBUTION SYSTEM
1.1 | GI sheet metal rectangular duct
Supply, Fabrication, Installation, Testing & Commissioning of following gauges of ducting complete with splitters, neccessary supports, dampers, and turning vanes as per specification and HVAC layout. Aproved Makes: JINDAL, TATA, SAIL, Equivalent. All exposed ducts and supports shall be painting with 2 coats of primer & 2 coats of epoxy paint. (Make-JSW/ESSAR)
a | 24 gauge ducting - 0.63 mm thickness (Width upto - 750mm) | Sq. mt | 115 |  | 0
b | 22 gauge ducting - 0.80 mm thickness (Width 751 - 1500) | Sq. mt | 20 |  | 0
2 | Accoustic Insulation
| Accoustic lining of duct work with 25mm thick -32kg/m3 Density,Resin Bonded fibreglass Rigid Boards using shalikote primer hot bitumen and mechanically fastened Nuts & Washers,covered with RP tissue and 30 G aluminium perforated sheet as per specs. Makes : KIMMCO,OWEN'S CORNING, U P TWIGA. | Sq. mt | 18 |  | 0
3 | XLPE Insulation (Supply / Exhaust / Fresh Air Duct) :
Providing and fixing XLPE insulation by applying adhesive on ducts complete as per specifications and drawings. Make-SUPREME / PARAMOUNT. (Exhaust- out side insulation, Fresh air -outside insulation, Supply- Inside insulation, Supply-outside painted.)
a | 13 mm thick | Sq. mt | 134 |  | 0
4 | Thermal Exhaust Duct Insulation ( Only in BOH )
| Exhaust Air Duct insulation with 13mm thick heatlon insulation within store. No insulation for duct outside store. | Sq. mt |  |  | 0
5 | Thermal insulation- (Out side Building )
| Providing and fixing nitrial rubber by applying adhesive outside the ducts complete with 2 layer of UV paint and fiber glass cloth. (13mm thick) | Sq. mt |  |  | 0
4 | Continous / Linear Grilles
Extruded Aluminium Powder Coated Continous / Linear Grilles Of Required Airflow Angles (0/15/30/45 degree deflection: 1 or 2 way) with four side flanges as per requirements. (Make - AIRVISION/COSMOS)
a | 6" Width | Rmt | 12 |  | 0
b | 8" Width | Rmt | 3 |  | 0
5 | Supply Air Square Grille
Supply, installation of aluminium extruded white powder-coated supply air square grilles with four side flanges (0/22.5/45 degree deflection: 1 or 2 way), with aluminium powder coated, multiple flape type with dampers. (Kitchen Area)
a | Neck Size - 12" x 12" (Outer Size - 14" x 14") | Nos. | 6 |  | 0
6 | Return Air Square Grille
Return air square grills without damper shall be four side flanges with active sizes as given below.
a | Neck Size - 14" x 14" (Outer Size - 16" x 16") | Nos. | 6 |  | 0
7 | Canvass Connection
a | Installation of Double Canvass connection for all air outlet / inlet, Fire retardant type with GI flanges for Units. | Nos. | 3 |  | 0
8 | Volume Control Damper (make - Cosmos/ Caryaire/ Air Product)
| Supply & Installation of volume control damper made of 100x40x1.55mm thk galvanised steel frame & with opposed blades of 1.55mm galvanised sheet steel. | Sq. mt | 1 |  | 0
9 | Collar Damper (make - Cosmos/ Caryaire/ Air Product)
a | Supply & Installation of Collar Damper gear operated with vertical blades. | Sq.mt | 3 |  | 0
10 | Drain Piping
Supply, Installation, testing & commisioning of Drain Water piping work out of PVC / HDPE hard pipes with insulation Complete with T joints and bends
a | 32mm | Rmt | 5 |  | 0
11 | Electrical work for HVAC
| Supply and installation of all cabling, glanding, termination from starter panel to CSU. | Lot | 1 |  | 0
| TOTAL |  |  |  | 0
| GST 18% |  |  |  | 0
| TOTAL AMOUNT |  |  |  | 0