## BOQ
PROJECT : LUCKNOW STREET AT T3 , LUCKNOW AIRPORT
SUMMARY TO SCHEDULE OF PRICES - HVAC WORKS
PROJECT : LUCKNOW STREET AT T3 , LUCKNOW AIRPORT
SUMMARY TO SCHEDULE OF PRICES - HVAC WORKS
The prices are to be quoted in the below mentioned form and shall include the supply, installation, Testing and Commissioning at site of all the equipments, ancillary materials except where specified otherwise and all such items whatsoever which may be required to fulfill the intent and purpose as laid down in the drawings and specifications shall include all taxes and duties on a basis works contract.
S.No. | Description | Unit | Qty. | Rate(Rs.) | Amount(Rs.)
Part A | Airconditioning (Hi Side Works)
1 | Air Handling Units
Supply , Installation , testing & commissioning of Ceiling Suspended Type double skin air handling units of extruded aluminium section with 0.6 mm preplasticized/precoated GI sheet outside and 0.6 mm plain Galvanized sheet inside, minimum of 25 mm thick PUF insulation of 38KG/m3 , Plug Fans / DIDW Blower with TEFC motors, copper cooling coils with aluminium finned copper tubes with face velocity 500 . Filter section having 50 mm thick pre filters , IE3 motor suitable for 415 +10% volts,50 Hz, 3 phase AC supply,drain connections with 18G stainless steel drain pan and necessary vibration isolation arrangement to avoid any vibration etc. complete as per specifications and drawings. . Approval of AHU Technical Data by consultant prior to fabrication is required.
Design Parameters- 25 deg C -R.A.Temp, 55% RH, 8.0 deg C- CHW IN , Water Flow Rate- 2.0 GPM/ TR
1.1 | Ceiling Suspended Type
1.1.1 | 7650 CMH(4500 CFM)at 20 mm External Static Pressure, 6 RD Cooling Coil, Approx 12.0 TR, 1 x 2.25 KW Motor | Nos | 1 |  | 0
1.2 | Digital Heating/Cooling Thermostat for Air Handling Units | Nos. | 1 |  | 0
| Sub-Total Part-'A' Rs. |  |  |  | 0
Part B | Ventilation (Hi Side Works)
1 | Kitchen Scrubber (Dry Type)-With Fan Section
1.1 | Supply , Installation, Testing and Commissioning of Dry Type Scrubber each comprising of extract air intake section, electrostatic precipitation technology, dry type air cleaner to remove oil, smoke and fumes from exhaust air, as per the Specifications. Electrostatic section shall be made of 16 gauge galvanised sheet, high bake epoxy powder coated, washable type aluminium mesh filters, stainless steel spiked ionizers to create high voltage DC field, aluminum collector plates which should be alternatively charged positive and negative with large collecting area with 14" deep cell, to work as magnet for charged smoke and oil particles. Average efficiency of 90-95% in single pass as per ASHRAE test method. Electrostatic Precipitator should be able to charge particles from 0.01 micron to 10 microns through solid state power supply. Collector cell should be of permanent type and incorporate slide out facility for easy removal for cleaning. Power supplies shall be 100% solid state UL Listed, Module of capacity above 3000 CFM shall be equipped with Pulse width modulating (PWM)
The system should be fitted with interlock switch for safety . The system should allow connection to a fan section to achieve 500 FPM velocity across the air
Operating Voltage : 220V, 50 Hz
Ionizing Voltage : 12.5 to 13 KVDC
Collector Cell Voltage : 6 to 6.5 KVDC
Power Consumption : Not more than 50W per cell.
1.1.1 | Capacities :8000 CFM | Nos | 1 |  | 0
| Sub-Total Part-'B' Rs. |  |  |  | 0