## Low side work
PROJECT : KFC FOODCOURT AT T1 , MUMBAI
SUMMARY TO SCHEDULE OF PRICES (HVAC SYSTEM) R0
Amount(Rs.)
Part B | DX Equipments (Low Side Works) |  |  |  | 17000
Part D | Low Side Works |  |  |  | 499650
Part E | Electrical Works |  |  |  | 70700
| Grand Total |  |  |  | 587350
PROJECT : KFC FOODCOURT AT T1 , MUMBAI
SUMMARY TO SCHEDULE OF PRICES (HVAC SYSTEM) R0
1 | DX and Ventilation System
S.No. | Description | Unit | Qty | Rate | Amount
Part B | DX EQUIPMENTS (Low Side Works)
1 | Air Cooled Split units (R32)(Inverter Type)
1.1 | Installation . Testing and commissioning of Air Cooled Split airconditioners each comprising an outdoor unit consisting of hermetic scroll compressor, air cooled condensing unit, Condenser fan etc. with outer casing and indoor fan coil unit(s) consisting of centrifugal fans, fan motor, DX cooling coil, outer casing, filter, control and power panel with remote control etc. both inter connected with copper refrigerant pipe and drain pipe of required length as given, cabling and wiring, insulation with cross linked polyethelene foam, full charge of refrigerant gas and oil, M.S. base frame, supports etc. complete as per specifications and drawings.
A | HI WALL TYPE
1.1.1 | 1.5 TR | Nos | 1 | 2000 | 2000
B | DUCTABLE TYPE
1.1.2 | 11.0 TR | Nos | 1 | 15000 | 15000
| Sub-Total Part-'B' Rs. |  |  |  | 17000
PART-D : | LOW SIDE WORKS
1 | Piping
1.1 | Refrigerant Piping
1.1.1 | Refrigerant Piping (DX System)(R32 Refrigerant)
Providing and fixing copper piping with nitreal rubber with chaseling as per specifications and drawings.
a. | 1.5 TR Machine (Liquid Line + Gas Line) | Mtrs. | 15 | 1050 | 15750
b. | 11.0 TR Machine (Liquid Line + Gas Line) | Mtrs. | 10 | 1450 | 14500
(Note : 1RM is equal to 1 RM of gas line and 1 RM of liquid line)
1.2 | Drain Piping
1.2.1 | 32 mm PVC Pipe with 9 mm insulation | RM | 5 | 175 | 875
1.2.3 | 20 mm PVC Pipe with 9 mm insulation | RM | 5 | 160 | 800
2 | Ducting
2.1 | Factory Fabricated Ducting (GSS)
Supply, installation, balancing and commissioning of factory fabricated GSS sheet metal rectangular/round ducting complete with neoprene rubber gaskets, elbows, splitter dampers, vanes, hangers, supports etc. as per approved drawings and specifications of following sheet thickness complete as required.
2.1.1 | 0.63 MM (24 Gauge) | Sqm. | 100 | 1450 | 145000
2.1.2 | 0.8 MM (22 Gauge) | Sqm. | 10 | 1850 | 18500
2.1.3 | 1.00 MM (20 Gauge) | Sqm. | 10 | 2200 | 22000
2.2 | Site Fabricated Ducting (GSS)
Supply, installation, balancing and commissioning of fabricated at site GSS sheet metal rectangular/round ducting complete with neoprene rubber gaskets, elbows, splitter dampers, vanes, hangers, supports etc. as per approved drawings and specifications of following sheet thickness complete as required.
2.2.1 | 0.63 MM (24 Gauge) | Sqm. | 10 | 1450 | 14500
2.2.2 | 0.8 MM (22 Gauge) | Sqm. | 5 | 1850 | 9250
3 | Insulation/ Accoustic Lining
3.1 | Duct Acoustic Lining
Supplying and Application of Acoustic lining within the Supply Air duct with 15 mm thick class 'O' open cell nitrile Rubber of density 140-160 kg./Cubm. as per spefications.
3.1.1 | 15 MM thick | Sqm | 15 | 950 | 14250
3.2 | Nitrile Rubber Insulation- Class 'O'
Supplying and fixing of closed cell elastomeric insulation of density 55 kg/cu.m.and K valueof not less than 0.037W/mk at 20 deg C as per specifications and drawings (For indoor applications) with factory Laminated 7 mill woven glass cloth
3.2.2 | 13 MM Thick (Supply Air & Fresh Air Duct) | Sqm | 80 | 1350 | 108000
3.2.3 | 19 mm Thick (Exhaust Duct) | Sqm | 35 | 1650 | 57750
4 | Grilles / Diffusers/ Dampers / Louvers
4.1 | Supply, Installation, Testing and Commissioning of GI multiblade volume control duct damper complete with neoprene rubber gaskets, nuts, bolts, screws linkages, flanges etc., as per specifications. | Sqm. | 1 | 8250 | 8250
4.2 | Supply, Installation, Testing and Commissioning of multiblade Al volume control Collar / Grille / exhaust Air Opening damper complete with suitable links, lever and quadrants for manual control of airflow and with suitable links , lever and quadrants for manual control of airflow and neoprene rubber gaskets, nuts, bolts, screws, flanges etc., as per specifications. | Sqm. | 0.5 | 8250 | 4125
4.3 | Supply, Installation, Testing and Commissioning & fixing of powder coated extruded aluminium Supply / Exhaust Air Grills as per specifications | Sqm. | 1 | 8850 | 8850
4.4 | Supply, Installation, Testing and Commissioning & fixing of powder coated extruded Aluminium Continuous Grille as per specifications
4.4.1 | 200 MM Aluminium Continuos Grille | RM | 5 | 1400 | 7000
4.4.2 | 150 MM Aluminium Continuos Grille | RM | 25 | 1250 | 31250
4.4.3 | 100 MM Aluminium Continuos Grille | RM | 10 | 1050 | 10500
4.5 | Providing and fixing of powder coated extruded aluminium exhaust air louvers/ fresh air louvers with bird screen and mounting arrangement as per specification and drawings. Free Area shall be more than 60% of gross area.
4.5.1 | Fresh Air / Exhaust Air Louvers with Bird Screen Mesh | Sqm. | 1 | 8500 | 8500
| Sub-Total Part E Rs. |  |  |  | 499650
Part F | ELECTRICAL WORKS
Electrical Work
1 | Electrical Control Panel
Supply, installation, testing and commissioning of panel boards made of 2.0 mm thick steel sheet duly powder coated with voltmeter, ammeter, electronic energy meter, indicating lights, Stop/manual /Auto selector switch in each, outgoing current operated single phase preventer. The starters should have potential free contacts for connection to Building Automation System. The panel shall include contactors /over load relay with built in single phase protection / Time delay relay for delayed automatic start of the motor. All panels should have spare NO/ NC Contacts for BMS applications as required.
1.1 | Panel-PA10
| (1 x 2.25 KW + 1 X 3.75 KW) | Nos | 1 | 22500 | 22500
INCOMER
-- | 1 No. incoming 40 Amps TP MCB
-- | 1 No. Digital Type voltmeter with selector switch with control MCB
-- | 1 No. Digital Type Ammeter 0-63 A with C.T.'s
-- | 1 Set of RYB indication lamps with control MCB
-- | 1 No. of 63 Amps Aluminium conductor 25kA bus bar duly sleeved as required.
OUTGOING
2 No. 16 Amps TP MCB for AHU's
1 No. DOL starter for 2.25 KW motor .
1 No. DOL starter for 3.75 KW motor .
2 Nos. of single phase preventor (current based-MPRD2)
2 Nos. direct reading Digital Type Ammeter
| Each star-delta/DOL starter consists of current operated MN type over load relay, contactor, push button, ON/OFF indication light | Set | 1 | 12600 | 12600
2 | Control & Transmission Wiring
2.1 | Providing & fixing control cum transmission wiring of 2 core x 1.5 sqmm copper in MS conduits between indoor and out door unit and between indoor units and their remote sensor/controller. | RM | 25 | 350 | 8750
3 | Power Cabling
3.1 | Indoor Units
3.1.1 | Providing and fixing flexible power cable of 3 core x 1.5 sqmm copper between Indoor units and their power points | RM | 5 | 145 | 725
3.1.2 | Providing and fixing flexible power cable of 3 core x 2.5 sqmm copper between Indoor units and their power points | RM | 5 | 145 | 725
5 | Cables
Supplying and laying of XLPE insulated aluminium conductor armored cables of 1.1 KV grade of following sizes directly on wall/structural frame/ cable trays or racks using approved type of clamps,End terminations with Double Compression type glands on both ends, double earthing with GI strip/wire of suitable size and hardware as per specifications.
5.1 | 3 C x 4 Sq. mm | RM | 40 | 335 | 13400
7 | Earthing
Supply,Installation, Testing and Commissioning of the following earthing clamped to wall with suitable clamps saddles and fixing bolts/ in ground including the cost of digging and back filling as required and complete as required to comply with IS 3043:1987. All copper joints shall be tinned. The rates shall be inclusive of making test joints where ever required
7.1 | 25 mm x 6 mm GI strip | RM | 10 | 650 | 6500
7.2 | 8 SWG GI Wire | RM | 10 | 550 | 5500
| Sub-Total Part F Rs. |  |  |  | 70700