## HVAC BOQ
NAME OF PROJECT: Bar Lounge at UNA
HVAC WORK
S.NO. | ITEM DESCRIPTION | UNIT | QTY. | RATE | AMOUNT
A | HIGH SIDE WORK-EQUIPMENTS HEAD -1
1 | Ductable Split unit
Supply, installation, testing and commissioning of CONCEALED Duct type units with Scroll compressor with green Regrigerant R-410A/R-32. The unit should be complete with indoor & outdoor unit, condensing unit, controls, control panel, tubular type refrigerant, canvas connection remote control and drain piping. The refrigerant piping, control wiring should be based on the indoor unit and outdoor unit distance being 3 mtrs/Ckt along with 13 mm thk nitrile rubber insulation. The insulated drain piping should be of 32 mm dia. and distance 3 mtrs/unit. Indoor unit should be provided with thermostats and remote control. The installation should be complete with all the required accessories like the supports, clamps required to make the installation complete. The cost should also include Chasing in walls as well as all the supports needed to install the units at the higher level.
The quoted price shall include the GI frame structure to mount the outdoor unit or to suit the site condition.
1.1 | 11 TR ( 4400 cfm) HSP split air conditioning units as described above | No. | 2
2 | 'Supply, Installation, Testing and Commissioning of split type 4 way cassette airconditioning units, each comprising of an outdoor and a single indoor unit. Condensing unit shall be complete with hermatically sealed scroll compressor/s, with aluminium fins, thermostatic expansion valve and air cooled condenser with fan. Evaporating unit shall suitable as per site requirement with swing louvers and adjustable blades from sides. Indoor Units complete with in-built drainage arrangements, fan, refrigerant liquid and refrigerant piping, cordless remote control, and fresh air port etc . The outdoor unit enclosure shall be factory painted to a smooth finish. The quoted price shall be inclusive of Anti Corrosion Treatment for remote aircooled condensers, full refrigerant charge, vibration isolation arrangement, associated electrical work and MS base frame duly painted with black enamel paint for mounting of condensing units.
2.1 | 3 TR nominal capacity split unit with scroll compressor and single Cassette type indoor unit. | Nos. | 1
3 | Supplying, installing, testing and commissioning of INLINE FANS suitable for installing in any position in vertical or horizontal ducts. The casing shall be double skin, internally acoustically lined and constructed of galvanised steel. The fan shall be DIDW with forward curve impeller fitted with maintenance free external rotor motor. The motor shall be suitable for 220±10% volt single phase 50 cycles AC supply. All units shall be complete with duct flexible connector and volume control damper and static pressure or to suit the system, shall be as follows:
3.1 | Capacity: 100-200 CFM Static Pressure: 15 mmwg | No. | 1
B | LOW SIDE WORK -PIPING-COPPER AND DRAIN HEAD-2
1 | Providing & fixing of inter connecting copper piping between indoor & outdoor units as per manufacturer specifications duly insulated with closed cell nitrile foam tabular insulation of 13mm thickness. All piping inside the room shall be properly supported with hanger in M.S. painted cable tray and exposed piping shall be properly supported in G.I. cable tray with top cover
1.1 | 6.4 mm OD soft copper (Insulation 13 mm) | RM | 1
1.2 | 9.5 mm OD soft copper (Insulation 13 mm) | RM | 10
1.3 | 12.7 mm OD soft copper (Insulation 13 mm) | RM | 1
1.4 | 15.9 mm OD soft copper (Insulation 13 mm) | RM | 50
1.5 | 28.6 mm OD soft copper (Insulation 13 mm) | RM | 45
2 | Fabricating and installing following size of perforated G.I cable trays to run the insulated refreigerant pipes (directly exposed to ambient) & electrical power & control cables (directly exposed to ambient) including horizontal and vertical bends, reducers, tees, cross members & other accessories as required and duly supported from the floor as required.
2.1 | 150 mm width X 50 mm depth X 2 mm thickness | RM | 15
3 | Supplying, installing and testing of UPVC pipe ( heavy duty) with 6 mm thick nitrile rubber insulation with protective coating on condensing water piping and fitting like bends, elbow, tee and union, etc. as per the approved shop drawings and specifications.
3.1 | 32 mm Dia | Rmt | 20
3.2 | 25mm Dia | Rmt | 1
4 | Civil works associated with refrigerant piping & condensate drain piping.
4.1 | Cutting and chasing of walls/ floor and making asthetically good appearance & finishes. | RM | 5
C | AIR DISTRIBUTION
(FOR FACTORY FABRICATED DUCTS AS PER “SMACNA” STANDARDS & SPECIFICTIONS)
1 | Supply, Fabrication, installation and testing of factory fabricated sheet metal ducts with sleeve joints and supports complete with the approved shop drawings and as required by the specifications and hanging of the ducts to be done by thread wire on metal cushion with gripple support.
| 24G sheet | sq.m | 80
| 26G sheet | sq.m | 80
2 | Supplying and erecting GI sheet of fabricated at site and mentioned guage to be used for fabrication of ducting complete with neoprene rubber garkets, elbows, splitter dampers, vanes, hangers, supports etc. as per approved drawings and specifications of following sheet thickness complete as required:
| 22G sheet | sq.m | 5
| 24G sheet | sq.m | 5
3 | Supply, installation, testing and balancing of powder coated Extruded Aluminium Supply air Grilles with volume control dampers in accordance with the approved shop drawings and specifications. (Minimum Chargable area would be 0.1 Sqm Per Pc) | SQMT | 3
4 | Supplying & fixing of opposed blade volume control dampers in supply air duct collars as per approved drawings and specifications. Volume control damper shall be provided at the junction of each branch duct with main duct. Dampers shall be 2 gauge heavier than the gauge of large duct but should not be less than 20 gauge, and shall be rigid in construction so as not to flutter with the passage of air. | SQMT | 0.2
5 | Supply, fabrication, installation and testing the flexible connections constructed of fire resistance flexible double canvas sleeve as per the approved shop drawings. | Nos. | 3
6 | Supply, installation, testing and balancing of Powder coated/Anodised extruded aluminium construction exhaust air louvers with bird screen for exhaust air as per specifications and approved shop drawings. (Minimum Chargable area would be 0.1 Sqm Per Pc) | SQMT | 0.1
7 | Supply, installation, testing and balancing of Powder coated/Anodised extruded aluminium construction. inlet air louvers with bird screen and volume damper for fresh air as per specifications and approved shop drawings. | SQMT | 0.2
8 | Supply, installation, testing and balancing of powder coated Extruded Aluminium exhaust air Grilles with volume control dampers in accordance with the approved shop drawings and specifications. (Minimum Chargable area would be 0.1 Sqm Per Pc) | SQMT | 0.2
D | THERMAL INSULATION
1 | Supply, installation and testing of Acoustic lining with Open cell nitrile rubber with in supply and return air ducts of specified thickness as per the specifications. All ducts shown cross hatched on the approved shop drawings shall be provided with acoustic lining as perthe specifications:
| 15 mm thick | sq.m | 10
2 | Supplying and fixing of following thickness duly laminated aluminum foil of mat finish closed cell Nitrile rubber(Class“O”) insulation on existing duct after applying suitable adhesive for Nitrile rubber. The joints shall be sealed with 50mm wide and 3mm thick self adhesive nitrile rubber tape insulation complete as per specifications and as required.
2.1 | 13 mm thick | sq.m | 160
E | ELECTRICAL INSTALLATION
2 | Supply, laying, testing and commissioning of PVC sheathed stranded FRLS wires in MS conduits recessed / surface including cutting, chesing the wall surface and making for the same, sizes as given below of copper conductor including terminations complete as required.
a) | 2C x 1.5 mm2 (control wiring for IDU to ODU) | RM | 60
C | Details of Materials / Equipment/Manufacturer’s Name
1 | Air Distribution Ducting (Site Febricated) | Sail / Nippon / OR Equivalent Approved
2 | Grilles / Diffusers / Jet Nozzles | Ravistar / Cosmos / Carryaire/ Airflow /Tristar/ Mapro Eq Approved
3 | Aero-Foil Dampers | Carryaire / Ravistar OR Equivalent Approved
4 | Fresh Air Louvers/Assembly | Ravistar/ OR Equivalent Approved
5 | Smoke / Fire Damper | Cosmos /Air Master / Caryaire / Dynacraft / Air Product / Ravistar/Tristar
6 | Flexible Duct Connectors | Klimatech,
7 | Anchor Fastener | Hilti
8 | UPVC Drain Piping | Prince / Supreme
9 | Filters | Dyna / Thermadyne / Spectrum / AAF OR Equivalent Approved
10 | Cushy Foot Mounts | Resistoflex/ OR Equivalent Approved
11 | Duct Thermal & Acoustic Insulation | Thermobreak / Supreme/ ARMACELL
12 | Closed Cell Nitrile Rubber along with adhesive | Armaflex / K-flex/ ARMACELL
13 | Motors | Siemens / HAVELL/ ABB / Bharat Bijlee / Marathon
14 | Cables | Polycab / Finolex / Hawells
15 | Switchgears- MCB’s, MCCB’s etc. | Legrand / Indo-Asian / Siemens
16 | Factory Made Duct | Alpha duct / Rollastar / Zeco / Nutech
17 | Split unit | Toshiba / Bluestar / Daikin / Samsung / Mitsubishi/LG/Hitachi /Voltas
18 | Cushy Foot Mounts | Resistoflex/ OR Equivalent Approved
19 | Inline Fans | AIRFLOW/HUMIDIN/ Carryair/ Kruger / System Air / Sphire Eq Approved
20 | Copper Pipes | Maxflow / Yorkshire / Rajco / Mehta tubes
21 | Copper Pipe fittings | Conex Banninger/ NIBCO
22 | Copper Pipe Insulation | Thermobreak / Supreme

## MAKE LIST
NAME OF PROJECT: Bar Lounge at Uba
HVAC APPROVED MAKES LIST
Sr. No. | Details of Materials / Equipment | Manufacturer’s Name
1 | Air Distribution Ducting (Site Febricated) | Sail / Nippon / OR Equivalent Approved
2 | Grilles / Diffusers / Jet Nozzles | Ravistar / Cosmos / Carryaire/ Airflow /Tristar/ Mapro Eq Approved
3 | Aero-Foil Dampers | Carryaire / Ravistar OR Equivalent Approved
4 | Fresh Air Louvers/Assembly | Ravistar/ OR Equivalent Approved
5 | Smoke / Fire Damper | Cosmos /Air Master / Caryaire / Dynacraft / Air Product / Ravistar/Tristar
6 | Flexible Duct Connectors | Klimatech,
7 | Anchor Fastener | Hilti
8 | UPVC Drain Piping | Prince / Supreme
9 | Filters | Dyna / Thermadyne / Spectrum / AAF OR Equivalent Approved
10 | Cushy Foot Mounts | Resistoflex/ OR Equivalent Approved
11 | Duct Thermal & Acoustic Insulation | Thermobreak / Supreme/ ARMACELL
12 | Closed Cell Nitrile Rubber along with adhesive | Armaflex / K-flex/ ARMACELL
13 | Motors | Siemens / HAVELL/ ABB / Bharat Bijlee / Marathon
14 | Cables | Polycab / Finolex / Hawells
15 | Switchgears- MCB’s, MCCB’s etc. | Legrand / Indo-Asian / Siemens
16 | Factory Made Duct | Alpha duct / Rollastar / Zeco / Nutech
17 | Split unit | Toshiba / Bluestar / Daikin / Samsung / Mitsubishi/LG/Hitachi /Voltas
18 | Cushy Foot Mounts | Resistoflex/ OR Equivalent Approved
19 | Inline Fans | AIRFLOW/HUMIDIN/ Carryair/ Kruger / System Air / Sphire Eq Approved
20 | Copper Pipes | Maxflow / Yorkshire / Rajco / Mehta tubes
21 | Copper Pipe fittings | Conex Banninger/ NIBCO
22 | Copper Pipe Insulation | Thermobreak / Supreme