## PHE BOQ
Bangalore International Airport Limited
DOC NO. :B00B01-TFS-D_GN-DOM-02-PH-II- PHE BOQ-0001
DOMESTIC LOUNGE-PHASE-II-PHE BOQ |  |  |  | Rev: | R1
|  |  |  | Date: | 22.06.2024 |  | RS comments 10/6/24 | Meptek Reply
Item No. | Description | Unit | Qty. | Rate | Amount | Make
A | WATER SUPPLY PIPING
[7 empty] | Approved make to be specified for all items | Specified as required
1 | Providing & fixing PPR-C ( 3 layer pipes-SDR-7.4) confirming to DIN 8078, 8077 - for Domestic, RO, flushing and Hot water, including cutting the pipes to correct length, Fusion welded jointing as per manufacturer, fixing with ms clamps, including necessary fitings like elbows ,tees,unions reducers,coupling, pipe nipples etc.complete, with testing, painting.The work shall also include chasing the walls with machine wherever required for concealed piping/require sleeve in walls and making good of chased surface (Pipe shall be tested with 1.5 times working pressure as covered in specifications) |  |  |  |  | Astral / Ashirwad /supreme / Prince or Approved Equivalent
1.1 | 20 mm Dia | R.mt | 20
1.2 | 25 mm Dia | R.mt | 150
1.3 | 32mm Dia | R.mt | 60
1.4 | 40mm Dia | R.mt | 20
1.5 | 50mm Dia | R.mt | 0
2 | Providing & fixing HDPE-PE-100-PN-10 ABOVE 50MM DIA- for Domestic, RO, flushing and Hot water, including cutting the pipes to correct length, Fusion welded jointing as per manufacturer, fixing with ms clamps, including necessary fitings like elbows ,tees,unions reducers,coupling, pipe nipples etc.complete, with testing, painting.The work shall also include chasing the walls with machine wherever required for concealed piping/require sleeve in walls and making good of chased surface (Pipe shall be tested with 1.5 times working pressure as covered in specifications) |  |  |  |  | Astral / Ashirwad or Approved Equivalent
2.1 | 65mm Dia | R.mt | 0
2.2 | 75mm Dia | R.mt | 0
3 | Providing & Fixing of gun metal heavy Ball Valves (approved makes as covered in specification) screwed type for water system of the following diameters(15Kg/Sq.cm). Valve shall have with unions. |  |  |  |  | Leader / Neta / Zolotto / or approved Equivalent
3.1 | 20mm Dia | Nos. | 8
3.2 | 25mm Dia | Nos. | 2
3.3 | 32mm Dia | Nos. | 2
3.4 | 40mm Dia | Nos. | 2
3.5 | 50mm Dia | Nos. | 0
4 | Providing ,fixing, testing and commissioning Electromagnetic flow meter-flow (30 GPM-1.89 LPS) including providing & fixing matching with required accessories 16Kgs/Sq.cm). - Contractor to check existing make in BIAL airport and provide that. |  |  |  |  | Krone or equivalent | KRONE or equivalent. Please note that the lead time is 8weeks
4.1 | 25 mm Dia incoming line | Nos. | 0
4.2 | 32 mm Dia incoming line | Nos. | 1
4.3 | 40 mm Dia incoming line | Nos. | 4
4.4 | 50 mm Dia incoming line | Nos. | 0
5 | Supply, installation,testing & commissioning of Storage Type Electric Hot Water Generator of mentioned capacity, suitable for 3 KG/cm2 pressure, Wall Mounted / Floor standing type, with Auto Shut-off Thermostat, along with isoltion Valves, Air Release valve, SS flexible connections andall other std accessories ( Prior to proceed check with client for instant geyser requirement if any) |  |  |  |  | AO Smith/Racold / Venus / Usha / or Approved Equivalent
4.1 | 10 L Capacity | Nos. | 0
4.2 | 20 L Capacity | Nos. | 2
4.3 | 30 L Capacity | Nos. | 0
A | SUB TOTAL OF A
B | RO PLANT-PRIOR TO PROCEED LOCATION TO BE FINALISED |  |  |  |  | Iron Exchange or Approved Equivalent | Please check the location. This is very very critical.
1 | Supply , installations, testing and comminissioning of Package RO plant 200 Lit/Hr including required internal pumps , all assesories, valves and membrance cleaning system, ultra-violet sterilizer, internal piping within the whole pacakge suitable to connect the inlet and outlet to plumbing contractor work including presure gages etc. | Nos | 2 |  |  | Iron Exchange or Approved Equivalent
2 | Sintex storage tank -300 lit (RO water) | Nos | 2 |  |  | Sintex or Approved Equivalent
3 | Horizntal, pressure booster pumps with motors mounted on a single base frame, complete with all accessories, suction/discharge butterfly valves, suction strainers, discharge non-return valves, pressure gauges and of the following capacities |  |  |  |  | Grundfos/ Kirlosker or Approved Equivalent
| a)For RO water supply | Nos | 4
| 50 lpm @ 2.0 kg/cm2 discharge pressure. |  | (2W+2S)
SUB TOTAL OF B
C | DRAINAGE
1 | Providing & Fixing spun C.I.hubless Pipes as per IS 3989 / 1729 (As perISO 6594/As per IS 15905) to correct grade length and alignment including cutting pipes to correct lengths joining as specified by manufacturere including required h M.S.brackets, clamps, testing, painting the pipes with three coats of bitumatic paint complete as per specifications for the following diameters including fittings such as tees. bends, single junction, double junction etc. |  |  |  |  | NECO Centri/LANCO Kalahasti / Kejriwal / or Approved Equivalent
1.1 | 75mm Dia | R.mt | 30
1.2 | 100 mm Dia | R.mt | 65
1.3 | 150 mm Dia | R.mt | RO
2 | UPVC Type B pipe confirming to IS 13592 (6 Kg/CM2) for Soil, Waste upto 65mm dia. confirming to IS 13592 in correct grade,length & alingment in Solvent Cement joints including cutting the pipes to correct length, jointing with solvent cement joints,fixing with M.S heavy brackets/clamps testing, including cutting holes in R.C.C walls/floors making good the same etc all complete including plain fittings such as bends, tees etc. of the following diameters ( basin /Sink to FT & in toilet internal) |  |  |  |  | supreme / Prince or Approved Equivalent
1.1 | 40mm Dia | R.mt | 50
1.2 | 50mm Dia | R.mt | 40
1.3 | 65mm Dia | R.mt | 15
1.4 | 75mm Dia | R.mt | 20
3 | Supply, Install PVAC multiTraps including fixing with lead caulked joints and rings, c/w Circular SS 304 Grating, ( in bar and live kitchen) | Nos. | 6
4 | Supply, Install CI multiTraps including fixing with lead caulked joints and rings, c/w Circular SS 304 Grating, ( Subject to site requirement) | Nos. | 8
5 | Supply, Install CI floor Traps including fixing with lead caulked joints and rings, c/w Circular SS 304 Grating, | Nos. | 6
6 | Supply, Install CI urinal Traps including fixing with necessary consumables with Circular SS Grating with anti cockroach jali Suitable for 75mm Dia outlet | Nos. | 1
7 | Supply, Install PVC P-Traps including required accessories | Nos. | 0
8 | Supply, Install CI custom made clean out plungs with brass cap including fixing with necessary consumables.(Optional if required at site) | [5 empty] | Custom made brass plug must required. | Considered
8.1 | 40mm Dia | Nos. | 0
8.2 | 75 mm Dia | Nos. | 2
8.3 | 100 mm Dia | Nos. | 5 |  |  |  | Qty missing | Added
8.4 | 150 mm Dia | Nos. | 0
9 | Supply, Install GREASE TRAP-MODEL LIPUMOBIL-S | Nos. | 2 |  |  |  | BIAL will ask Grease trap for Bar area sinks. Capacity to be mentioned. | Considered.Data Sheet attached
10 | Only Installation of S.S. grating of 300x300mm shown in the layout (Note- supply of SS gratings will be by kitchen consultant or TFS) | Nos. | 1 |  |  |  | TFS supply. To be added in Kitchen equipment. | Added note
11 | Only Installation of S.S. grating of 900x600mm shown in the layout (Note- supply of SS gratings will be by kitchen consultant or TFS) | Nos. | 0 |  |  |  | TFS supply. To be added in Kitchen equipment. | Added note
12 | Only Installation of S.S. grating of 900x300mm shown in the layout (Note- supply of SS gratings will be by kitchen consultant or TFS) | Nos. | 0 |  |  |  | TFS supply. To be added in Kitchen equipment. | Added note
SUB TOTAL OF C
D | CORE CUTS
1 | Providing core cuts as per following size with backfilling/water proofing/core cuts to be sealed as required standared/as required by project manager
1.1 | 75mm Dia | Nos. | 0
1.2 | 100 mm Dia | Nos. | 0
1.3 | 150 mm Dia | Nos. | 4 |  |  |  | Put some qty | Added
D | CORE CUTS
E | SANITARY AND C. P. FITTINGS & FIXTURES
Only installation, testing and commissioning of sanitary and C.P. fittings
1.1 | EWC with seat cover | Nos | 10
1.2 | Concealed flush tank | Nos | 10
1.3 | Concealed flush valve | Nos | 0
1.4 | Health Faucet | Nos | 10
1.5 | 2 Way Bib-Cock with connection for Health Faucet | Nos | 10
1.6 | Bided | Nos | 0
1.7 | Under Counter Wash Basin including waste Coupling | Nos | 11
1.8 | Wash Basin Cock | Nos | 11
1.9 | shower and mixer | Nos | 0
1.1 | Bath Tub including waste Coupling and nessessary connections | No | 0
1.11 | Under Counter Sink including waste Coupling | Nos | 3
1.12 | Sink Pillar Cock | Nos | 3
1.13 | Bottle Trap for WHB/ sink and urinal with all connecting pipes | Nos | 18
1.14 | Angle Cock with PVC pipe connection upto WHB/sink/Geyser connection | Nos | 29
1.15 | Urinal | Nos | 4
1.16 | Auto Flush Valve & Sensor with connecting piping & spreader for urinal(DC) | Nos | 4
1.17 | Soap Dispenser | Nos | 11
1.18 | Paper Holder | Nos | 10
1.19 | Towel Ring | Nos | 0
1.2 | Rain shower ( optional) | Nos | 0
1.21 | hand shower ( optional) | Nos | 0
1.22 | Diverter with thermostate ( optional) | Nos | 0 |  |  |  | what about Handy cap toilet fixtures? | Considered in overall qty as only installation is part of the work. Supply will be by Client.
SUB TOTAL -D-SANITARY AND C. P. FITTINGS & FIXTURES ( ONLY INSTALLATIONS)
GRAND - TOTAL A , B, C, D AND E
NOTES :
1. Taxes and duties shall be Extra as actual
2. Supply and installation of Sanitary fixtures and fitting in th kitchen and toilets
3. Supply of S.S. gratings in kitchen

## General Notes
Bangalore International Airport Limited
DOC NO. :B00B01-TFS-D_GN-DOM-02-PHASE-II-PHE BOQ-0001
DOMESTIC LOUNGE-PHE BOQ
BIAL INTERNATIONAL LOUNGE-PHE PRICED BOQ-KITCHEN , BAR & TOILETS
GENERAL NOTES
1 | The items given in this schedule are provisional. The Contractor shall be paid for the actual quantity of work executed as measured at the site at the rates tendered. The Owner reserves the right to increase or decrease any of the quantities, or to ommit totally any item of work. Any claim by the Contractor on these accounts will not be entertained.
2 | All the items of work given in this schedule of quantities shall be executed strictly in accordance with the latest Indian Standard Specifications.
3 | The Contractor shall visit the site and shall satisfy himself as to the conditions under which the work is to be performed. He shall also check and ascertain the location of any existing structure or equipment or any other situation which may affect the work. No extra claim as a consequence of ignorance or on ground of insufficient description will be allowed at a later date.
4 | All equipment and material shall be IS approved.
5 | All approvals shall be obtained from Owner / Consultant
6 | All equipment and material shall be inspected at manufacturer’s works as per relevant IS by the Owner or his representative before despatch to site.
7 | All vendor drawings shall be approved by the Owner/Consultant before fabrication work starts.
8 | All Testing and Commissioning shall be as per relevant details covered in the specifications. All these testing records are to be maintained and submitted for Owner / Owner’s representative.
9 | All items of work under this Contract shall be executed strictly to fulfill the requirements laid down under “Basis of Design” in the specifications. Type of equipment, material specification, methods of installation and testing and type of control shall be in accordance with the specifications, approved shop drawings and the relevant Indian Standards, however capacity of each component and their quantities shall be such as to fulfill the above mentioned requirement.
10 | The unit rate for all equipment or materials shall include cost in INDIAN RUPEES (INR) for equipment and materials including all taxes and duties and also including forwarding, freight, insurance and transport into Contractor’s store at site, storage, installation, testing, balancing, commissioning and other works required.
11 | The rate for each item of work included in the Schedule of Quantities shall, unless expressly stated otherwise, include cost of :
a | All materials, fixing materials, accessories, appliances tools, plants, equipment, transport, labour and incidentals required in preparation for and in the full and entire execution, testing, balancing, commissioning and completion of work called for in the item and as per Specifications and Drawings.
b | Wastage on materials and labour.
c | Loading, transporting, unloading, handling/double handling, hoisting to all levels, setting, fitting and fixing in position, protecting, disposal of debris and all other labour necessary in and for the full and entire execution and for the job in accordance with the contract documents, good practice and recognize principles.
d | Liabilities, obligations and risks arising out of Conditions of Contract.
e | All requirements of Specifications, whether such requirements are mentioned in the item or not. The Specifications and Drawings where available, are to be read as complimentary to and part of the Schedule of Quantities and any work called for in one shall be taken as required for all.
f | BOQ shall be read in conjuction with technical specification, drawings,In the event of conflict between Bill of Quantities and other documents including the Specifications and drawings, the most stringent shall apply. The interpretation of the Consultant/Project Manager shall be final and binding.
12 | The Contractor shall procure and bring Materials/Equipment to the site only on the basis of drawings approved for construction and shop drawings and not on the basis of Bill of Quantities which are approximate only. This also applies to the Contractor’s requisition for Owner supplied materials.
13 | The contractor shall cooperate with all trades and agencies working on the site. He shall make provision for hangers, sleeves, structural openings and other requirements well in advance to prevent hold up of progress of the construction schedule. All supports to the civil structure shall be provided with anchor fasteners.
14 | On award of the work, contractor shall submit a schedule of construction in the form i.e BAR chart for approval of the Project Manager.
15 | On award of the work the contractor shall be issued three (3) sets of consultant’s drawings. The drawings shall be the basis of contractor’s shop drawings.
16 | Shop drawings are detailed working drawings coordinated with other trading work, which incorporate the contractor’s details for execution of the work and incorporate equipment manufacturer’s details and dimensions to ensure that the same can be installed in the space provided.
17 | All shop drawings will be made on AutoCAD and colored prints has to be produced for site work.
18 | This Schedule shall be fully priced and the extensions and totals duly checked. The rates for all items shall be filled in INK including NIL items.
19 | No alteration whatsoever is to be made to the text or quantities of this Schedule unless such alteration is authorised in writing by Consultant. Any such alterations, notes or additions shall, unless authorized in writing, be disregarded when tender documents are considered.
20 | In the event of an error occurring in the amount of the Schedule, as a result of wrong extension of the unit rate and quantity, the unit rate quoted by the tenderer shall be regarded as firm and the extensions shall be amended on the basis of rates.
21 | Any error in totaling in the amount column and in carrying forward total shall be corrected. Any error, in description or in quantity, omission of items from this Schedule shall not vitiate this Contract but shall be corrected and deemed to be variation required by the Consultant/Project Manager.
22 | Rates have been called for a number of items of works, as alternatives which, for the present do not form part of the total value of tender. However the rates for these items shall be quoted, with due care so that in the event of choice of an alternative item of work, said rate shall form part of the contract and shall not violate the contract any way.
23 | The contractor shall , from time to time, clear away all debris and excess materials accumulated at the site failing which the same shall be done by Project Manager at contractor’s risk and cost and cost of clean up shall be deducted from the contractors prorata bill.
24 | After the devices and equipment have been installed and commissioned, contractor shall cleanup the same and remove all plaster, paints, stains, stickers and other foreign matter or discoloration leaving the same in a ready to use condition.
25 | On completion of all works, contractor shall demolish all stores, remove all surplus materials and leave the site in a broom clean condition, failing which the same shall be done by the Project Manager at the Contractor'’ risk and cost. Cost of the cleanup shall be deducted from the contractor’s bills on pro-rata basis in proportion to his contact value.
26 | Provision for scaffolding if any required at site , contactor shall need to be provided.
27 | Remove existing drain and water supply lines which are not required. Clean the site for new installations.
28 | Required grooves shall be provided for driange connections with drip seal joint(C.I and PVC pipes connections)