## Summary
Project: Gorden Rasmay Mumbai
Scope of Work : Electrical and ELV
SUMMARY
S.No | Description | Supply | Installation | Total | Remarks
A | Electrical Works :
1 | LT Switchgear and Distribution Boards | 264150 | 10400 | 274550
2 | MCB Distribution boards | 78565 | 7250 | 85815
3 | Low Voltage Cables and End Termination | 91866 | 14450 | 106316
4 | Swicthes and Sockets | 120955 | 9950 | 130905
5 | Circuit Mains | 209750 | 24000 | 233750
6 | Point Wiring | 86400 | 37200 | 123600
7 | Cable Trays/Raceways | 46583 | 10675 | 57258
8 | Earthing | 15635 | 2930 | 18565
9 | PVC pipes (Electrical/IT/AV/CCTV/ACS) | 43675 | 5375 | 49050
10 | Structural Works | 0 | 0 | 0
11 | Miscellaneous Works | 11715 | 50725 | 62440
12 | Light Fixtures | 287000 | 9550 | 296550
13 | UPS | 85000 | 5000 | 90000
B | ELV Works :
1 | IT/CCTV Works | 881695 | 41240 | 922935
| Electrical and ELV - Total Amount | 2222989 | 228745 | 2451734

## Electrical Works
Project Name : Gorden Rasmay Mumbai | [7 empty] | Date : 09.12.2024
Electrical Works | [7 empty] | Rev No : R0
Sl No | ITEM DESCRIPTION | UNIT | QTY | Rate |  | Amount |  | Remarks
|  |  | Total | Supply | Installation | Supply | Installation
1 | LT SWITCHGEAR and Distribution Boards
Supply, installation, testing and commissioning of Low voltage switchgear's, free standing, Cubical type, dead front, Frame and Doors:2mm, Internal Partations:1.6mm thick, Gland Plates:3mm Thick, powder coated (Paint Shade: RAL 7032/7035), indoor type with vermin proof hinged lockable doors for each compartment, bus bar interconnections for incoming and outgoing including feeders earthing and painting and as per specifications comprising of ACB,MCCB and MCB horizontal and vertical aluminum bus bar, earth bus bar as per SLD. All meters shall be digital with LED display, whereever mentioned and shall have RS 485 Modbus RTU half duplex communication interface for provision of BMS connectivity and wired accordingly. Provide required NO/NC potential free contacts wires and terminal blocks in the cable alley for BMS operation (Optional).The swtichboards are to be tested as per IS 8623 -1977 specifications. The busbars are of high conductivity Al. alloy E91E IS 5082 specification and cable entries will be from either top or bottom depending on location. LT Switchgear shall be as per technical specification and single line diagram
1.1 | MDB
| MDB shall be as per Single line diagram and technical specifications.(Indoor -IP 42) | Nos | 1 | 155690 | 3000 | 155690 | 3000
1.2 | ISOLATORS
a | 160A 4P MCCB in metallic enclosure -IP 42 | Nos | 1 | 20462 | 1000 | 20462 | 1000 | Main Isolator (AS per Site Condition)
b | 63A 4P MCB in metallic enclosure -IP 42 | Nos | RO | 2968 | 200
c | 40A 4P MCB in metallic enclosure -IP 42 | Nos | RO | 2515 | 200
d | 25A 4P MCB in metallic enclosure -IP 42 | Nos | RO | 2515 | 200
e | 40A DP MCB in metallic enclosure -IP 42 | Nos | 2 | 1499 | 200 | 2998 | 400 | UPS Input and Output
f | 25A DP MCB in metallic enclosure -IP 42 | Nos | 0 | 1499 | 200 | 0 | 0
1.3 | STARTERS
a | Supply & Installation of 1.5kW Similat to Motor KW of fan slelected by OEM of unit as per approved TDS DOL/STAR DELTA starter with contactor, MPCB, overload relay, ON-OFF push buttons, Auto/Manual, ON/OFF/Trip indicating lamps, NO/NC Contacts and potential free contacts with required accessories and provied universal sockets as shown in SLD, refere Single line diagram and technical specifications. Starter panel shall be supplied with space provisons with internal wring circuits and sight glass for VFD instlattions. Installation and wiring terminations for VFD will be electrical vendor scope. Supply of VFD in HVAC vendor scope. | Nos | 1 | 25000 | 2000 | 25000 | 2000
b | Supply & Installation of 2.2kW Similat to Motor KW of fan slelected by OEM of unit as per approved TDS DOL/STAR DELTA starter with contactor, MPCB, overload relay, ON-OFF push buttons, Auto/Manual, ON/OFF/Trip indicating lamps, NO/NC Contacts and potential free contacts with required accessories and provied universal sockets as shown in SLD, refere Single line diagram and technical specifications. Starter panel shall be supplied with space provisons with internal wring circuits and sight glass for VFD instlattions. Installation and wiring terminations for VFD will be electrical vendor scope. Supply of VFD in HVAC vendor scope. | Nos | 1 | 28000 | 2000 | 28000 | 2000
b | Supply & Installation of 3.0kW Similat to Motor KW of fan slelected by OEM of unit as per approved TDS DOL/STAR DELTA starter with contactor, MPCB, overload relay, ON-OFF push buttons, Auto/Manual, ON/OFF/Trip indicating lamps, NO/NC Contacts and potential free contacts with required accessories and provied universal sockets as shown in SLD, refere Single line diagram and technical specifications. Starter panel shall be supplied with space provisons with internal wring circuits and sight glass for VFD instlattions. Installation and wiring terminations for VFD will be electrical vendor scope. Supply of VFD in HVAC vendor scope. | Nos | 1 | 32000 | 2000 | 32000 | 2000
| Total - Section-1 |  |  |  |  | 264150 | 10400
2 | MCB Distribution boards
a | 12 Way TPN MCB Distribution Board -PPI (KDB) | Nos | 1 | 37025 | 2500 | 37025 | 2500
MCB DB comprising the following
Type of DB - 12 way TPN PPI MCB DB (Double Door)
100A 4P MCB - 1 No. as incomer
63A DP RCCB, 30mA, 2 Module - 3 Nos. as Sub incomer per phase
20A SP MCB, 10 kA - 29 Nos. as outgoings : MCB are of 'C' Curve
32A SP MCB, 10 kA - 1 Nos. as outgoings : MCB are of 'C' Curve
The rate shall include providing Cu. bus barsinterconnection, separate earth bus, separate neutral bus for each phases, Blank Plates and incluuding necessary connected civil works like chipping, rough plastering etc.
b | 8 Way TPN MCB Distribution Board - PPI (LPDB) | Nos | 1 | 32025 | 2500 | 32025 | 2500
MCB DB comprising the following
Type of DB - 8 way TPN PPI MCB DB (Double Door)
32A 4P MCB - 1 No. as incomer
25A DP RCCB, 30mA, 2 Module - 3 Nos. as Sub incomer per phase
10A SP MCB, 10 kA - 18 Nos. as outgoings : MCB are of 'C' Curve
The rate shall include providing Cu. bus barsinterconnection, separate earth bus, separate neutral bus for each phases, Blank Plates and incluuding necessary connected civil works like chipping, rough plastering etc.
c | 12 Way SPN MCB Distribution Board | Nos | 1 | 9515 | 2250 | 9515 | 2250
MCB DB comprising the following
Type of DB - 12 way SPN MCB DB (Single Door)
40A DP RCBO,30mA, 2 Module - 1 No. as incomer
6A SP MCB, 10 kA - 4 Nos. as outgoings : MCB are of 'C' Curve
10/16A SP MCB, 10 kA - 10 Nos. as outgoings : MCB are of 'C' Curve
The rate shall include providing Cu. bus barsinterconnection, separate earth bus, separate neutral bus for each phases, Blank Plates and incluuding necessary connected civil works like chipping, rough plastering etc.
| Total - Section- 2 |  |  |  |  | 78565 | 7250
3 | LOW VOLTAGE CABLES AND END TERMINATION
3.1 | Low voltage Aluminium conductor cables
Supply and laying of 1100 V grade, XLPE insulated,extruded PVC Inner Sheathed and extruded FRLS-PVC Outer sheatehed , aluminium conductor, Armoured power cable as per specifications. The cable shall be laid in indoor trenches / cable trays as required. The cable shall be clamped at regular intervals to the suppoprts in trench or to cable trays or brick wall using MS clamps and fasteners. Rate shall exclude the cost of cable trays and termination in this item.
NOTE: Cables will not be procured based on BOQ only. True measurements will be taken by Contractor before ordering, based on Drawings/ Site actual requirements ( Applicable to all respect Line items)
a | 3.5CX 50Sqmm Alu.arm Cable | Rmt | 30 | 495 | 55 | 14850 | 1650 | Qty Varies as per Site Condition
b | 3.5CX 35Sqmm Alu.arm Cable | Rmt | RO | 445 | 55
c | 3.5CX 25Sqmm Alu.arm Cable | Rmt | RO | 185 | 50
d | 4CX 16Sqmm Alu.arm Cable | Rmt | RO | 435 | 42
e | 4CX 10Sqmm Alu.arm Cable | Rmt | 15 | 325 | 40 | 4875 | 600 | LPDB
f | 3.5CX 120 Sqmm Alu.arm Cable | Rmt | RO | 750 | 100 |  |  | Available till Shop Front(Client to confirm)
3.2 | Low Voltage Copper Conductor Cables
Supply and laying of 1100 V grade, XLPE insulated,extruded PVC Inner Sheathed and extruded FRLS-PVC Outer sheatehed copper conductor, Armoured/Un armoured power cable as per specifications. The cable shall be laid in indoor trenches / cable trays as required. The cable shall be clamped at regular intervals to the suppoprts in trench or to cable trays or brick wall using MS clamps and fasteners. Rate shall exclude the cost of cable trays and termination in this item.
Armoured Copper Cables :
a | 4Cx 16sqmm Cu Arm Cable | Rmt | 15 | 395 | 40 | 5925 | 600 | KDB
b | 4Cx 6sqmm Cu Arm Cable | Rmt | 100 | 335 | 40 | 33500 | 4000 | Oven, planetory,Combi oven,Dish Washer,Cooler
c | 4Cx 4sqmm Cu Arm Cable | Rmt | 60 | 237 | 40 | 14220 | 2400 | AC unit
d | 3Cx 6sqmm Cu Arm. Cable | Rmt | RO | 260 | 40
e | 3Cx 4sqmm Cu Arm. Cable | Rmt | 20 | 245 | 40 | 4900 | 800 | Scrubber
3.3 | Copper Flexible Cables :
a | 3Cx6sqmm Cu Flexible Cable | Rmt | 20 | 155 | 25 | 3100 | 500 | UPS
b | 4Cx6sqmm Cu Flexible Cable | Rmt | RO | 200 | 35
3.4 | LOW VOLTAGE CABLE END TERMINATION:
Supply and providing LV cable end termination for below listed cable with copper lugs, brass cable glands, tapping, crimping, etc. complete. Single Compression Glands : Cable Size Below 150 Sqmm Double Compression Glands : Cable size above 185sqmm and Single core cables 400sqmm and above
a | 3.5CX 50 Sqmm Alu.arm Cable | Nos | 2 | 2095 | 300 | 4190 | 600
b | 3.5CX 35Sqmm Alu.arm Cable | Nos | RO | 175 | 140
c | 3.5CX 25Sqmm Alu.arm Cable | Nos | RO | 175 | 140
d | 4CX 16Sqmm Alu.arm Cable | Nos | RO | 160 | 140
e | 4CX 10Sqmm Alu.arm Cable | Nos | 2 | 150 | 140 | 300 | 280
f | 3.5CX 120 Sqmm Alu.arm Cable | Nos | RO | 1100 | 250
3.5 | Armoured Copper Cables :
a | 4Cx 16sqmm Cu Arm Cable | Nos | 2 | 247 | 125 | 494 | 250
b | 4Cx 6sqmm Cu Arm Cable | Nos | 10 | 247 | 125 | 2470 | 1250
c | 4Cx 4sqmm Cu Arm Cable | Nos | 6 | 247 | 125 | 1482 | 750
d | 3Cx 6sqmm Cu Arm. Cable | Nos | RO | 270 | 125
e | 3Cx 4sqmm Cu Arm. Cable | Nos | 2 | 240 | 125 | 480 | 250
3.6 | Copper Flexible Cables :
a | 3Cx6sqmm Cu Flexible Cable | Nos | 8 | 135 | 65 | 1080 | 520
b | 4Cx6sqmm Cu Flexible Cable | Nos | RO | 185 | 65
| Total - Part 3 |  |  |  |  | 91866 | 14450
4 | SWITCHES AND SOCKETS
Supply and install switches and Sockets System as required according to the specification, drawings and design. The installation rate of all the following accessories shall include for the supply of all materials such as passivated metal switchbox,junction boxes, switch plate, switches, conduit accessories, wires, tags, supports, fittings fixings and the like, to form complete elements and shall include for earthing the switchboxes The installation rate shall include for termination of all cables and wires into the devices, testing,commissioning and setting to work as required by the specifications.
NOTE: SWITCHES AND SOCKETS will not be procured based on BOQ only. True measurements will be taken by Contractor before ordering, based on Drawings/ Site actual requirements ( Applicable to all respect Line items)
Power Receptacles with Box
4.1 | Supply, installation, testing and Commissioning of 1 x 6/16A, Universal 5 pin round/flat socket controlled with 1 x 16A Switch with Indication lamp including interconnection etc., complete.The sockets shall be with face plate, GI BOX with accessories.Rate shall include the cost for fixing of back box with plastering and rough finish | Nos | 57 | 465 | 95 | 26505 | 5415
4.2 | Supply, installation, testing and Commissioning of 1 x 6A, universal socket controlled with 1 x 6A Switch including interconnection etc., complete.The sockets shall be with face plate, GI BOX with accessories.Rate shall include the cost for fixing of back box with plastering and rough finish | Nos | 4 | 365 | 80 | 1460 | 320 | Signages
4.3 | Supply, installation, testing and Commissioning of 2 x 6/16A,, universal socket controlled with 2 x 16A Switch including interconnection etc., complete.The sockets shall be with face plate, GI BOX with accessories.Rate shall include the cost for fixing of back box with plastering and rough finish | Nos | RO | 815 | 100
4.4 | Supply, installation, testing and Commissioning of 3 x 6A, universal socket controlled with 1 x 16A Switch including interconnection etc., complete.The sockets shall be with face plate, GI BOX with accessories. Rate shall include the cost for fixing of back box with plastering and rough finish | Nos | RO | 1135 | 150
4.5 | Supply, installation, testing and Commissioning of 2 x 6A, universal socket controlled with 2 x 6A Switch including interconnection etc., complete.The sockets shall be with face plate, GI BOX with accessories. Rate shall include the cost for fixing of back box with plastering and rough finish | Nos | RO | 690 | 100
4.6 | Supply, installation, testing and Commissioning of 1 x 20A, universal socket controlled with 1 x 20A Switch floor mounted pop up box including interconnection etc., complete.The sockets shall be with face plate, GI BOX with accessories.Rate shall include the cost for fixing of back box with plastering and rough finish (MK Type Floor Box) | Nos | RO | 4420 | 500
Power Receptacles without Box
4.7 | Supply, Installation testing and commissioning of 3 nos. of 6/16 A, multi Pin Universal socket controlled by 1 no. 16 A common switch along with face plate, raceway/Table mounted and other necessary accessories to complete the installation. | Nos | 1 | 750 | 125 | 750 | 125
4.7 | Supply, Installation testing and commissioning of 6/16 A, multi Pin Universal socket controlled by 1 no. 16 A common switch along with face plate, raceway/Table mounted and other necessary accessories to complete the installation. | Nos | RO | 450 | 125
Industrial Sockets :
4.8 | Supply, installation, testing and Commissioning of 16A, 1 phase Industrial Plug & Socket controlled with 16A DP MCB in a enclosure with all accessories. (IP65) | Nos | 7 | 4950 | 250 | 34650 | 1750
4.9 | Supply, installation, testing and Commissioning of 20A, 1 phase Industrial Plug & Socket controlled with 20A DP MCB in a enclosure with all accessories. (IP65) | Nos | 3 | 5500 | 250 | 16500 | 750
4.10 | Supply, installation, testing and Commissioning of 25A, 1 phase Industrial Plug & Socket controlled with 25A DP MCB in enclosure with all accessories.(IP65) | Nos | RO | 5500 | 250
4.11 | Supply, installation, testing and Commissioning of 32A, 1 phase Industrial Plug & Socket controlled with 25A DP MCB in enclosure with all accessories.(IP65) | Nos | RO | 7000 | 250
4.12 | Supply, installation, testing and Commissioning of 32A, 3 phase Industrial Plug & Socket controlled with 32A 4P MCB in enclosure with all accessories.(IP65) | Nos | 4 | 7900 | 300 | 31600 | 1200
4.12 | Supply, installation, testing and Commissioning of 63A, 3 phase Industrial Plug & Socket controlled with 63A 4P MCB in enclosure with all accessories.(IP65) | Nos | 1 | 9200 | 300 | 9200 | 300
4.13 | Supply and installation of 3 Module Metal Boxes | Nos | RO | 75 | 40
4.14 | Supply and installation of 4 Module Metal Boxes | Nos | RO | 90 | 40
4.15 | Supply and installation of 6 Module Metal Boxes | Nos | RO | 110 | 50
4.16 | Supply and fixing of Blankplates | Nos | 2 | 40 | 15 | 80 | 30
4.17 | Supply and fixing of 3 Pin Plug top suitable for 16/20A | Nos | 2 | 105 | 30 | 210 | 60
| Total - Section - 4 |  |  |  |  | 120955 | 9950
5 | CIRCUIT MAINS
CIRCUIT MAIN FOR LIGHTING/POWER :
Supply and drawing of 1100V grade, multi strand FRLS insulated copper conductor wire. drawn into existing raceways/cable trays with necessary fixing accessories.
5.1 | 3 core 1.5 sqmm Double Insulated Copper copper conductor flexible cable with FRLS Sheathing in the existing raceways/conduits. Rate shall exclude the cost of Raceway/Conduit in this items. | Rmtrs | 40 | 50 | 15 | 2000 | 600 | Exit Signage
5.2 | 3 core 2.5 sqmm Double Insulated Copper copper conductor flexible cable with FRLS Sheathing in the existing raceways/conduits. Rate shall exclude the cost of Raceway/conduit in this items. | Rmtrs | 75 | 180 | 20 | 13500 | 1500 | Lighting Circuit mains
5.3 | 3 core 4 sqmm Double Insulated Copper copper conductor flexible cable with FRLS Sheathing in the existing raceways/conduit. Rate shall exclude the cost of Raceway/conduit in this items. | Rmtrs | 150 | 210 | 25 | 31500 | 3750 | Power
5.4 | 3 core 6 sqmm Double Insulated Copper copper conductor flexible cable with FRLS Sheathing in the existing raceways/conduit. Rate shall exclude the cost of Raceway/conduit in this items. | Rmtrs | RO | 250 | 25
5.5 | 2R x 2.5 sq.mm. + 1R 1.5 sq mm FRLS, MSCC wires drawn in 25mm Dia GI conduit with all accessories for general lighting.The rate shall include the cost of conduits and its accessories . | Rmtrs | RO | 100 | 30
5.6 | 2R x 4sqmm and 1RX2.5Sqmm FRLS MSCC wires drawn in 25mm dia GI conduit with all accessories for general purpose power sockets.The rate shall include the cost of conduits and its accessories. | Rmtrs | RO | 165 | 35
5.7 | 1 core 4 sqmm Double Insulated Copper copper conductor flexible cable with FRLS Sheathing in the existing raceways/conduits. Rate shall exclude the cost of Raceway/conduit in this items. | Rmtrs | 1750 | 90 | 10 | 157500 | 17500 | Lighting Circuit mains
5.8 | 1 core 6 sqmm Double Insulated Copper copper conductor flexible cable with FRLS Sheathing in the existing raceways/conduits. Rate shall exclude the cost of Raceway/conduit in this items. | Rmtrs | 50 | 105 | 13 | 5250 | 650 | Lighting Circuit mains
| Total - Section - 5 |  |  |  |  | 209750 | 24000
6 | POINT WIRING
Point wiring of light, using 1100 volt grade, 3Rx1.5Sqmm multi strand FRLS insulated copper conductor flexible cable, drawn in existing raceways/Conduit. The rate shall include providing mounting boxes with tapped holes for lights switches, moulded front plates with brass screws earthing of all points using third core of the cable, For MCB Controlled Lights -DB to 1st light will be measured as circuit wiring.The point wiring shall be as per specification.Rate shall exclude the cost of MCB,Rceways in this item.(CONDUIT - GI)
6.1 | PRIMARY LIGHT POINT (Switch Control)
| Primary light point means wiring from first switch control to the first light outlet. The switch and all necessary accessories would be part of primary point.'. Not to include the incoming lighting circuit from MCB-DB to switch.' But to include the sub-circuit if it is drawn from adjacent switch box. Ceiling flexible conduit shall be included at the drop of light fixture. | Nos | 12 | 2600 | 800 | 31200 | 9600
6.2 | SECONDARY LIGHT POINT (Switch Control)
| Secondary light point means extention of light outlet from existing primary point. Same to be controlled by the existing switch of primary point. Ceiling flexible conduit shall be included at the drop of light fixture. | Nos | 46 | 1200 | 600 | 55200 | 27600
6.3 | SECONDARY LIGHT POINT (MCB Control)
| Secondary light point means extention of light outlet from existing primary point. Same to be controlled by the existing MCB of primary point. Ceiling flexible conduit shall be included at the drop of light fixture. The Wiring from DB to First Light point will be measured under circuit mains. | Nos | RO | 715 | 500
6.4 | Ceiling fan point controlled by 6/10 A flush type SP switch. The rate shall include MS fan hook boxes. The rate shall also include cost of 300 W electronic fan speed controller in this item only.Rate shall exclude the cost of ceiling fan in this item. | Nos | RO | 1200 | 750
| Total - Section - 6 |  |  |  |  | 86400 | 37200
7 | CABLE TRAY/RACEWAYS
7.1 | Ladder Type
Supply and providing Ladder cable trays factory fabricated out of 2mm thick pre galvanized sheet steel, channel size 75 x 15 mm and rung size 30 x 6 mm, spaced at 250 mm interval, supporting angle frame at every 1.8 m, bottom angle fasteners, anchor grip bolts, synthetic enamelled painting, etc. The tray shall be suspended from ceiling using anchor bolt and angle iron supports or mounted from wall. The rate shall include all accessories like bends, elbows, tees, coupler plates, etc., which will be measured as linear measurement and fixing accessories.The rate shall include the cost of Supports
a | 150 mm wide 50 mm height | Rmtrs | RO | 650 | 150
b | 300 mm wide 75 mm height | Rmtrs | RO | 850 | 250
c | 450 mm wide 75 mm height | Rmtrs | RO | 1050 | 350
7.2 | Perforated Type
Supply and providing MS Perforated cable trays factory fabricated out of 2mm thick pre galvanized sheet steel, channel size 50 mm supporting angle frame at every 1.8 m, bottom angle fasteners, anchor grip bolts, synthetic enamelled painting, etc. The tray shall be suspended from ceiling using anchor bolt and angle iron supports or mounted from wall. The rate shall include all accessories like bends, elbows, tees, coupler plates, etc., which will be measured as linear measurement and fixing accessories.The rate shall include the cost of Supports
a) | 50 mm wide 50 mm height | Rmtrs | 5 | 515 | 50 | 2575 | 250
b) | 100 mm wide 50 mm height | Rmtrs | RO | 653 | 55
c) | 150 mm wide 50 mm height | Rmtrs | RO | 771 | 65
d) | 200 mm wide 50 mm height | Rmtrs | 15 | 878 | 125 | 13170 | 1875
e) | 300 mm wide 50 mm height | Rmtrs | 7 | 1084 | 150 | 7588 | 1050
7.7 | POWDER COATED FRAME FOR MCB DB's
a | Supply and Installation of DB Frame with wire ways shall be made out of 1.6mm thick CRCA sheet steel and powder coating colour shall match the colour of MCB DB's with hinged type door. 100mm x 100mm 1.6mm thick, wire ways / Raceway with 2mm thick screwed / press to fit cover with hinged type door for making Frame for MCB DB's. Complete required including installation accessories. | Rmtrs | 15 | 1550 | 500 | 23250 | 7500
| Total - Section - 7 |  |  |  |  | 46583 | 10675
8 | EARTHING
8.1 | Supply and Installation of earthing station as per IS3043 complete with 600x600x3.15mm Copper plate earthing with salt, charcoal, 2 nos. of 25x3mm Copper strip up to test link,19mm dia GI watering pipe with funnel, test link earthing chamber 450x450mm CI cover etc with required civil works complete. The CI Frame and cover shall be of heavy duty type. | Nos | RO | 23000 | 1500
8.2 | Supply and Installation of earthing station as per IS 3043 complete with GI pipe earthing with salt, charcoal, 2 nos. of 50x6mm GI strip up to test link ,40mm dia GI watering pipe with funnel,test link, earthing chamber of 450x450mm CI cover etc with required civil works complete.The CI Frame and cover shall be of heavy duty type. . | Nos | RO | 16800 | 1500
8.3 | Supply and running of below listed sizes of electrolytic copper / GI earth conductor tapes / wires and laid along with cable or clamped to brick wall, etc., as required.
a | 8 SWG GI wire for Earthing | Rmtrs | 40 | 24 | 7 | 960 | 280
b | 25x3mm GI Flat | Rmtrs | 25 | 122 | 25 | 3050 | 625
c | 25x6mm GI Flat | Rmtrs | RO | 186 | 30
d | 1Cx6sqmm Cu Flexible Cable Earthing (Green) | Rmtrs | 75 | 95 | 15 | 7125 | 1125
e | 1Cx4sqmm Cu Flexible Cable Earthing (Green) | Rmtrs | 50 | 79 | 15 | 3950 | 750
8.4 | Supply and installation of Earth pads made out of copper/GI busbars installed on 1100 V insulators including hardware and other minor civil works.associated works.
a | Busbar of 0.5 Mtr length made out of 25 x 3 mm Cu. strip with drill holes of M8 at 25mm interval mounted on insulators and acrylic cover to be provided. | Nos | RO | 645 | 150
b | Busbar of 0.5 Mtr length made out of 25 x 6 mm Cu. strip with drill holes of M8 at 25mm interval mounted on insulators and acrylic cover to be provided. | Nos | RO | 790 | 150
c | Busbar of 0.5 Mtr length made out of 45 x 6 mm GI strip with drill holes of M8 at 25mm interval mounted on insulators. | Nos | 1 | 550 | 150 | 550 | 150
| Total - Part 8 |  |  |  |  | 15635 | 2930
9 | PVC pipes (Electrical/IT/AV/CCTV/ACS)
9.1 | Supply and laying of 2 mm thick rigid FRLS PVC conduits in concealed conduit system using conduit accessories like junction boxes, collars, bends, elbows, binding wires, etc. | [6 empty] | For IT,CCTV,Wifi Only conduit provision
a | 32 mm dia conduit | Rmtrs | RO | 45 | 15
b | 25 mm dia conduit | Rmtrs | RO | 35 | 10
c | 20 mm dia conduit | Rmtrs | RO | 36 | 8
GI pipes (Electrical/IT/AV/CCTV/ACS)
9.2 | Supply and laying of 2 mm thick rigid MS conduits in concealed/Open conduit system using conduit accessories like junction boxes, collars, bends, elbows, binding wires, etc.
a | 32 mm dia conduit | Rmtrs | 10 | 280 | 25 | 2800 | 250
b | 25 mm dia conduit | Rmtrs | 125 | 215 | 25 | 26875 | 3125
c | 20 mm dia conduit | Rmtrs | 80 | 175 | 25 | 14000 | 2000
| Total - Section - 9 |  |  |  |  | 43675 | 5375
10 | STRUCTURAL WORKS
10.1 | Supply, cutting, welding, grouting, fastening, cleaning and painting of MS Channels, angles, plate, supporting brackets/structures , etc complete with necessary hardwares. | Kgs | RO | 250 | 150
10.2 | Supply of 6mm thick MS chequred plates duly painted. Plates to be cut size as per site requirement. | Kgs | RO | 175 | 125
| Total - Section - 10 |  |  |  |  | 0 | 0
11 | MISCELLANEOUS ITEMS
11.1 | Supply and fixing of danger boards of appropriate voltage grade, size and style as required by Electrical Inspectorate. | Nos | 1 | 865 | 100 | 865 | 100
11.2 | Supply of Rubber checkered mat of size 2000 x 1000 x 10mm thick, 11000 V grade. | Nos | 0 | 4500 | 100 | 0 | 0
11.3 | Supply of Rubber checkered mat of size 2000 x 1000 x 3mm thick, 11000 V grade. | Nos | 1 | 3950 | 100 | 3950 | 100
11.4 | Supply of Standard First aid box complete with all accessories. | Nos | 1 | 1500 | 200 | 1500 | 200
11.5 | Supply of Wooden framed glass fronted shock treatment chart as per IE rules fixed to wall. | Nos | 1 | 2500 | 125 | 2500 | 125
11.6 | SITC of Hand held Fire Extinguisher - ABC Powder - 6 Kg with floor mount accessories | Nos | 1 | 2900 | 200 | 2900 | 200
11.7 | Temporary Works
a | For temporary Lighting in the construction area with necessary light fixtures ,cabling & Power Distribution control panel for construction works.The cost shall include necessary industrial sockets, cables, distribution boards, earthing,Light fixtures and all safety accessories as required. | LS | RO |  | 85000
b | Professional charges towards filing application, preparation of drawings in necessary formats for approval, follow up and arranging approval of drawings, scheme by Local electricity authority Electrical Inspectorate, obtaining clearance from electricity authority / Electrical Inspectorate. | LS | RO |  | 250000
c | Preparation and Submission of as built drawings of total work executed (2 Sets hard and soft copy) | Nos | 1 |  | 50000 | 0 | 50000
| Total - Section - 11 |  |  |  |  | 11715 | 50725
12 | LIGHT FIXTURES
12.1 | Supply Installation of LED 2x2 Grid Light (Type-1) | Nos | 21 | 5500 | 150 | 115500 | 3150
12.2 | Supply Installation of LED Recessed Mounted Type Light Fixtures (Type-2) | Nos | 20 | 2800 | 150 | 56000 | 3000
12.3 | Supply Installation of LED Hanging Light Fixtures (Type-3) | Nos | 3 | 7500 | 200 | 22500 | 600
12.3 | Supply Installation of LED Track Light Fixtures (Type-4) | Nos | 9 | 8500 | 200 | 76500 | 1800
12.2 | Supply Installation of LED Decorative suspended lLight fixture (Type-5) | Nos | 1 | 2500 | 200 | 2500 | 200
12.2 | Supply Installation of LED Decorative suspended lLight fixture (Type-5) | Nos | 4 | 3500 | 200 | 14000 | 800
12.2 | Supply Installation of LED Strip Light (Type-7) | Mtrs | 0 | 600 | 50 | 0 | 0
| Total - Section - 12 |  |  |  |  | 287000 | 9550
13 | UPS
a | Supply, Installation, Testing & Comissioning of: 5 KVA 1 Phase input/1 phase output UPS with 90 mins. Backup Battery Type: SMF with racks & enclouser (Output Power Factor Unity ) | Nos | 1 | 85000 | 5000 | 85000 | 5000
| Total - Section - 13 |  |  |  |  | 85000 | 5000

## ELV Works
ESTIMATION FOR ELV
Project name: Gorden Rasmay Mumbai | [6 empty] | Date: | 09.12.2024
Location: | [6 empty] | Revision | R0
Project no: | [6 empty] | Document No:
S.no | Description | Unit | Qty | Rate |  | Amount |  | Remarks
|  |  |  | Supply | Installation | Supply | Installation
1 | IT/NETWORKING :
1.1 | 4-pair, Cat 6 UTP FRLS Cable | Mtrs | 100 | 40 | 10 | 4000 | 1000
1.2 | Cat 6 UTP Information Outlet for Workstation end | Nos | 4 | 250 | 30 | 1000 | 120
1.3 | Cat 6 RJ45-RJ45 UTP Patch Cords, color matched, Yellow - Workstation end, 7 ft | Nos | 4 | 195 | 10 | 780 | 40
1.4 | Single Face Plates | Nos | 4 | 95 | 20 | 380 | 80
1.5 | Dual Face Plates | Nos | 0 | 150 | 25 | 0 | 0
1.6 | Supply and fixing of Metal box suitable information outlet , flush/surface type in position .The rate shall exclude the cost of faceplate and Information Outlet. | Nos | 4 | 45 | 10 | 180 | 40
1.7 | Supply, installation, testing and Commissioning of RJ11 Telephone Point. The Telephone Socket shall be with face plate, GI BOX with accessories. | Nos | 0 | 150 | 15 | 0 | 0
1.8 | Cat 6 24 Port Angled Discrete Jack panel - fully loaded (1U).The rate shall include the cost of Patch Panel, Information Outlets with all the required supporting accessories. | Nos | 1 | 7500 | 1000 | 7500 | 1000
9 | 06 U wall mount rack with required mounting accessories, Rate shall include required accessories, tools etc., complete as required. | No | 1 | 8500 | 500 | 8500 | 500
2 | CCTV :
1 | Supply, installation, testing and Commissioning of UL approved, IP based Dome Indoor type 5MP,HD Dome camera | Nos | 5 | 4500 | 250 | 22500 | 1250
2 | Supply, installation, testing and Commissioning of UL approved, Outdoor type 2MP Camera | Nos | RO | 9500 | 250
3 | Supply, installation, testing and Commissioning of 8 Channel NVR Ultra 4 K resolution and recording software with Storage capacity of 30Days .with all required accessories | No | 1 | 28000 | 2500 | 28000 | 2500
4 | CAT 6 PoE Cable, as per the survey done, Rate shall include required accessories, tools etc., complete as required. | Mtr | 100 | 40 | 10 | 4000 | 1000
5 | Cat 6 Sngle Information Outlets including faceplates and backbox accessories. | Nos | 5 | 395 | 150 | 1975 | 750
6 | Cat 6 12 Port Angled Discrete Jack panel - fully loaded (1U).The rate shall include the cost of Patch Panel, Information Outlets with all the required supporting accessories.(CCTV) | Nos | RO | 6500 | 750
7 | Cat 6, PoE 7ft Gigabit Snagless Molded Patch Cable (RJ-45 Male) with factory crimping, these patch cords will suffice for connecting between Data Outlet & CCTV | No | 0 | 250 | 25 | 0 | 0
8 | Cat 6, PoE 4ft Gigabit Snagless Molded Patch Cable (RJ-45 Male) with factory crimping, these patch cords will suffice for connecting between Data Outlet & CCTV (100%) | No | 5 | 210 | 25 | 1050 | 125
9 | 05 U wall mount rack with required mounting accessories, Rate shall include required accessories, tools etc., complete as required. | No | RO | 7500 | 500
5 | WIFI - DATA
5.1 | 4-pair, Cat 6A UTP Cable, roll of 305m, Grey | Box | 70 | 11250 | 300 | 787500 | 21000
5.2 | Cat6A UTP Information Outlet for Workstation end | Nos | 3 | 275 | 30 | 825 | 90
5.3 | Cat6A RJ45-RJ45 UTP Patch Cords, color matched, Yellow - Field end, 7 ft | Nos | 3 | 200 | 10 | 600 | 30
5.4 | Single Face Plates (100%) | Nos | 3 | 75 | 20 | 225 | 60
5.5 | Dual Face Plates | Nos | 0 | 80 | 20 | 0 | 0
5.6 | Quad Face Plates | Nos | 0 | 85 | 20 | 0 | 0
5.7 | Blank Inserts | Nos | 0 | 15 | 5 | 0 | 0
5.8 | Supply and fixing of Metal box suitable information outlet , flush/surface type in position . The rate shall exclude the cost of faceplate and Information Outlet. | Nos | 3 | 35 | 10 | 105 | 30
10 | PVC pipes
Supply and laying of 2 mm thick rigid FRLS PVC conduits in concealed conduit system using conduit accessories like junction boxes, collars, bends, elbows, binding wires, etc.
a | 32 mm dia conduit | Mtrs | RO | 45 | 15
b | 25 mm dia conduit | Mtrs | RO | 35 | 10
c | 19 mm dia conduit | Mtrs | RO | 36 | 8
11 | GI pipes
Supply and laying of 2 mm thick rigid GI conduits in concealed/Open conduit system using conduit accessories like junction boxes, collars, bends, elbows, binding wires, etc.
a | 32 mm dia conduit | Mtrs | 0 | 280 | 25 | 0 | 0
b | 25 mm dia conduit | Mtrs | 30 | 215 | 25 | 6450 | 750
c | 19 mm dia conduit | Mtrs | 35 | 175 | 25 | 6125 | 875
12 | 1.5 meter length, Powder coated MS 25 mm dia Conduit supports for CCTV cameras with required supporting /mounting accessories complete. | No | RO
13 | Supervision, Programming, Testing & Commissioning, Documentation, Training. | LS | 1 |  | 10000 | 0 | 10000
| TOTAL AMOUNT |  |  |  |  | 881695 | 41240
TAX
GRAND TOTAL - SUPPLY + INSTALLATION +TAXES
Makes:
CAMERAS & SOFTWARE: Hikvision,Dahua,Bosch
NVR: Hikvision,Dahua,Bosch
CAT 6 Cables : Legrand,Tyco,R&M,Systimax,Commscope
RACKS : Rittal ,Valrack,Netrack
Exclusions:
Active components, Network Switch & servers ,Wifi Equipmnet
Note:
All Devices shall be of Enterprize Class Only