## Fire and Life Saftey
Project Name :Gordan_Ramsey_Mumbai | [7 empty] | Date : 06.12.2024
Fire Alarm, Extinguisher Fire Signage,Fire Sprinkler and PA System | [7 empty] | Rev No : R0
Sl No | ITEM DESCRIPTION | UNIT | QTY | Rate |  | Amount |  | Remarks
|  |  | Total | Supply | Installation | Supply | Installation
1 | FIRE Alarm System Works
1.1 | Supply installation testing and commissioning of addressable type smoke detectors with LED indication lamp, MS Back box, detector base braket, along with complete fixing accessories.(Above false ceiling) | Nos | RO | 4500 | 100
1.2 | Supply installation testing and commissioning of addressable type smoke detectors with LED indication lamp, MS Back box, detector base braket, along with complete fixing accessories.(Below false ceiling) | Nos | 4 | 4500 | 100 | 18000 | 400
1.2a | Supply installation testing and commissioning of addressable type Multi Sensor Heat detectors with LED indication lamp, MS Back box, detector base braket, along with complete fixing accessories. | Nos | 5 | 6500 | 100 | 32500 | 500
1.3 | Supply installation testing and commissioning of Response indicators with complete fixing accessories for the detectors placed above false ceiling and below false flooring | Nos | RO | 550 | 100
1.4 | Supply installation testing and commissioning of addressable Hooter cum STROBE along with its control modules complete with all fixing materials. | Nos | RO | 3500 | 200
1.5 | Supply and installation of analogue addressable type Manual call points with Glass and hammer and monitor module with complete fixing accessories also with self illuminated signage. | Nos | 1 | 3100 | 200 | 3100 | 200
1.6 | Supply and installation of Short circuit Fault Isolators @ 20 detectors with complete fixing accessories | Nos | RO | 2500 | 100
1.7 | Supply and installation of Monitor Module with complete fixing accessories | Nos | 1 | 3500 | 100 | 3500 | 100
1.8 | Supply and installation of Control Relay Module with complete fixing accessories | Nos | 1 | 3500 | 100 | 3500 | 100
1.9 | Supply and laying of PVC insulated,2C x 1.5sq.mm shielded armored FRLS copper cable (RED COLUR) including cable glands and all fixing accessories where ever required complete with end terminations at both sides. The colour of the cable shall be RED only.( Shall be on actuals ). | Rmtrs | 100 | 85 | 25 | 8500 | 2500
1.10 | Supply, installation, testing and commissioning of Gas Detector Panel which consists of display board which will have 160 Character Display with Touch key pad, Mother board which will have ARM CORTEX M3 32 Bit Processor, Inbuilt RS-485 Networking Circuit for peer to peer networking, Inbuilt USB 2.0 Port for upload and download the Configuration tools, Two inbuilt programmable inputs, Two inbuilt NAC's, and Three Programmable Relays, and 4 Loop Card circuits. power Supply, Installation and Commissioning Board which will have SMPS fully protected board, which its operates on 120 to 220V AC ± 10% with 50/60 Hz, battery backup 24V DC with built-in charger. the panel have IP-50 rating Optional: for BMS integration thru MODBUS converter, Graphical Software, Software for TCP/IP Module, provision for GSM based Auto dialler, provision for printer thru compatible module, fire alarm panel with battery backup for 6 hours operation, with battery charger, alarm bell, test buttons etc.
a | 2 loop panel | Nos | 1 | 95000 | 5000 | 95000 | 5000
b | 4 loop panel | Nos | RO | 115000 | 5000
1.11 | SITC of Hand held Fire Extinguisher - ABC Powder - 6 Kg with floor mount accessories | Nos | 2 | 2800 | 150 | 5600 | 300
1.12 | SITC of Hand held Fire Extinguisher - CO2 - 4.5 Kg with floor mount accessories | Nos | 4 | 3500 | 150 | 14000 | 600
1.13 | Supply installation testing and commissioning of Emergency Exit -LED Battery Backup(180Min) | Nos | 0 | 4500 | 100 | 0 | 0
1.14 | Supply installation testing and commissioning of Fire Exit - LED Battery Backup (180Min) | Nos | 4 | 5500 | 100 | 22000 | 400
1.15 | Supply installation testing and commissioning of Exit - LED Battery Backup (180Min) | Nos | 0 | 3900 | 100 | 0 | 0
2 | PA System Works
2.1 | Supply and installation testing and commissioning of 6 Watt 180mm dia Surface mounted white colour speakers along with all fixing accessories. | Nos | 0 | 1800 | 150 | 0 | 0
2.2 | Supply and installation testing and commissioning of 6 Watt Recesse Mounted Ceiling speakers along with all fixing accessories . | Nos | 5 | 1800 | 150 | 9000 | 750
2.3 | Supply and laying of shielded twin twisted pair 1.0 sqmm cable in existing conduit ( Shall be on actuals ). | Rmtrs | 50 | 20 | 10 | 1000 | 500
2.4 | Supply and fixing of 20mm dia heavy guage GI conduit concealed in wall/ above false ceiling for taking copper wires including all accessories such as Conduit junction boxes, bends etc as required ( Shall be on actuals ). | Rmtrs | 40 | 155 | 15 | 6200 | 600
2.5 | Mixer Amplfier -240W with Pre recorded Message ,Music Ssytem etc complete in a PA rack (The rate to include the Cost of rack and other required acessories ) | Nos | RO | 55000 | 2000
2.6 | Mixer Amplfier -120W with Pre recorded Message ,Music Ssytem etc complete in a PA rack (The rate to include the Cost of rack and other required acessories ) | Nos | RO | 35000 | 2000
3 | Fire Sprinkler System:
3.1 | Supply, installation, testing and commissioning of G.I Heavy grade piping as per IS: 1239/3589 GI Forged Threaded GI forged socket welded & 65mm and above Seamless schedule 40) with necessary fittings such as tees, elbows,union,flanges, bends, rubber gaskets, reducers, GI nut bolt, washer etc. The pipes being suspended from ceilings by using support with clamps, hangers using anchor fastners upto 65 mm & above 80 mm pipe should be support with galvanized channel supports complete Rate quoted shall include painting with one coat of zinc cromet primer & 2 coats of synthetic enamel PO red paint and for painting of pipe & brackets and clamps as per IS-5 for above ground piping as per the NBC / IS standards and local fire service department requirement complete including supply and installation of G.I. Rods, clamps and , fasteners etc. All supports shall be hot dip galvanized in the range of DFT of micron 80 to 90 micron with 7 tank process, hot dip galvanizing shall be confirming to IS:2629/2633/4759/6745. Anchor fastners to be used of chemical type only where pipe supports to be taken from brick/block work.
a | 150mm nominal dia | Rmtrs | 0 | 2800 | 500 | 0 | 0
b | 100mm nominal dia | Rmtrs | 0 | 2100 | 440 | 0 | 0
c | 80mm nominal dia | Rmtrs | 10 | 1900 | 390 | 19000 | 3900
d | 65mm nominal dia | Rmtrs | 10 | 1100 | 260 | 11000 | 2600
e | 50mm nominal dia | Rmtrs | 0 | 950 | 350 | 0 | 0
f | 40mm nominal dia | Rmtrs | 5 | 760 | 290 | 3800 | 1450
g | 32mm nominal dia | Rmtrs | 15 | 595 | 190 | 8925 | 2850
h | 25mm nominal dia | Rmtrs | 45 | 450 | 180 | 20250 | 8100
3.2 | Supplying, installing, testing and commissioning conventional Standard Response Sprinkler quartzoid bulb type with 15mm screwed end connection of 68 deg. C. temperature rating, K-Factor =5.6 GPM/psi½ (80.6 LPM/bar½) and orifice shall not be less than 6mm. Sprinklers shall be UL Listed / BIS approved with Chrome finished.
a | Pendent Sprinkler | Nos | 22 | 1500 | 200 | 33000 | 4400
b | Upright Sprinkler | Nos | RO | 950 | 125
b | Concealed Sprinkler | Nos | RO | 2500 | 125
3.3 | Stainless steel corrugated flexible pipe(hose) for dropping sprinklers below false ceiling, pipe shall be 16 bar pressure rating and 1500 mm long, 25 mm dia with union / reducer collar, clamps etc. as required. | Nos | 22 | 1900 | 100 | 41800 | 2200
3.4 | Supply & fixing of approved type rosette plates (Recessed type, in two piece) for Sprinklers below false ceiling area. | Nos | 22 | 175 | 30 | 3850 | 660
3.5 | Supply and Installation, Testing and Commissioning of CI butterfly valves (body conforming to IS 210 GR FG 200) slim seal standard lever operated type conforming to IS13039/BS5155 with required flanges, nuts, bolts etc complete with supervisory tamper switch for monitoring. The valves shall be suitable for 150 psi pressure rating. Tamper Switch equipped with 2 Nos. of NO-NC contacts for monitoring | [6 empty] | Assumption ,varies as per Site Condition
a | 100 mm dia | Nos | RO | 12500 | 500
b | 80 mm dia | Nos | RO | 10000 | 500
c | 65 mm dia | Nos | RO | 8000 | 500
3.6 | Fire Sprinkler Pipe Modifictaion Works (Extending the branch pipe as per proposed Interior layout wherever required and removal of existing rigid dropers) | Lot | RO |  | 10000
| Total Amount |  |  |  |  | 363525 | 38110 | 401635
TAX
GRAND TOTAL - SUPPLY + INSTALLATION +TAXES