## TechItemDoc
ItemCode | Item Name | UOM | Qty | Unit Price | Remarks
A | WATER SUPPLY PIPING
1 | CPVC Pipes conforming to ASTM D-2846, SDR-11 grade and CPVC solvent weld fittings like elbows, tees, couplars, brass threaded adaptors, insert ring etc. suitable for (domestic and flushing) cold applications rated, concealed piping within wall / floor including jointing with fittings using solvent cement, brass threaded end fittings for making connection to fixtures. The work shall also include chasing the walls with machine wherever required for concealed piping and making good the same after laying of pipes & necessary pressure testing Chasing finishing shall be done with 1:1 cement mixed mortar, restore the same original condition for internal and shaft piping, including necessary hot deep galvanised supports vertical / horizontal, as per direction of Site incharge direction. [The rate shall include supply of S.S.screws and nut bolts etc.chasing in walls done by machine] (For Domestic and Flushing water-Toilet internal) (Pipe shall be tested with 1.5 times working pressure as covered in specifications) |  |  |  | Astral / Ashirwad /supreme / Prince or Approved Equivalent
1.1 | 20 mm Dia | R.mt | 55
1.2 | 25 mm Dia | R.mt | 20
1.3 | 32mm Dia | R.mt | 20
2 | Copper pipes and tubes shall be hand tempered conforming to requirements of EN 1057 ( formerly BS 2871) Table X , half and the fittings shall confirm the EN-1254-I ( Formerly BS 864: part-02). The fittings shall be end feed capillary fittings within wall/ceiling / floor including cutting & chasing the wall/ floor, jointing, making connection to fixtures, equipment and piping with purposes made connectors, etc. including insulation of closed cell elastomeric nitrile rubber. thermal conductivity of elastometric nitrile rubber shall not exceed 0.038w/m deg K. The insultaion should have fire performance and thickness of nitrile rubber should be 9mm (for hot water piping)
2.1 | 20mm Dia | R.mt | 10
2 | Providing & Fixing of forged brass lever operated Ball Valves (10Kg/Sq.cm). Valve shall have with unions. |  |  |  | Leader / Neta / Zolotto / or approved Equivalent
2.2 | 25mm Dia | Nos. | 1
2.3 | 32mm Dia | Nos. | 1
3 | Providing ,fixing, testing and commissioning Electromagnetic flow meter including providing & fixing matching with required accessories 16Kgs/Sq.cm). - Contractor to check existing make in BILA airport and provide that.
3.2 | 32 mm Dia incoming line | Nos. | 1
4 | Supply, installation,testing & commissioning of Storage Type Electric Hot Water Generator of mentioned capacity, suitable for 3 KG/cm2 pressure, Wall Mounted / Floor standing type, with Auto Shut-off Thermostat, along with isoltion Valves, Air Release valve, SS flexible connections andall other std accessories |  |  |  | AO Smith/Racold or Approved Equivalent
4.2 | 25 L Capacity | Nos. | 1
6 | SITC of Eco smart RO-100 with all required accessories | No | 1 |  | Make- Ion Exchange/ or equivalent
7 | Supply, Installation, Commissioning & Testing for Booster pump for Ro water supply WITH FLOW SWITCH GRAVITATIONAL FLOW (top to bottom flow) with both side Sensor operations- A) 3CUM PER HR. B) HEAD: 25M, C) PHASE: SINGLE PHASE, D) PROTECTION: IP55, E) MONOBLOCK TYPE, with sensors cabling & Control panel.(Pump shall be Auto fill stop and Auto empty start mechanisam) |  |  |  | Grundfoss /Kirloskar / Bharat Bijli / Agasti / or Approved Equivalent
7.1 | 0.75 HP | Nos. | 2
8 | Supply, Installation of sintex loft mounted water tank of 50 Ltrs | Nos. | 1 |  | Sintex
9 | P/F water level Indicator on loft water tank by means of a transparent clear tube fixed along height of the water tank hence making water level visible | Nos. | 3
10 | Providing & Fixing Brass Non Return Vavles of ISI mark. Rates are for BRASS valves |  |  |  | Make – KITZ / ZOLOTO / AUDCO /or Approved Equivalent
12.1 | 20mm | Nos | 4
12.2 | 25mm | Nos | 4
11 | SITC of ACO grease trap -model Lipumobil 0.8 -Capacity -48 lit ( 0.8 LPS) with all required accessories ( Order shall be placed as per space available below the counter) | Nos | 3 |  | Aco or Approved Equivalent
14 | Supply, Installalation , testing commissioning of S.S. Grease trap nurgreen Make -NGT 8 ( 15.9 lit) | Nos. | 1
B | DRAINAGE
1 | UPVC-SWR pipes (working pressure 10kg/cm2) conforming to IS 13592/92 and IS 14735-type-B solvent posted ( for Dia above 50mm) and for ( Dia below 50mm) shall be as per IS 4985 and 7834 Class-05 (10 kg/cm2) including cutting the pipes to required lengths, laying in the position to required grade and level, jointing, supporting with PVC cleat,hot deep galvanised bracket supports,hot deep galvanised nut-bolts, anchor fastners, PVC coated U-clamp, testing and rectifying leakages for piping within vertical shafts / supported on wall / hung below slab etc. with all material & labor complete and as directed. [The Rate shall include supply and fixing of nesessary items] Vertical line bracket shall be fixed at every 0.8 mtr to 1.00 mtr.] |  |  |  | Supreme / Finolex / Prince / Oriplast / or Approved Equivalent
1.1 | 40mm Dia | R.mt | 5
1.2 | 50mm Dia | R.mt | 15
1.3 | 65mm Dia bendable pipe | R.mt | 5
1.4 | 75mm Dia | R.mt | 20
1.5 | 100 mm Dia | R.mt | 15
3 | Supply, Install PVC Multi Floor Trap for the following pipes including making all approved quality Solvent cement joints with material & labour etc. all complete as per direction of the engineer-in-charge. | Nos. | 2
4 | Supply, Install PVC urinal Traps including fixing with necessary consumables with Circular SS Grating with anti cockroach jali Suitable for 75mm Dia outlet | Nos. | 1
5 | Supply, Install PVC P- Traps including fixing with necessary consumables with Circular SS Grating with anti cockroach jali Suitable for 75mm Dia outlet | Nos. | 1
C | SANITARY AND C. P. FITTINGS & FIXTURES
Only installation, testing and commissioning of sanitary and C.P. fittings( Client /Architect to select the model no as required and provide fixtures)
1.1 | EWC with seat cover | Nos | 2
1.2 | Concealed flush tank | Nos | 2
1.4 | Health Faucet | Nos | 2
1.5 | 2 Way Bib-Cock with connection for Health Faucet | Nos | 2
1.7 | Under Counter Wash Basin including waste Coupling | Nos | 3
1.1 | Jet Spray | Nos | 2
1.12 | Under Counter Sink including waste Coupling | Nos | 4
1.13 | Sink Pillar Cock | Nos | 4
1.14 | Bottle Trap for WHB/ sink and urinal with all connecting pipes | Nos | 6
1.15 | Angle Cock with PVC pipe connection upto WHB/sink/Geyser connection | Nos | 8
1.16 | Urinal | Nos | 2
1.17 | Auto Flush Valve & Sensor with connecting piping & spreader for urinal(DC) | Nos | 2
SUB TOTAL -C-SANITARY AND C. P. FITTINGS & FIXTURES ( ONLY INSTALLATIONS)
D | S.S. GRATING
Supply , installations/ testing and commissioning of S.S.Gratings
1 | Only installation of S.S Grating size, 300mm x 300mm, in 16 swg 25mm x25mm Square Pipe around the Frame and 20mmX 20mm Square pipe in center of frame with SS perforated tray (304 SWR). Complete as per architectural detail drawing & Site Engineer's instruction. (100 mm Dia S.S 304 grade finish unions reducers/coupling or 75mm Dia S.S 304 grade finish unions reducers/coupling or 50mm Dia S.S 304 grade finish unions reducers/coupling) | Nos. | 4