## TechItemDoc
ItemCode | Item Name | UOM | Qty | Unit Price | Remarks
1 | Providing, laying, jointing, testing and commissioning of G.I. `C' Class pipes (IS:1239 (Part-I) including cutting,threading welding etc providing all malleable galvanized iron fittings conforming to IS 1879, viz. Flanges, bends, tees, elbows,reducers, unions, grooved couplings( as per FM approved and UL listed), supporting with G. I. clamps, hangers, M.S. brackets etc. including cutting holes and chases in brick or RCC wall / slabs and making good the same to the Approval of Architect / consultant,complete including painting with one coat of primer and two or more coats of synthetic enamel paint of approved make and shade. -All pipes joints will be threaded up to 50 mm dia pipes and above will be grooved couplings. (Welded joints not permitted). 2) Clevis hanger support for dia 25mm to 100mm dia pipe. 3) Supports (ISA-50x50x6mm thick) for dia 150mm pipe. 3) Channel support (ISMC 100x50x5mm thick) for dia 150mm multiple pipes.
i) | 25 mm dia. | RMT | 90
ii) | 32 mm dia. | RMT | 10
iii) | 40 mm dia. | RMT | 12
iv) | 50 mm dia. | RMT | 30
v) | 65 mm dia. | RMT | 10
vi) | 80 mm dia | RMT | 12
vii) | 100 mm dia. | RMT | 5
2 | Providing , fixing testing and commissioning of concealed type FM approved and UL listed sprinkler heads 68 deg. Temp.(K-5.6) | No. | 60
3 | Providing , fixing testing and commissioning of upright type FM approved and UL listed sprinkler heads 68 deg. Temp.(K-5.6)-Optional subject to site requirements | No. | 10
4 | Providing , fixing testing and commissioning of pendent type FM approved and UL listed sprinkler heads 79 deg. Temp-(K-5.6)-in kitchen | No. | 4
5 | Providing & fixing testing and commissioning of FM approved and UL listed SS Flexible pipe -1.6mt L | No. | 60
6 | FM approved and UL listed Gun metal chrome finished Ball valves (PN 25) with fittings of screwedend type.
I) | 50 mm dia. | No. | 2
7 | FM approved and UL listed Butterfly Valves (PN 25) with CI Body, Black Nitrile Body Liner and Nylon Coated SG Iron Disc with material and labour including hydraulic testing etc. complete as per drawing, specification & to the level of satisfaction of Site- Incharge.
II) | 80 mm dia. | No. | 2
14 | Dismantaling existing sprinkler heads/pipes as shown in the layouts and make it workable as per requirements.( Note- Existing ceiling services height apx. 3.6-4mt to be considered.) | RMT | 150