## GAS PIPING- BOQ
Anaexer -1 (Edli .com
Work Scope : SITC PNG Pipeline & Gas Leake Detactor System
S/NO | DESCRIPTION | Make | Qty. | UNIT | Unite price
[5 empty] | Supplay | Installation | SITC | Amount
1 | PNG Gas Daiphram Type Meter Model G-4 , Running Pressure 2-bar, Flow Rate 6 m3/h with fiting (elbo,tee,Cupler) | honywell/Matrix | 1 | Nos. | 20500 | 4715 | 25215 | 25215
2 | Pressure Control Regulator RJ-4 Inlet 0 to 19 bar, Outlet 0 to 1.5 Bar | United/honywell | 1 | Nos. | 3200 | 736 | 3936 | 3936
3 | Gas Filter 25mm almuniam Body | Vanaz/Honywell/vel | 1 | Nos. | 3950 | 908.5 | 4858.5 | 4858.5
4 | Pressure Gauge 4" Dail 2.5 Bar | Mahaveer/ H-guru | 2 | Nos. | 2850 | 655.5 | 3505.5 | 7011
5 | Low Pressure Gauge 0.500Mbar ( for used Low pressure Equipment) | Mahaveer/ H-guru | 2 | Nos | 2760 | 634.8 | 3394.8 | 6789.6
6 | Low Presssure Regulator RJ-4 Blue ( For Used Point Deck Oven) | united/Vanaz | 2 | Nos | 3400 | 782 | 4182 | 8364
7 | MS Pipe 40 mm NB IS-1239 ,, MS Fitting (Elbow. Tee, Reducer ANSI B16.5 , 11 ) MS Support , U-Clamp , M clamp , Sleeve and ancher Fastner . | Tata/Jindal/MSL | 30 | RMT | 1150 | 264.5 | 1414.5 | 42435
8 | CS Ball Valve 40 NB Srew end 150 # single pc design ASME-B16.10 | L&T | 2 | No. | 6000 | 1380 | 7380 | 14760
9 | Ball Valve 15 NB Screwed , NPTTF end, 3 pcs design ASME B16.10 (for Used Point) | L&T | 5 | Nos. | 4500 | 1035 | 5535 | 27675
10 | Painting of pipes. 2 coats of red oxide and 2 coats of Golden Yellow final paint. Total 120 microns thickness | Acian/Burger | 30 | RMT | 95 | 21.85 | 116.85 | 3505.5
11 | Hose Pipe 3/4" , Dia ,1.5 mtr Lent Havy Duty Black Used Point | Hyflex/suraksha | 4 | Nos. | 1650 | 379.5 | 2029.5 | 8118
12 | Testing & commissioning of Pipe with Nitrogen gas for Testing with pressure of 6 Bar to test all joints with soap test for the leakage , then it will be time holded for 4 hrs then 6 hrs & finally 24 hrs to check wheather the leakage is there or not. After this we will release PNG Gas & will start the line Test Pressure 6 air & 4-Bar Nitrojen | Job | 1 | JOB | 8500 | 1955 | 10455 | 10455
LPG Leak Detector & Alarm System
13 | Gas Leakage Detector Display Type | Ambetronic/Crimcent | 4 | Nos | 12500 | 2875 | 15375 | 61500
14 | Control alarm Panel 4 zone | Ambetronics/N.G | 1 | Nos | 14500 | 3335 | 17835 | 17835
15 | Solenoid valve with Fittings(65MM) 24V DC | Uflow/Falocon | 1 | Nos | 7500 | 1725 | 9225 | 9225
16 | Siren Flash / Hooter 24V DC | agni | 1 | Nos | 1250 | 287.5 | 1537.5 | 1537.5
17 | Armoured cable 3C x 1.5mm | Polycabe | 50 | Mtr. | 140 | 32.2 | 172.2 | 8610
Total (Basic) | [7 empty] | 261830.1