## ELE LOAD SHEET
NOIDA INTERNATIONAL LOUNGE
SUMMARY FOR ELECTRICAL LOAD
REVISION: R1, DATE: 2024.12.24
Sr.No. | DESCRIPTION | WATTAGE (W) | No of Units/Area | CONNECTED LOAD | MAX. DMD LOAD | DIVERSITY | UPS LOAD
1 | LIGHTING LOAD (1.25W/SQ.FT) | 1.25 | 2044.4 | 2.5555 | 2.5555 | 100% | 0.38332
2 | RAW POWER LOAD (1.0W/SQ.FT) | 1 | 2044.4 | 2.0444 | 1.2266 | 60% | 0.184
3 | ELV LOAD |  |  | 2 | 2 | 100% | 0.3
4 | KITCHEN EQUIPMENTS |  |  | 58.725 | 46.98 | 80%
5 | HVAC LOAD
a | 4300CFM AHU | 2200 | 1 | 2.2 | 1.76 | 80%
b | 1700CFM Kitchen Fresh air fan | 1100 | 1 | 1.1 | 0.88 | 80%
c | 2000CFM Kitchen Exhaust fan | 1100 | 1 | 1.1 | 0.88 | 80%
6 | MISCELLANEOUS |  |  | 3 | 1.5 | 50%
| TOTAL LOAD IN KW |  |  | 72.7249 | 57.7821 |  | 0.484
| TOTAL LOAD IN KVA |  |  | 80.8054 | 64.2024
UPS CALCULATIONS
| Total C & S Load | [5 empty] | 0.484
| TOTAL EMERGENCY LOAD 15% of total lighting load | [5 empty] | 0.38332
| Total Emergency / Critical Load (kW) | [5 empty] | 0.86732
| 20% Spare Load | [5 empty] | 0.17346
| Grand total Load (kW) | [5 empty] | 1.0408
| Total Load (kVA) @ 0.9 PF | [5 empty] | 1.1564
| Recommended UPS rating (KVA) -1PH. I/C & O/G .(with Plus Minus 5%) | [5 empty] | 3
| Nearest size available--(1#3KVA) | [5 empty] | 3
SIZING OF CAPACITOR BANK (KVAR)
| PF-1 = Actual Power Factor |  |  |  |  | 0.9
| PF-2 = Target Power Factor |  |  |  |  | 0.99
| P= Total Power (kW) |  |  |  |  | 57.7821
Qc = P * {tan [acos (pf1)] - tan [ acos (pf2)]}
| Qc = Required Capacitor output (kVAr) |  |  |  |  | 19.7517
Hence We considered 20 kVAr – 4 step APFC panel ( 10+5+2.5+2.5 kVAr )

## Sheet1
Area Code | ITEM NO. | DESCRIPTION | OVERALL SIZE | QTY | Make | Model | ELECTRICAL | [5 empty] | PLUMBING / DRAINAGE | [5 empty] | LPG / PNG |  |  |  | EXHAUST CFM | REMARK
|  |  | All Dimensions in MM L x W x H |  |  |  | HP | Watts | Electrical Load In KW | Phase | Amps | Type Of Socket | Hot ( mm Ø ) | Cold ( mm Ø ) | RO ( mm Ø ) | Optimum Pressure Psi / Bar | Waste ( mm Ø ) | Tape Model Number/Make | Type of Burner | No Of Burner | Consumption Per Burner Per Hour | BTU Per Burner Per Hour |  |  | R PHASE | Y PHASE | B PHASE
Main Kitchen | MK - 01 | Hot Holding Cabinet -To accommodate 12 GN Pans | 659 x 883 x 1455 | 1 | Hatco | FSHC - 12W1 |  | 1650 | 1.6 | 230V 1 PH | 20 | Industrial | [12 empty] | 1.6
Main Kitchen | MK - 02 | Vertical Two Door Chiller | 700 x 880 x 2043 | 1 | BlueStar | RC2D700GP |  | 250 | 0.25 | 230V 1 PH | 16 | Industrial | [13 empty] | 0.25
Main Kitchen | MK - 03 | Vertical Two Door Chiller | 700 x 880 x 2043 | 1 | BlueStar | RC2D700GP |  | 250 | 0.25 | 230V 1 PH | 16 | Industrial | [14 empty] | 0.25
Main Kitchen | MK - 04 | Vertical Two Door Chiller | 700 x 880 x 2043 | 1 | BlueStar | RC2D700GP |  | 250 | 0.25 | 230V 1 PH | 16 | Industrial | [12 empty] | 0.25
Main Kitchen | MK - 05 | Work Table With Sink and Part 2 U/S | 1100 x 500 x 850 + 150 | 1 | CUSTOM FABRICATED | [7 empty] | 12 | 12 |  |  | 100 | EX-8DF10
Main Kitchen | MK - 06 | Idli Steamer | 54 Idlis Capacity | 1 | CUSTOM FABRICATED |  |  |  | 3 | 230V 1 PH | 20 | Industrial | [13 empty] | 3
Main Kitchen | MK - 07 | Two Door Work Top Chiller ( Compressor On RHS ) | 1365 x 700 x 850 | 1 | Blue Star | UC2100GP | 1/2 HP | 0.375 | 0.375 | 230V 1 PH | 15 | Normal | [14 empty] | 0.375
Main Kitchen | MK - 08 | Over Head Shelves - Ceiling Suspended | 1365 x 350 x 450 + 300 | 1 | CUSTOM FABRICATED
Main Kitchen | MK - 09 | Microwave Oven (23 Litres Capacity) | 512 x 403 x 310 | 1 | Menumaster | RMS510DS |  | 1500 | 1.5 | 230V 1 PH | 15 | Normal | [12 empty] | 1.5
Main Kitchen | MK - 10 | Hot Bain Marie (1/1 GN Pan x 3) | 1365 x 700 x 850 | 1 | CUSTOM FABRICATED |  |  |  | 3 | 230V 1 PH | 20 | Industrial | [13 empty] | 3
Main Kitchen | MK - 11 | Over Head Shelves - Ceiling Suspended | 1365 x 350 x 450 + 300 | 1 | CUSTOM FABRICATED
Main Kitchen | MK - 12 | Knee Operated Hand Wash Sink | 450 x 450 x 850 + 150 | 1 | Aluids | C9300-1-G-1 KVC | [6 empty] | 12 | 12 |  |  | 100
DishWash | DW - 01 | Soiled Dish Landing Table With Glass Rack Shelf | 1250 x 750 x 850 + 150 | 1 | CUSTOM FABRICATED | [11 empty] | 100
| DW - 02 | Pre Rinse 2 Sink Unit | 1200 x 740 x 850 + 150 | 1 | CUSTOM FABRICATED | [7 empty] | 12 | 12 |  |  | 100
| DW - 03 | Pre - Rinse Faucet |  | 1 | T & S | EX-1DP12-H
DishWash | DW - 04 | Hood Type Dish Washer (Electrically Operated) | IMPORTED | 1 | Electrolux / DHIR |  |  | 9 | 9 | 415V 3PH | 32 | Industrial |  | 12 |  |  | 100
DISHWASHER ACCESSORIES
|  | Pump for Wash Cycle (Aqua Make) |  | 1 |  | AD0A00401
|  | Pump for Rinse (Aqua Make) |  | 1 |  | AD01001030B
|  | Liquid Soap – Powerkleen | 35 Litres Capacity | 1
|  | Soap – Powerinze | 35 Litres Capacity | 1
|  | Basket – Plate Racks |  | 3
|  | Basket – Cutlery Rack |  | 6
|  | Basket – Glass Rack |  | 3
|  | Extender for Glass Rack |  | 3
DishWash | DW - 05 | Unloading Table | 1100 x 740 x 850 + 150 | 1 | CUSTOM FABRICATED
DishWash | DW - 06 | Clean Dish Rack | 1000 x 500 x 1800 | 1 | CUSTOM FABRICATED
DishWash | DW - 07 | Clean Dish Rack | 1000 x 500 x 1800 | 1 | CUSTOM FABRICATED
| DW - 08 | Ice Cube Machine | 500 x 580 x 800 | 1 | Icematic | C54 |  | 1167 | 1.167 | 230V 1 PH | 16 | Industrial |  |  | 12 |  | 100 | [9 empty] | 1.167
LIVE KITCHEN
Live Kitchen | LK - 01 | Two Door Work Top Chiller ( Compressor On RHS ) | 1365 x 700 x 850 | 1 | Blue Star | UC2100GP | 1/2 HP | 0.375 | 0.375 | 230V 1 PH | 15 | Normal | [12 empty] | 0.375
Live Kitchen | LK - 02 | Wall Shelf | 1365 x 300 | 1 | CUSTOM FABRICATED
Live Kitchen | LK - 03 | Induction | 330 x 430 x 75 | 1
Live Kitchen | LK - 04 | Work Table With Sink And Part 2 U/S | 1250 x 700 x 850 + 150 | 1 | CUSTOM FABRICATED
Live Kitchen | LK - 05 | Dry Garbage Bin | 584 x 304 x 765 | 1 | FRONTIER POLYMERS PVT. LTD. | FLB SLIM
Live Kitchen | LK - 06 | Grease Trap - 7 KG Grease Capacity | 404 x 337 x 303 | 1 | Nugreen | NGT 14
Live Kitchen | LK - 07 | Table Top Automatic Juice Extractors J 80 | 235 x 535 x 500 | 1 | Robot Coupe | J 80 |  | 700 | 0.7 | 230V 1 PH | 16 | Industrial | [13 empty] | 0.7
Live Kitchen | LK - 08 | Work Table With 2 U/S | 1425 x 650 x 850 | 1 | CUSTOM FABRICATED
Live Kitchen | LK - 09 | Induction Top | 410 x 380 x 95 | 1 | Stella | TS- 3501 |  |  | 3.5 | 230V 1 PH | 16 | Industrial | [14 empty] | 3.5
Live Kitchen | LK - 10 | Hot Bain Marie (1/1 GN Pan) - Table Model | 650 x 425 x 300 | 1 | CUSTOM FABRICATED |  |  |  | 2 | 230V 1 PH | 16 | Industrial | [12 empty] | 2
Live Kitchen | LK - 11 | Table Top Automatic Juice Extractors J 80 | 235 x 535 x 500 | 1 | Robot Coupe | J 80 |  | 700 | 0.7 | 230V 1 PH | 16 | Industrial | [13 empty] | 0.7
Live Kitchen | LK - 12 | Cold Bain Marie With Drawer Chiller Below | 1200 X 650 X 850 | 1 | CUSTOM FABRICATED |  | .75 HP | 0.56 | 0.56 | 230V 1 PH | 15 | Normal | [14 empty] | 0.56
Live Kitchen | LK - 13 | Spare number
Live Kitchen | LK - 14 | Open Deck Chiller with out Glass Door | 1285 x 750 x 1930 | 1 | Blue Star | KORAL12CFV/DL/MT |  |  | 1 | 230V 1 PH | 15 | Normal | [12 empty] | 1
|  | TOTAL | [22 empty] | 6.725 | 7.65 | 5.852
Buffet | BS - 01 | Water Dispencer |  | 1
Buffet | BS - 02 | Glass Rack (Below The Counter) |  | 1 | Interior Contractor Scope
Buffet | BS - 03 | Juice Dispenser ( Table Top Model) |  | 1
Buffet | BS - 04 | Conveyor Toaster |  | 1
Buffet | BS - 05 | Milk Storage | 228 x 469 x 344 | 1 | Kappi Machines | Seitek BC9CN |  | 400 | 0.4 | 230V 1 PH | 15 | Normal | [13 empty] | 0.4
Buffet | BS - 06 | Coffee Machine - Automatic | 380 x 560 x 690 | 1 | Kappi Machines | Kalrem X 685 |  | 2700 | 2.7 | 230V 1 PH | 20 | Industrial |  |  | 12 |  | 100 | [9 empty] | 2.7
Buffet | BS - 01 | Induction ( Sunk - In Type) | 340 x 340 x 75 | 1 | Stella | TS - 678 |  | 320 | 3.2 | 230V 1 PH | 15 | Normal | [12 empty] | 3.2
Buffet | BS - 02 | Induction ( Sunk - In Type) | 340 x 340 x 75 | 1 | Stella | TS - 678 |  | 320 | 3.2 | 230V 1 PH | 15 | Normal | [13 empty] | 3.2
Buffet | BS - 03 | Induction ( Sunk - In Type) | 340 x 340 x 75 | 1 | Stella | TS - 678 |  | 320 | 3.2 | 230V 1 PH | 15 | Normal | [14 empty] | 3.2
Buffet | BS - 04 | Induction ( Sunk - In Type) | 340 x 340 x 75 | 1 | Stella | TS - 678 |  | 320 | 3.2 | 230V 1 PH | 15 | Normal | [12 empty] | 3.2
Buffet | BS - 05 | Induction ( Sunk - In Type) | 340 x 340 x 75 | 1 | Stella | TS - 678 |  | 320 | 3.2 | 230V 1 PH | 15 | Normal | [13 empty] | 3.2
Buffet | BS - 06 | Electrical Dual Heat Lamp | 500 x 700 x | 1
Buffet | BS - 07 | Soup Turren / Sambhar
Buffet | BS - 08 | Sunk - In Cold Well With 2 Oh/ Sh For Dessert | 900 x 600 x | 1
Buffet | BS - 09 | Sunk - In Cold Well With 2 Oh/ Sh For Dessert | 900 x 600 x | 1
|  | TOTAL | [22 empty] | 6.4 | 6.8 | 5.9
Drain Grating
| DG -01 | SS Drain Grating | 350 x 350 | 5 | CUSTOM FABRICATED
Corner Guard
| CG-01 | S/S Corner Guard | 1200 Ht. | 3 | CUSTOM FABRICATED
Exhaust Hood
| EX-01 | Exhaust Hood With SS Filters | 1000 x 1000 x 500 | 1 | CUSTOM FABRICATED
OTHER ITEM
| EXT1 | Water Boiler (Geyser) | 35 Lits. Capacity | 1 |  |  |  | 3000 | 3 | 230V 1 PH | 20 | Industrial |  | 12 | [12 empty] | 3
| EXT2 | Air Curtain | BRANDED : 900mm Length |  | TECHNOCRAT |  | 1/2 HP | 0.375 | 0.375 | 230V 1 PH | 15 | Normal | [12 empty] | 0.375
| EXT3 | Insect Killer | BRANDED | 1 | TECHNOCRAT |  | 1/2 HP | 0.75 | 0.75 | 230V 1 PH | 15 | Normal | [13 empty] | 0.75
| EXT4 | Garbage Bins |  |  | Neelkamal
| EXT5 | Exhaust System
| EXT6 | Fresh - Air System
BAR AREA
| BA - 01 | Sunk - in Sink Bowl | 300 x 300 x 250 | 1 | CUSTOM FABRICATED
| BA - 02 | Under Counter Glass Washer | 450 x 575 x 700 | 1 | Electrolux | NGWDPDD |  | 3500 | 3.5 | 230V 1 PH | 20 | Industrial |  | 12 |  |  | 100 | [7 empty] | 3.5
| BA - 03 | Two Door Back Bar Bottle Cooler | 900 x 520 x 900 | 1 | Blue Star | BC250A | 1/2 HP | 0.373 | 0.373 | 230V 1 PH | 15 | Normal | [14 empty] | 0.373
| BA - 04 | Blender | 240 x 250 x 460 | 1 | JTC | TM -800 AQ |  | 1200 | 1.2 | 230V 1 PH | 15 | Normal | [13 empty] | 1.2
| BA - 05 | Blender | 240 x 250 x 460 | 1 | JTC | TM -800 AQ |  | 1200 | 1.2 | 230V 1 PH | 15 | Normal | [13 empty] | 1.2
| BA - 06 | Bear Kegs |  | 2
| BA - 07 | Beer Chilling Machine | 450 x 450 x 800 | 1 | Elanpro | HE 120 |  |  |  | 230V 1 PH | 15 | Normal
| BA - 08 | Bear Tap
| BA - 09 | Cocktail Station | 750 x 575 x 800 + 50 | 1 | CUSTOM FABRICATED | [11 empty] | 100
|  | TOTAL | [6 empty] | 58.725 | [15 empty] | 3.875 | 3.15 | 3.373