## Summ
SUMMARY OF COST OF INTERIOR -ELECTRICAL & ELV WORK - NOIDA INTERNATIONAL LOUNGE
SR. | DESCRIPTION | TENDER AMOUNT (Rs.)
NO. | OF ITEM |  | MAT. | INST. | TOTAL
1 | PANELS / DBs | Rs. | 0 | 0 | 0
2 | CABLES : | Rs. | 0 | 0 | 0
3 | POINT WIRING : | Rs. | 0 | 0 | 0
4 | RACEWAYS, CABLE TRAYS & JUNCTION BOX | Rs. | 0 | 0 | 0
5 | LIGHT FIXTURES INSTALLATION | Rs. | 0 | 0 | 0
6 | EARTHING : | Rs. | 0 | 0 | 0
7 | Miscellaneous Item | Rs. | 0 | 0 | 0
8 | DATA DISTRIBUTION | Rs. | 0 | 0 | 0
9 | SUPPLY & INSTALLATION OF SAFETY ITEMS | Rs. | 0 | 0 | 0
10 | UPS/ INVERTER System: | Rs. | 0 | 0 | 0
11 | CCTV | Rs. | 0 | 0 | 0
12 | PA SYSTEM | Rs. | 0 | 0 | 0
13 | FIRE ALARM SYSTEM | Rs. | 0 | 0 | 0
| TOTAL | Rs. | 0 | 0 | 0
NOTE:- | GST Extra
Exclusions:
1. Passive data network devices and active networking components are excluded.
2. Epabx & Telephone instruments are excluded.
3. SERVER is excluded.
4. Light Fixture- Supply Excluded.

## TENDER BOQ
BILL OF QUANTITY FOR ELECTRICAL WORK FOR NOIDA INTERNATIONAL LOUNGE
TENDER BOQ. R0
SR. | DESCRIPTION OF ITEM | UNIT | QTY | UNIT RATE (Rs.) |  | AMOUNT (Rs.)
NO. |  |  |  | MAT. | INST. | MAT. | INST. | TOTAL
1 | PANELS / DBs
Supply and Installation of main LT panel,genarally conforming to IS 8623/IS-13947/IEC-439 front operated, dead back floor mounted , totally enclosed, compartmentalised, vermin proof,indoor, non-drawout type,power panel, fabricated out of 2/1.6mm thick CRCA sheets, fully powder coated after seven tank treatment, having gasketed & hinged cover on each cubicle with insulated door knob, incorporating horizontal and vertical copper busbars complete with all internal wiring, danger sign board, earth-bus and lugs, cable chamber, busbar chamber,aluminium anodized name plates etc.as required, including 2 nos. of 6" dia instrument cooling fan with switch and ventilation louvres with wire mesh,housing below mentioned switchgears / meters. 9W fitting with CFL lamp, switch shall be provided in each vertical section,:(Panel should conform to Form- 3b of IEC- 439) (GA drawing of the panel to be got approved from the Consultant before taking up fabrication and all panels to be factory inspected before despatch)
Notes: 1. All MCCBs shall have rotary handle
2. All MCCBs shall have phase spreader assembly on
both Line & Load ends.
3. All MCCB shall have Minimum Ics=Icu
4. Incomer shall have auxilliary ON/OFF & TRIP status contacts and the same shall be wired up
electronic trip setting to Metering Compartment)
5. The panel shall conform to Form-3b as per IEC-439
6. All MCCB to be of Schneider/ABB make
7. All MCCB to be current limiting type, LSIG
8. Incomer MCCB to be shunt trip facility
7. With DOL Starter 1.1KW & 1.1KW for air washer & exhaust fan
8. With VFD for 1.1KW & 1.1KW for air washer & exhaust fan make Selec
Refer: SLD
1.1.1 | MAIN PANEL | Set | 1 |  |  | 0 | 0 | 0
1.2 | Suply and installation of Four -Tier, Multi-Way, TPN,
Distribution Board for Lighting & Power distribution, surface
mounted on wall, sheet metal fabricated,powder coated,
having dust-proof and vermin 'proof, gasketed and hinged
acrylic door with all internals such as DIN rails, neutral-link,
interconnected wiring complete with earthing lugs housing
switchgears: (IP-43 with Metal Door) Refer: SLD & DB Schedule
(Make: Legrand-Ekinoxe /Schneider)
1.2.1 | APFC panel of 20 kVAR capacity. The capacitors shall be of 'Heavy Duty APP' type, rated for 440 V, 50 Hz. and with capacitor duty contactors. Complete with an 4-step APFC relay. The steps shall be 10-5-2.5-2.5 kVAR. The APFC panel shall be having provision for Auto-Manual operation. The panel shall be conforming to IS- 13585, 1994. The metering section shall be consisting of ammeter and voltmeter with selector switches.(The APFC shall be intigrated with main panel) | No. | 1
1.2.2 | KITCHEN DB 1 (12WAY TPN) | Set | 1 |  |  | 0 | 0 | 0
1.2.3 | KITCHEN DB 2 & (2+6WAY TPN) | Set | 2 |  |  | 0 | 0 | 0
1.2.4 | LPDB 1 (2+12WAY TPN) | Set | 1 |  |  | 0 | 0 | 0
1.2.5 | UPSDB (16WAY SPN) | Set | 1 |  |  | 0 | 0 | 0
1.4 | S & I of 63A, TPN, MCB type Isolator + 415 V, Industrial Power socket in powder coated metal box for supplying power to AC equipment etc. IP65 | Nos | RO |  |  | 0 | 0 | 0
1.5 | S & I of 16A, TPN, MCB type Isolator + 415 V, Industrial Power socket in powder coated metal box for supplying power to AC equipment etc. IP65 | Nos | 2 |  |  | 0 | 0 | 0
1.6 | S & I of 40A, TP, MCB + 415 V, in powder coated sheet metal box for terminating UPS to UPS DB etc. | Nos | 2 |  |  | 0 | 0 | 0
1.7 | S & I of 32A,TP ELCB + 415 V, Industrial Power socket in powder coated metal box for supplying power to Kitchen equipment etc. IP65 | Nos | 1 |  |  | 0 | 0 | 0
1.8 | S & I of 16A,TP ELCB + 220 V, Industrial Power socket in powder coated metal box for supplying power to Kitchen equipment etc. IP65 | Set | 8 |  |  | 0 | 0 | 0
1.9 | S & I of 20A,TP ELCB + 220 V, Industrial Power socket in powder coated metal box for supplying power to Kitchen equipment etc. IP65 | Nos | 6 |  |  | 0 | 0 | 0
1.1 | S & I of 25 ELCB 300mA, Metal clad,Power socket in powder coated metal box for supplying power to AC etc. IP65 | Nos | 1 |  |  | 0 | 0 | 0
| Sub Total of 1.0 |  |  |  |  | 0 | 0 | 0
2 | CABLES :
2.1 | Supply and laying, effecting proper connections, testing & commissioning of the following sizes of 1.1 KV XLPE armoured/ unarmoured GI insulated GI sheathed aluminium /copper conductor cables conforming to IS : 1554 and IS 694 for Flexible copper cable Part I - 1976 with latest amendments laid over MS supports in existing RCC ducts/ laid in ground /laid on Cable Trays including clamping the cables to supports in an approved manner as required complete with all accessories.All cables shall have thermo setting insulation XLPE and low emission of smoke and corrosive gas when affected by fire. Necessary Markers shall be provided at the intervals as per the specifications.
2.1.1 | 3.5C x 120 Sq.mm. AL Cable | R.M | RO |  |  | 0 | 0 | 0
2.1.2 | 3.5C x 95 Sq.mm. AL Cable | R.M | RO |  |  | 0 | 0 | 0
2.1.3 | 3.5C x 70 Sq.mm. AL Cable | R.M | RO |  |  | 0 | 0 | 0
2.1.4 | 3.5C x 50 Sq.mm. AL Cable - MAIN PANEL | R.M | 80 |  |  | 0 | 0 | 0
2.1.5 | 3.5C x 35 Sq.mm. AL Cable | R.M | RO |  |  | 0 | 0 | 0
2.1.6 | 3.5C x 25 Sq.mm. CU Cable | R.M | RO |  |  | 0 | 0 | 0
2.1.7 | 4C x 16 Sq.mm. CU Cable - KPDB1,KPDB2 & KPDB3 | R.M | 50 |  |  | 0 | 0 | 0
2.1.8 | 4C x 10 Sq.mm. CU Cable | R.M | RO |  |  | 0 | 0 | 0
2.1.9 | 4C x 6 Sq.mm. CU Cable - LPDB-1, DISHWASHER | R.M | 40 |  |  | 0 | 0 | 0
2.1.10 | 4C x 4 Sq.mm. CU Cable | R.M | RO |  |  | 0 | 0 | 0
2.1.11 | 4C x 2.5 Sq.mm. CU Cable - AHU, EX FAN, FA FAN | R.M | 80 |  |  | 0 | 0 | 0
2.1.12 | 4C x 2.5 Sq.mm. CU Cable | R.M | 40 |  |  | 0 | 0 | 0
2.1.13 | 3C x 16 Sq.mm. CU able | R.M | RO |  |  | 0 | 0 | 0
2.1.14 | 3C X 6sq.mm CU Cable - UPS, UPS DB | R.M | 50 |  |  | 0 | 0 | 0
2.1.15 | 3C X 4sq.mm CU Cable | R.M | 20 |  |  | 0 | 0 | 0
2.1.16 | 3C x 2.5 Sq.mm. CU Cable | R.M | 10 |  |  | 0 | 0 | 0
2.1.17 | 3C X 4sq.mm CU GI Cable | R.M | RO |  |  | 0 | 0 | 0
2.1.18 | 3C X 1.5sq.mm CU GI Cable | R.M | 20 |  |  | 0 | 0 | 0
2.1.19 | 1C x 70 Sq.mm, Copper, Flexible, Bunched together | Mtr. | RO |  |  | 0 | 0 | 0
2.1.20 | 1C x 4 Sq.mm, Copper, Flexible, Bunched together | Mtr. | RO |  |  | 0 | 0 | 0
2.1.21 | 2C X 2.5sq.mm CU Cable | R.M | 20 |  |  |  |  | 0
2.1.22 | 5C X 2.5sq.mm CU Cable - LCS | R.M | 20 |  |  |  |  | 0
2.2 | CABLE TERMINATION
Making cable and terminations including brass single compression glands and crimping type copper lugs for cable sizes mentioned below for aluminium or copper.
2.2.1 | 3.5C x 120 Sq.mm. AL Cable | R.M | RO |  |  | 0 | 0 | 0
2.2.2 | 3.5C x 95 Sq.mm. AL Cable | R.M | RO |  |  | 0 | 0 | 0
2.2.3 | 3.5C x 70 Sq.mm. AL Cable | R.M | RO |  |  | 0 | 0 | 0
2.2.4 | 3.5C x 50 Sq.mm. AL Cable - MAIN PANEL | R.M | 2 |  |  | 0 | 0 | 0
2.2.5 | 3.5C x 35 Sq.mm. AL Cable | R.M | RO |  |  | 0 | 0 | 0
2.2.6 | 3.5C x 25 Sq.mm. CU Cable | R.M | RO |  |  | 0 | 0 | 0
2.2.7 | 4C x 16 Sq.mm. CU Cable - KPDB1,KPDB2 & KPDB3 | R.M | 6 |  |  | 0 | 0 | 0
2.2.8 | 4C x 10 Sq.mm. CU Cable | R.M | RO |  |  | 0 | 0 | 0
2.2.9 | 4C x 6 Sq.mm. CU Cable - LPDB-1, DISHWASHER | R.M | 2 |  |  | 0 | 0 | 0
2.2.10 | 4C x 4 Sq.mm. CU Cable | R.M | RO |  |  | 0 | 0 | 0
2.2.11 | 4C x 2.5 Sq.mm. CU Cable - AHU, EX FAN, FA FAN | R.M | 6 |  |  | 0 | 0 | 0
2.2.12 | 4C x 2.5 Sq.mm. CU Cable | R.M | 40 |  |  | 0 | 0 | 0
2.2.13 | 3C x 16 Sq.mm. CU able | R.M | RO |  |  | 0 | 0 | 0
2.2.14 | 3C X 6sq.mm CU Cable - UPS, UPS DB | R.M | 2 |  |  | 0 | 0 | 0
2.2.15 | 3C X 4sq.mm CU Cable | R.M | 2 |  |  | 0 | 0 | 0
2.2.16 | 3C x 2.5 Sq.mm. CU Cable | R.M | 2 |  |  | 0 | 0 | 0
2.2.17 | 3C X 4sq.mm CU GI Cable | R.M | RO |  |  | 0 | 0 | 0
2.2.18 | 3C X 1.5sq.mm CU GI Cable | R.M | 2 |  |  | 0 | 0 | 0
2.2.19 | 1C x 70 Sq.mm, Copper, Flexible, Bunched together | Mtr. | RO |  |  | 0 | 0 | 0
2.2.20 | 1C x 4 Sq.mm, Copper, Flexible, Bunched together | Mtr. | RO |  |  | 0 | 0 | 0
2.2.21 | 2C X 2.5sq.mm CU Cable | R.M | 3 |  |  | 0 | 0 | 0
2.2.22 | 5C X 2.5sq.mm CU Cable - LCS | R.M | 5 |  |  | 0 | 0 | 0
| Sub Total of 2 |  |  |  |  | 0 | 0 | 0
3 | POINT WIRING :
3.1 | LIGHT POINT
Sub mains / Pre-Primary wiring i.e. from DB to room switch board shall be carried out for Pre-primary point using 2.5 sqmm copper stranded. All lighting fixture, wiring shall be carried out for primary point using 2.5 sqmm copper stranded & for secondary wiring 1.5sqmm copper stranded conductor 660/1100V grade PVC FRLSH insulated wire in "GI Conduits" (including flexible conduits for drops to light fittings)". Individual junction / inspection boxes shall be provided for each lighting fitting for the purpose of looping from fitting to fitting.
also including insulated green color copper earth wire for each circuit and providing modular grid plate type switches,sockets etc. as required. Each light point to be terminated using 5A connector or 5A two pin female socket (for cove lighting) as directed at site. Each circuit feeding not more than 12-8 points/800 watts as per following configuration:(LDBs located at two locations as shown) (The Switch Socket cost shall be paid separately.)
From distribution board to switch board will be termed as Pre-primary point, average wiring length for Pre-primary point to be considered as 15 metres. From switch board to first light fitting and switch board to switch board will be termed as primary point, average wiring length for primary point to be considered as 6 metres and First fitting to subsequent fitting on the same circuit shall be termed as secondary point, average wiring length for secondary point to be considered as 3 metres. Light point wiring shall be included submains wiring from D.B. to room switch board.
Note: Length may vary as per actual site condition. Vendor shall be crossverify before bidding.
3.1.1 | Pre-Primary point (sub mains point) | Nos | 22 |  |  | 0 | 0 | 0
3.1.2 | Primary point | Nos | 15 |  |  | 0 | 0 | 0
3.1.3 | Secondary Point | Nos | 50 |  |  | 0 | 0 | 0
3.2 | LIGHT POINT- for AUTOMATION
All lighting fixture, wiring shall be carried out for primary point using 1.5 sqmm copper stranded & for secondary wiring 1.5sqmm copper stranded conductor 660/1100V grade PVC FRLSH insulated wire in "GI Conduits" & 1 pair 1.5sqmm jacketed cable in Separate Conduit (including flexible conduits for drops to light fittings)". Individual junction / inspection boxes shall be provided for each lighting fitting for the purpose of looping from fitting to fitting.
From DB to first light fitting/driver will be termed as primary point, average wiring length for primary point to be considered as 20 metres and First fitting to subsequent fitting on the same circuit shall be termed as secondary point, average wiring length for secondary point to be considered as 5 metres. Light point wiring shall be included submains wiring from D.B. to room lights/Driver.
Note: Length may vary as per actual site condition. Vendor shall be crossverify before bidding.
3.2.1 | Primary point | Nos | RO |  |  | 0 | 0 | 0
3.2.2 | Secondary Point | Nos | RO |  |  | 0 | 0 | 0
3.3 | Power Point (Utility)
Primary wiring i.e. from DB to first power point shall be carried out for primary point using 3R x 2.5 sqmm copper stranded. Secondary wiring 2.5sqmm copper stranded conductor 660/1100V grade PVC FRLSH insulated wire in "GI Conduit". Individual junction/inspection boxes shall be provided for each power point to loop from power point to a power point. Only 4 points looped in one circuit) From DB to First Socket.
From distribution board to first power point will be termed as primary point, average wiring length for primary point to be considered as 15 metres. First power point to subsequent power point on the same circuit shall be termed as secondary point, average wiring length for secondary point to be considered as 4 metres. Power point wiring shall be included wiring from D.B. to room indivisual power point.
Note: Length may vary as per actual site condition. Vendor shall be crossverify before bidding.
3.3.1 | Primary point | Nos | 12 |  |  | 0 | 0 | 0
3.3.2 | Primary point ( Distance between Switch & socket Will be Average Length 2.5 Mtr. ) | Nos | RO |  |  | 0 | 0 | 0
3.3.3 | Secondary Point | Nos | 18 |  |  | 0 | 0 | 0
3.4 | Power Point (Kitchen & BAR)
Primary wiring i.e. from DB to first power point shall be carried out for primary point using 3R x 4 sqmm copper stranded. & Also used 3R x 2.5sqmm copper stranded. Secondary wiring 4 sqmm copper stranded conductor 660/1100V grade PVC FRLSH insulated wire in "GI Conduit". Individual junction/inspection boxes shall be provided for each power point to loop from power point to a power point. Only 4 points looped in one circuit) From DB to First Socket.
From distribution board to first power point will be termed as primary point, average wiring length for primary point to be considered as 22 metres. First power point to subsequent power point on the same circuit shall be termed as secondary point, average wiring length for secondary point to be considered as 1 metres. Power point wiring shall be included wiring from D.B. to room indivisual power point.
Note: Length may vary as per actual site condition. Vendor shall be crossverify before bidding.
3.4.1 | Primary point | Nos | 35 |  |  | 0 | 0 | 0
3.4.2 | Primary point ( Distance between Switch & socket Will be Average Length 2.5 Mtr. ) | Nos | RO |  |  | 0 | 0 | 0
3.4.3 | Secondary Point | Nos | 12 |  |  | 0 | 0 | 0
3.5 | S & I of GI conduits including all accessories, clamps, spacers, bends, tee, cross etc. as required at site for miscellaneous use in following sizes:
3.5.1 | 20mm dia | Mtr | RO |  |  | 0 | 0 | 0
3.5.2 | 25mm dia | Mtr | 80 |  |  | 0 | 0 | 0
3.6 | S & I of flexible GI conduits including all accessories, clamps, spacers, end adopters (Glands) etc. as required at site in following sizes:
3.6.1 | 20mm dia | Mtr | RO |  |  | 0 | 0 | 0
3.6.2 | 25mm dia (COMMON) | Mtr | 50 |  |  | 0 | 0 | 0
3.7 | Supply, Installation testing and commission of 240V-AC, wiring devices and its accessories such as modular shuttered type switch socket outlets with modular front plate, on Suitable MS box, G.I. back box and all required accessories etc. Supply & Installation scope includes all civil works related to this job such as chiselling , making good with concrete and plaster, supply of fixing screw / wall plugs and other necessary hardware, marking identification numbers of circuits & interconnections of the switch /sockets as per standard drawing, complete as per site requirement. Switches and sockets may be individual or combined with bigger lighting switchboards, contractor to refer drawings to understand exact scope of work. LEGRAND
3.7.1 | 6A One way plate type switch | Nos. | 12 |  |  | 0 | 0 | 0
3.7.2 | 6A Two way plate type switch | Nos. | RO
3.7.3 | 1nos. C CABLE PORT(SB1) | Nos. | 4
3.7.4 | 1no. 6/16A SOCKET & SWITCH + 1nos. C CABLE PORT(SB2) | Sets | 13 |  |  | 0 | 0 | 0
3.7.4 | 6/16A SOCKET & SWITCH POWER (SB3) | Sets | 2 |  |  | 0 | 0 | 0
3.7.5 | 2no. 6A SOCKET & 1no. 16A SOCKET + SWITCH FOR UPS POWER + 2nos DATA + TELEPHONE(SB4) | Sets | 1 |  |  | 0 | 0 | 0
3.7.6 | 6/16A SOCKET & SWITCH POWER + 1nos. C CABLE PORT(SB5) | Sets | 6 |  |  | 0 | 0 | 0
3.7.8 | 15A SOCKET & SWITCH POWER-KITCHEN EQIPMENTS | Sets | 18 |  |  | 0 | 0 | 0
3.7.9 | 20A SOCKET & SWITCH POWER-KITCHEN | Sets | RO |  |  | 0 | 0 | 0
3.7.10 | LED SCREEN | Nos. | RO
3.7.11 | data cum telephone back GI BACK box 2”x2” suitable for data socket | Nos. | 1
3.7.12 | USB Point | Nos. | RO |  |  | 0 | 0 | 0
| Sub Total of 3.0 |  |  |  |  | 0 | 0 | 0
4 | RACEWAYS, CABLE TRAYS & JUNCTION BOX
4.1 | S & I of GI trunking same as above but of size 100mm x 40mm x1.6 mm for power cables.(Electrical Room) | Mtr | RO |  |  | 0 | 0 | 0
(PROFAB/ASIAN/Approved equivalent)
4.2 | S & I of trunking same as above but of size 85mm x 38mm x1.6 mm thick for power/data cables. | Mtr | RO |  |  | 0 | 0 | 0
4.3 | S & I of trunking same as above but of size 65mm x 38mm x1.6 mm thick for power/data cables. | Mtr | RO |  |  | 0 | 0 | 0
(PROFAB/ASIAN/Approved equivalent)
4.4 | S & I of 1 Run x 25mm dia, Conduit in Floor. | Mtr | 120 |  |  | 0 | 0 | 0
4.5 | S & I of floor junction boxes similar to above but size 350mm x 350mm x 60 mm | Nos | RO |  |  | 0 | 0 | 0
4.6 | S & I of floor junction boxes similar to above but size 250mm x 250mm x 60 mm | Nos | RO |  |  | 0 | 0 | 0
4.7 | S & I of floor junction boxes similar to above but size 150mm x 150mm x 60 mm | Nos | 10 |  |  | 0 | 0 | 0
4.8 | S & I of GI Pregalvanizd Perforated type Cable Tay
of following sizes suspended from ceiling or fixed
vertically on wall/column as per route directed at site
including all necessary bends, tees, crosses and also
including all necessary supporting arrangement.
All supporting hardware including nuts, bolts etc.
shall be also of galvanised M.S. as approved
(PROFAB/INDIANA/ASIAN/approved equivalent)
4.8.1 | 100mm x 50mm x 1.6mm | Mtr | 15 |  |  | 0 | 0 | 0
4.8.2 | 300mm x 50mm x 1.6mm | Mtr | 15 |  |  | 0 | 0 | 0
4.8.3 | 450mm x 50mm x 2.0mm | Mtr | RO |  |  | 0 | 0 | 0
| Sub Total of 4.0 |  |  |  |  | 0 | 0 | 0
5 | LIGHT FIXTURES INSTALLATION
5.1 | Installation of lighting fixtures with lamps as per the details below including necessary hardware such as clamps, nuts, bolts, nails screws and suspension rods as required for fixing the fixtures in position as directed by architect / consultant at site.
5.1.1 | CEILING MOUNTED ADJUSTABLE SPOT 12W | Nos | 20 |  |  | 0 | 0 | 0
5.1.2 | CEILING MOUNTED ADJUSTABLE SPOT 12W | Nos | 27 |  |  | 0 | 0 | 0
5.1.3 | CEILING MOUNTED COB 12W | Nos | 7 |  |  | 0 | 0 | 0
5.1.4 | DECORATIVE WALL MOUNTED | Nos | 2 |  |  | 0 | 0 | 0
5.1.5 | DECORATIVE WALL MOUNTED | Nos | 1 |  |  | 0 | 0 | 0
5.1.6 | DECORATIVE CEILING SUSPENDED | Nos | 1 |  |  | 0 | 0 | 0
5.1.7 | LED STRIP LIGHT | Mtr | 38 |  |  | 0 | 0 | 0
5.1.8 | PANEL LIGHT | Nos | 6 |  |  | 0 | 0 | 0
5.1.9 | SINGNAGE | Nos | 2 |  |  | 0 | 0 | 0
| Sub Total of 5.0 |  |  |  |  | 0 | 0 | 0
6 | EARTHING :
6.1 | S & I of earth pit comprising of specially designed SEE/Ashlok brand Earth Electrode system 3.00 meter long including necessary materials like side fill compound etc. as required with standard brick masonary chamber with hinged cover and watering arrangement model SEE-60/C with SFC-20/Equivalent ASHLOK MODEL T39 HD (50MM DIA. 3 MTR) | Nos | 2 |  |  | 0 | 0 | 0
6.2 | S & I of copper /GI earthing wires/strips in following sizes
6.3 | 8 SWG GI bare wire | Mtr | 150 |  |  | 0 | 0 | 0
6.4 | 8 SWG CU bare wire | Mtr | 30 |  |  | 0 | 0 | 0
6.5 | 25mm x 3mm thick GI strip welded & painted green | Mtr | RO |  |  | 0 | 0 | 0
6.6 | 25mm x 6mm thick GI strip welded & painted green | Mtr | 60 |  |  | 0 | 0 | 0
6.7 | S & I of isolated/dedicated earthing / grounding system for computers etc.using insulated green-yellow copper earthing wire laid/fixed bare on wall/ceiling from separately made earth pit to the equipment in following sizes The rate shall include termination also.
6.7.1 | 6 Sqmm copper, yellow-green/green insulation | Mtr | 20 |  |  | 0 | 0 | 0
6.8 | S & I of Main bus for isolated earth comprising of 300mm x 25 mm x 3mm thick Tinned copper bar fixed on insulated support and having 10 nos of holes and nut bolts studs for clamping the earth leads,all contained in MS/GI box and having transparent acrylic cover as approved by the consultant | Nos | 1 |  |  | 0 | 0 | 0
| Sub Total of 6.0 |  |  |  |  | 0 | 0 | 0
7 | Miscellaneous Item
7.1 | Supply & Install. Of RG 6 TV Cable in 25mm GIConduit | Mtr. | 40 |  |  | 0 | 0 | 0
7.2 | Supply & Laying of RG11 use for Main Cable TV | Mtr. | 60 |  |  | 0 | 0 | 0
7.3 | Install. Of TV Stand - Only Installation | Nos. | 1 |  |  | 0 | 0 | 0
| Sub Total of 7.0 |  |  |  |  | 0 | 0 | 0
8 | DATA DISTRIBUTION
Supply, Installation, termination & testing of data system:
8.1 | Main SERVER / ROUTER | Nos. | 1 |  |  | 0 | 0 | 0
8.2 | SMART GIGABIT SWITCH 24 PORTS | Nos. | 1 |  |  | 0 | 0 | 0
8.3 | Loaded PATCH PANEL for 24 Port | Nos. | 1 |  |  | 0 | 0 | 0
8.4 | LIU switch with Accessories. (Optional : if Fibre Optic Cable terminated) | Job | 1 |  |  | 0 | 0 | 0
8.5 | Supply & Installation of I/O DATA Outlet (RJ-45) | Nos. | 21 |  |  | 0 | 0 | 0
8.6 | S & I of Installation of Wi-Fi ceiling mounted Access Point, managed by controller software | Nos. | 3 |  |  | 0 | 0 | 0
8.7 | Supply, installation, termination & testing of all Terminations using Fluke Cable Analyser DTX 1800 for all CAT 6 Information Outlet including Information outlet | Lot | RO |  |  | 0 | 0 | 0
8.8 | CABLES:
8.8.1 | S&I Optical Fiber Cable with 12 fibers, with core dia. 50/125 µm (OM3), suitable for 1GBps Ethernet distance at 850 nm of wavelength, | Mtr. | RO |  |  | 0 | 0 | 0
8.8.2 | S&I Optical Fiber Cable with 6 fibers, with core dia. 50/125 µm (OM3), suitable for 1GBps Ethernet distance at 850 nm of wavelength, | Mtr. | RO |  |  | 0 | 0 | 0
8.8.3 | Supply & providing of CAT 6 UTP cables in the laid raceways/Conduits including terminations | Mtr. | 195 |  |  | 0 | 0 | 0
8.8.4 | Patch cord (2 mtr-user end) | Each | 21 |  |  | 0 | 0 | 0
8.9 | Supply, Installation, Testing & Commissioning of Velcro Ties ( 22 Mtrs = 1 Roll) | Roll | 1 |  |  | 0 | 0 | 0
8.10. | Supply, Installation, Testing & Commissioning of Cable Ties 200mm ( 100 Nos. Pkt) | Pkt. | 1 |  |  | 0 | 0 | 0
8.11 | Project Management including Freight & Forwarding, Cable Bunching, Printed Numbering, tube type Ferruling both sides, Face plate, Patch panel & patch cords both sides, Documentation etc.. | Job | 1 |  |  | 0 | 0 | 0
8.12 | Supplying and fixing 22U Rack Aluminium Frame - 600x800mm with 4 x FAN, Dual Split perforated Door at Front and Back Side, 2 x Vertical Cable Basket, 2 x 12 socket 5/15A PDU with MCB, side Panels of 2 nos and Heavy Duty Castors with break, 19" Reduced Channel - Loop Type (DATA+CCTV) | Job | 1 |  |  | 0 | 0 | 0
8.13 | Supply & installation of GI conduits with junction boxes, reducer etc. complete concealed/surface mounting as required.
| Sub Total of 8.0 |  |  |  |  | 0 | 0 | 0
9 | SUPPLY & INSTALLATION OF SAFETY ITEMS
9.1 | Sand buckets with stand (set of 3 buckets) | Sets | RO |  |  | 0 | 0 | 0
9.2 | Caution boards (11kV) of standard Size | Nos | RO |  |  | 0 | 0 | 0
9.3 | Caution boards (415V) of std. Size | Nos | 1 |  |  | 0 | 0 | 0
9.4 | Rubber mat at panel room 12mm thk. 1mtr. Wide | Mtrs | 1 |  |  | 0 | 0 | 0
9.5 | Shock treatment chart as per electricity board | Nos | 1 |  |  | 0 | 0 | 0
9.6 | First aid box with standard items | Nos | RO |  |  | 0 | 0 | 0
9.7 | 11 KV rating rubber hand gloves | Sets | RO |  |  | 0 | 0 | 0
9.8 | The contractor to submit all the AS BUILT DRAWINGS after the completion of the project for Electrical & ELV Services executed at site. | Part of Tender |  |  |  | 0 | 0 | 0
| Sub Total of 9.0 |  |  |  |  | 0 | 0 | 0
10 | UPS/ INVERTER System:
10.1 | Supply, Installation, testing and commissioning of 3 KVA UPS System Single Phase I/C & Single Phase O/G complete with 30 Minutes Battery Back-up the required accessories as specified in the drawings & the specifications. Make: Emerson/APC/Consul Neowatt/Vivtar Electronics | set | 1 |  |  | 0 | 0 | 0
| Sub Total of 10 |  |  |  |  | 0 | 0 | 0
11 | CCTV
11.1 | Supply & Installation of 2 Megapixel IR-20Mtr. IP Indoor Dome + Night vision. Camera Make: CP-PLUS | Nos. | 8 |  |  | 0 | 0 | 0
11.2 | Supply & Installation of 2 Megapixel IR-20Mtr. IP Indoor Bullet Camera+ Night vision. Camera Make: CP-PLUS | Nos. | RO |  |  | 0 | 0 | 0
11.3 | Supply & Installation of 2 Megapixel IR-30Mtr. IP Outdoor Bullet Camera + Night vision. Camera Make: CP-PLUS | Nos. | RO |  |  | 0 | 0 | 0
11.4 | Supply & Installation of 16 Channel NVR with 4 Sata Hard Disk Slot (Make: Honeywell/CP PLUS) | Nos. | RO |  |  | 0 | 0 | 0
11.5 | Supply & Installation of 24 Channel NVR with 4 Sata Hard Disk Slot (Make: Honeywell/CP PLUS) | Nos. | RO |  |  | 0 | 0 | 0
11.6 | Supply & Installation of 16 Channel NVR with 2 Sata Hard Disk Slot (Make: Honeywell/CP PLUS) | Nos. | 1 |  |  | 0 | 0 | 0
11.7 | Supply & Installation of 16Port PoE Switch (Make: Systimax) | Nos. | 1 |  |  | 0 | 0 | 0
11.8 | 6 TB HDD Hard Disk | Nos. | 1 |  |  | 0 | 0 | 0
11.9 | Monitor/PC system | Nos. | 1 |  |  | 0 | 0 | 0
11.1 | Supply & Installation of CAT-6 Cable for Camera Signal | Mtr. | 120 |  |  | 0 | 0 | 0
| Sub Total of 11 |  |  |  |  | 0 | 0 | 0
12 | PA SYSTEM
12.1 | Supply & Installation of 6W Ceiling Speaker with box | RM | 9 |  |  | 0 | 0 | 0
12.2 | Control Unit (with volume and on/off switch) (Smooth stepless control, but the control shall be through dimmer switch, the make of which will be same as the make of light control switches) | Nos. | 1 |  |  |  |  | 0
12.3 | Supply & Installation of 120W Booster Amplifier | Nos. | 1 |  |  | 0 | 0 | 0
12.4 | Installation of 2 core 2.5 Sq.mm PVC insulated twisted copper conductor Speaker wires as required. | RM | 80 |  |  | 0 | 0 | 0
| Sub Total of 12 |  |  |  |  | 0 | 0 | 0
13 | FIRE ALARM SYSTEM
13.1 | Single Loop Analog Addressable Fire Alarm Control panel (Expandable upto 1 Loop) with battery back up for 4 hours normal operation and 15 minutes alarm operation. The control panel per Loop Capacity 250 Detectrs and Devices, battery charger etc., 8.5" Touch Screen LCD Display, TCP/IP Connectivity, 10000 Event Log, Keyless Log on Using RFID Cards. The panel shall be UL listed and preferably FM approved with response time less than 10sec. Installation of fire alarm system shall be done as per IS 2189 or relevant NFPA standard.The panel shall have the web enabled facility which can able to send or receive e-mails with memory of 1000 events recording.Note:The vendor shall provide panel UL 9th edition listing certificate. (Make: Edwards / Honeywell) | Nos | 1 |  |  | 0 | 0 | 0
i) Each loop with Min. 99 Devices + 99 Detectors modules connection capability of Addressable FACP) 2 Loop Pannel.
ii) FACP with all in-built modules & displays.
iii) 240 volts AC power supply, automatic battery charger, 24 volts sealed lead acid batteries sufficient for 4 hours normal working.
iv) Programming & setting up
v) system to be capable of operating the system for 2 hours during an emergency condition including all necessary software for remote programming of fire alarm system through central control station.
vi) As the number of hooters are 43, additional power supplies to be provided as required.
Necessary Integration Facility with BMS for following functions:-
Alarm, Trouble condition,Supervisory alerts to BMS
Share Graphics of Security, Fire and HVAC
13.1.1 | Fire alarm Addressable control panel (1 Loop)
13.2 | Active Repeater Panel with 8.5" Touch Screen TFT display with TCP/IP Eable Repeater Panel shall monitor and control (Scroll, Acknowledge, Reset & Mute) all the events of the FACP to which it is connected and it shall have Port Vectoring / Event Filtering capability of showing only ALARMS, TROUBLES or SUPERVISORY or customized combinations of user selected events. | Nos | RO |  |  | 0 | 0 | 0
13.2.1 | Supply installation and testing of signal loop components in a suitable galvanised steel junction box.
13.3 | Detectors and Devices
13.3.1 | Supply,Installation,Testing & Commissioning of Analogue Addressable Monitor module having Rotary, decimal addressing system for monitoring the field devices & shall be capable of providing DPDTcontact rated at 24V DC, 2A. | Nos | RO |  |  | 0 | 0 | 0
13.3.2 | Supply,Installation,Testing & Commissioning of Analogue Addressable Relay module having Rotary, decimal addressing system for AHU tripping and shall be capable of providing DPDTcontact rated at 24v DC, 2A. | Nos | 2 |  |  | 0 | 0 | 0
(For all AHU's, Fans & Acess Control)
13.3.3 | Supply,Installation,Testing & Commissioning of Horn / Strobe rated at 82 dBA @ 3m for Audible annunciation and 75cd flashing at 1 Hz for visual indication with Control modules and necessary accessories including back box. | Nos | 2 |  |  | 0 | 0 | 0
13.3.4 | Supply, Installation,Testing & Commissioning of Analogue Addressable Flash scan Type Photoelectric smoke detectors( Below False Ceiling) having Rotary, decimal addressing system with standard base, built in isolation function and junction box. The detector shall be capable to address in the range of 1-159. The detector shall be with Visible bi-color LEDs for 360 deg viewing and shall blink green every time the detector is addressed, and illuminate steady red on alarm. | Nos | 10 |  |  | 0 | 0 | 0
13.3.5 | Supply,Installation,Testing & Commissioning of Analogue Addressable Flash scan Type Photoelectric smoke detectors (Above False Ceiling) having Rotary, decimal addressing system with standard base, built in isolation function and junction box. The detector shall be capable to address in the range of 1-159. The detector shall be with Visible bi-color LEDs for 360 deg viewing and shall blink green every time the detector is addressed, and illuminate steady red on alarm. | Nos | 4 |  |  | 0 | 0 | 0
13.3.6 | Supply,Installation,Testing & Commissioning of Analogue Addressable Flash scan Type Photoelectric Multi Sensor detectors having Rotary, decimal addressing system with standard base, built in isolation function and junction box. The detector shall be capable to address in the range of 1-159. The detector shall be with Visible bi-color LEDs for 360 deg viewing and shall blink green every time the detector is addressed, and illuminate steady red on alarm. (Make- Edward-SIGA PHD) | Nos | RO |  |  | 0 | 0 | 0
13.3.7 | Supply,Installation,Testing & Commissioning of Analogue Addressable Flash scan Type Heat Detector having Rotary, decimal addressing system with standard base, built in isolation function and junction box. The detector shall be capable to address in the range of 1-159. The detector shall be with Visible bi-color LEDs for 360 deg viewing and shall blink green every time the detector is addressed, and illuminate steady red on alarm. (Make- Edward-EST-SIGA-HFS) | Nos | 1 |  |  | 0 | 0 | 0
13.3.8 | Supply,Installation,Testing & Commissioning of Analogue Addressable Flash scan Type GAS leak Detector having Rotary, decimal addressing system with standard base, built in isolation function and junction box. The detector shall be capable to address in the range of 1-159. The detector shall be with Visible bi-color LEDs for 360 deg viewing and shall blink green every time the detector is addressed, and illuminate steady red on alarm. (Make- Edward-EST-SIGA-HFS) | Nos | 1 |  |  | 0 | 0 | 0
13.3.9 | Supply,Installation,Testing & Commissioning of Addressable Break Glass Manual Call Point having Rotary, decimal addressing system and having an integrally mounted addressable module that monitors and reports contact status. | Nos | 2 |  |  | 0 | 0 | 0
13.4 | SITC of Fault Isolator. | Nos | 1 |  |  | 0 | 0 | 0
13.5 | SITC of 2Cx1.5sq.mm multistranded FRLS Cu. Armoured for RED Colour,Mylan Shielded Screened cable For SLC. | Mtrs | 120 |  |  | 0 | 0 | 0
13.6 | Response indicator. | Nos | 4 |  |  | 0 | 0 | 0
| Sub Total of 13 |  |  |  | 0 | 0 | 0 | 0