## Electrical
Dominos ………………….Civil & Interiors BOQ¦ Ver 3.0
1. Partition, Panelling - Sq. Ft area – one side only
2. Storage Units - Sq. Ft area – Front elevation length x Front Finished height
3. False Ceiling - Sq. Ft area – Flat surface area in reflected ceiling plan
4. Flooring - Sq. Ft. area – Internal area contained within skirting
5. Pls Note Only Bison , Marine Ply and Wpc Board to be used instead of Commercial Ply
6. Chiseling work included in the items or else specified
7. Scaffolding will be in contractor scope upto 4mtr & Above 4mtr rate will be chargeable. If required for installation of civil & MEP.
8. All Items Rates are inclusive of material lead & lift charges.
F |  |  |  | Electrical
| F.1.0 |  |  | VTPN DB
|  | a.1 | 16 Way VTPN DB - Kitchen Equipment+ Lighting+Power DB | Triple pole and neutral distribution board (VTPNDB with vertical busbar) with Double door surface/flush mounted comprising of following:- | Each | 0 | 0
Incomer :
100A , TM based MCCB of 25kA with O/L, S/C & E/F Protection - 01 No
Outgoing :
6/32A SP MCB - 24 Nos
6/32 Amp TP MCB- 8 Nos
With all necessary connections
|  | a.2 | 12 Way VTPN DB - Kitchen Equipment+ Lighting+Power DB | Triple pole and neutral distribution board (VTPNDB with vertical busbar) with Double door surface/flush mounted comprising of following:- | Each | 1 | 0
Incomer :
63A , TM based MCCB of 25kA with O/L, S/C & E/F Protection - 01 No
|  |  |  | Outgoing : |  |  |  | 1
6/32A SP MCB - 18 Nos
6/32 Amp TP MCB- 6 Nos
With all necessary connections
|  | a.3 | 8 Way VTPN DB - Kitchen Equipment+ Lighting+Power DB | Triple pole and neutral distribution board (VTPNDB with vertical busbar) with Double door surface/flush mounted comprising of following:- | Each | 0 | 0
Incomer :
63A , TM based MCCB of 25kA with O/L, S/C & E/F Protection - 01 No
Outgoing :
6/32A SP MCB - 12 Nos
6/32 Amp TP MCB- 4 Nos
With all necessary connections
Sub Total of F.1.0 | [6 empty] | 0
| F.2.0 |  |  | TPN DB
|  | b.1 | 12 Way TPN DB - Kitchen Equipment+ Lighting+Power DB | DB shall have separate neutral links of rating not less than 100A for each phase. The main incoming neutral link shall be in addition to three outgoing neutral links and shall be of 125A. | Each | 0 | 0
Incomer :
63A FP, MCB of 10kA - 01 No
Sub Incomer
3Nos, DP, 63A, RCBO (30mA).
Outgoing :
6/32A SP MCB - 30 Nos
With all necessary connections
|  | b.2 | 8 Way TPN DB - Kitchen Equipment+ Lighting+Power DB | Triple pole and neutral distribution board (TPNDB) with Double door surface/flush mounted of 8 way (4+ 24 Module) 4 Horizontal Rows in 4 Vertical tiers configuration comprising of following:- | Each | 0 | 0
DB shall have separate neutral links of rating not less than 100A for each phase. The main incoming neutral link shall be in addition to three outgoing neutral links and shall be of 125A.
8 Way TPN Double door type DB for Power comprising of following:-
Incomer :
40A FP MCB,10kA - 01 No
Sub Incomer
3Nos, DP, 40A, RCBO (30mA).
Outgoing :
6/32A SP MCB - 18 Nos
With all necessary connections
|  | b.3 | 6 way TPN DB | Triple pole and neutral distribution board (TPNDB) with Double door surface/flush mounted of 6 way (4+ 18 Module) 4 Horizontal Rows in 4 Vertical tiers configuration comprising of following:- | Each | 0 | 0
DB shall have separate neutral links of rating not less than 100A for each phase. The main incoming neutral link shall be in addition to three outgoing neutral links and shall be of 125A.
8 Way TPN Double door type DB for Power comprising of following:-
Incomer :
40A FP MCB,10kA - 01 No
Sub Incomer
3Nos, DP, 40A, RCBO (30mA).
Outgoing :
6/32A SP MCB - 12 Nos
With all necessary connections
Sub Total of F.2.0 | [6 empty] | 0
| F.3.0 |  |  | SPN DB
|  | c.1 | 12 Way SPN DB - UPS DB | 12 Way SPN Double door type DB for Power comprising of following:- | Each | 0 | 0
Incomer :
32A DP MCB - 01 No
Outgoing :
6/32A SP MCB - 12 Nos
16A SP MCB -05 Nos
With all necessary connections
|  | c.2 | 8 Way SPN DB - UPS DB | 8 Way SPN Double door type DB for Power comprising of following:- | Each | 2 | 0
Incomer :
25A DP MCB - 01 No
|  |  |  | Outgoing : |  |  |  | 2
16A SP MCB - 04 Nos
10A SP MCB - 02 Nos
With all necessary connections
|  | c.3 | 6 Way SPN DB - UPS DB | 6 Way SPN Double door type DB for Power comprising of following:- | Each | 0 | 0
Incomer :
16A DP MCB - 01 No
Outgoing :
10A SP MCB - 03 Nos
16A SP MCB - 1 No
With all necessary connections
Sub Total of F.3.0 | [6 empty] | 0
| F.4.0 |  |  | Isolators /ELCB /RCBO & SWITCH SOCKETS
|  | a.1 |  | Supply , installation, testing comissioning of DP isolator of 25 A | Each | 0 | 0
|  | a.2 |  | Supply , installation, testing comissioning of DP isolator of 32 A | Each | 2 | 0 | 2
|  | a.3 |  | Supply , installation, testing comissioning of DP isolator of 40 A | Each | 0 | 0
|  | a.4 |  | Supply , installation, testing comissioning of DP MCB of 25 A | Each | 0 | 0
|  | a.5 |  | Supply , installation, testing comissioning of DP MCB of 32 A | Each | 2 | 0 | 2
|  | a.6 |  | Supply , installation, testing comissioning of DP MCB of 40 A | Each | 2 | 0 | 2
|  | a.7 |  | Supply , installation, testing comissioning of FP ELCB of 25 A, 100mA | Each | 2 | 0
|  | a.8 |  | Supply , installation, testing comissioning of FP ELCB of 40 A, 100mA | Each | 0 | 0
|  | a.9 |  | Supply , installation, testing comissioning of FP RCBO of 63 A, 100mA | Each | 0 | 0
|  | a.10 |  | Supply, Installation, testing comissioning of 10 amp TPN MCB | Each | 0 | 0
|  | a.11 |  | Supply, Installation, testing comissioning of 32 amp TPN MCB | Each | 0 | 0
|  | a.12 |  | Supply, Installation, testing comissioning of 40 amp TPN MCB | Each | 0 | 0
|  | a.13 |  | Providing and fixing TPN/DP enclosure box for indoor purpose | Each | 0 | 0
|  | a.14 |  | Providing and fixing TPN/DP enclosure box (Wheather Proof) for outdoor purposes | Each | 0 | 0
|  | a.15 |  | Providing and Fixing 16 amp single phase Industrial socket | Each | 0 | 0
|  | a.16 |  | Providing and Fixing 25 amp single phase Industrial socket | Each | 0 | 0
|  | a.17 |  | Providing and Fixing 25 amp three phase Industrial socket | Each | 0 | 0
|  | b |  | ISOLATOR - (BEFORE SERVO STABILIZER) |  |  | 0
|  | b.1 |  | 125A FP, 25kA Thermal Magnetic based MCCB with LSIG Protection with Box (As per the instruction of the Engineer Inchrge) | Each | 0 | 0
|  | b.2 |  | 100A FP, 25kA Thermal magneticr based MCCB with LSIG Protection with Box(As per the instruction of the Engineer Inchrge) | Each | 1 | 0 | 1
|  | c |  | 6/16 Amp Electrical Top | Each | 4 | 0 | 4
|  |  | Light Point Wiring Specifications | Point wiring shall include FRLS wire with all necessary "MMS PVC CONDUIT", with all fittings , accessories , couplings,collars etc., junction / pull / inspection boxes, wires, supports,bushings lamp holders, ceiling rose, flexible conduit, fan hooks wherever required, modular switch, switch box, Fan electronic regulator & terminations using tinned copper lugs of crimping type with cheisling and scaffolding. The scope of sub mains wiring from Panel to DB are excluded.All wiring should be terminated with coupler & connectors.All lighting fixture wiring shall be carried out for primary point using 1.5sqmm copper stranded & for secondary wiring 1sqmm copper stranded conductor 660/1100V grade PVC insulated wire in "PVC Conduit". Individual junction/inspection boxes shall be provided for each lighting fitting for the purpose of looping from fitting to fitting. From switch board/DB to first light fitting will be termed as primary point and First fitting to subsequent fitting on the same circuit shall be as termed secondary point. Light point wiring shall excluded submains wiring from Panel to DB. The scope of light point wiring starts after switch board/DB where switching control is directly from DB.
|  | d | Lighting points with PVC conduit | Wiring for the following light points with 2X1.5 sq mm PVC insulated copper conductor 650V grade FRLS wires in concealed or surface mounted 20/25mm dia MMS PVC conduit as required including providing 6 amps flush type PVC moulded switches, cover plate,5 sided 1.2mm thick G.I. Box one module for housing switches and earthing of the fixtures and outlet box with 1.5 mm PVC insulated copper conductor 650V grade green earth wire.(switches-as/approved make)- upto 10 Mt. wire length is inclusive.
|  | d.1 |  | Primary (First) light point controlled by a 6A switch. | Nos | 0 | 0
|  | d.2 |  | Primary (First) light point controlled by a MCB in the DB. | Nos | 0 | 0
|  | d.3 |  | Secondary (Loop) light point looped to first point and so on.(upto 6 mtr) wire length | Nos | 0 | 0
|  | d.4 |  | Supply, Installation, Testing & Commissioning of mains with 2 X 1.5 sq.mm and earth wire 1.5 sqmm FRLS PVC copper wire ,in rigid MMS PVC conduit min.25 mm dia, for light/fan/exhaust point from DB to point including all required accessories,etc as per specification.(If wire length increase above 10 mt mentioned in lighting circuit) | RMT | 0 | 0
|  | d.5 |  | Supply, Installation, Testing & Commissioning of mains with 2 X 2.5 sq.mm and earth wire 2.5 sqmm FRLS PVC copper wire ,in rigid MMS PVC conduit min.20 mm dia,including all required accessories,etc as per specification. | RMT | 0 | 0
|  | d.6 |  | Supplying & erecting mains with 2x4 sq.mm and earth wire 2.5 sqmm FRLS PVC copper wire laid with conduit/trunking/inside pole/Bus bars or any other places. | RMT | 0 | 0
|  | e | Lighting points with MS conduit | Wiring for the following light points with 2X1.5 sq mm PVC insulated copper conductor 650V grade FRLS wires in concealed or surface mounted 20/25mm dia MS conduit as required including providing 6 amps flush type PVC moulded switches, cover plate,5 sided 1.2mm thick G.I. Box one module for housing switches and earthing of the fixtures and outlet box with 1.5 mm PVC insulated copper conductor 650V grade green earth wire.(switches-as/approved make)- upto 10 Mt. wire length is inclusive.
|  | e.1 |  | Primary (First) light point controlled by a 6A switch. | Nos. | 4 | 0 | 4
|  | e.2 |  | Primary (First) light point controlled by a MCB in the DB. | Nos. | 4 | 0 | 4
|  | e.3 |  | Secondary (Loop) light point looped to first point and so on.(upto 6 mtr) wire length | Nos. | 8 | 0 | 8
|  | e.4 |  | Supply, Installation, Testing & Commissioning of mains with 2 X 1.5 sq.mm and earth wire 1.5 sqmm FRLS PVC copper wire ,in rigid MS conduit min.25 mm dia, for light/fan/exhaust point from DB to point including all required accessories,etc as per specification.(If wire length increase above 10 mt mentioned in lighting circuit) | Rmtr | 8 | 0 | 8
|  | e.5 |  | Supply, Installation, Testing & Commissioning of mains with 2 X 2.5 sq.mm and earth wire 2.5 sqmm FRLS PVC copper wire ,in rigid MS conduit min.20 mm dia,including all required accessories,etc as per specification. | Rmtr | 0 | 0
|  | f |  | Power Point wiring
All switch socket wiring shall be carried out for primary point using 3x2.5 sq mm wire in "PVC Conduit" for connection of 6/16amp socket. Individual junction/inspection boxes shall be provided for each Power Point for the purpose of looping with cheisling and scaffolding work if required .Inclusive of all G.I. Boxing and wire termination & MMS conduit etc. From DB to first switch socket will be termed as primary point and First socket to subsequent looping on the same circuit shall be as termed secondary point. Power point wiring shall excluded submains wiring from Panel to D.B. The scope of Power point wiring starts after DB where switching control is directly from DB.upto 10 Mt. wire length is inclusive.
|  | f.1 |  | First Point wiring with 6A,5pin wall socket outlet and controlled by a 6A switch | Nos | 0 | 0
|  | f.2 |  | Extra loop point wiring with 6A, 5 pin wall socket outlet and controlled by a 6A switch upto 6 mtr length | Nos | 0 | 0
|  | f.3 |  | First Point wiring with 16A,5pin wall socket outlet and controlled by a 16A switch | Nos | 0 | 0
|  | f.4 |  | Extra loop point wiring with 16A, 5 pin wall socket outlet and controlled by a 16A switch upto 6 mtr length | Nos | 0 | 0
|  | f.5 |  | Additional 6 Amp Switch & socket outlet in G.I. Box on modular cover plate adjoining and looped from the existing point. (Note:-additional means switch socket in modular box and plate adjoining the existing one on the same circuit.) Wire will be paid in Rmt separately | Nos |  | 0
|  | g |  | All switch socket wiring shall be carried out for primary point using 3X4 sq mm wire in "PVC Conduit" for connection of 16 amp socket . Individual junction/inspection boxes shall be provided for each Power Point for the purpose of looping with cheisling and scaffolding work if required .Inclusive of all G.I. Boxing and wire termination & MMS PVC conduit etc. From DB to first switch socket will be termed as primary point and First socket to subsequent looping on the same circuit shall be as termed secondary point. Power point wiring shall excluded submains wiring from Panel to D.B. The scope of Power point wiring starts after DB where switching control is directly from DB.upto 12 Mt. wire length is inclusive.
|  | g.1 |  | First Point wiring with 16A, 3Pin combined shuttered wall socket outlet and controlled by a 16A one way switch with indicator. | Nos | 5 | 0 | 5
|  | g.2 |  | Extra loop point wiring with 16A, 3Pin combined shuttered wall socket outlet and controlled by a 16A one way switch with indicator.upto 6 mtr wiring | Nos | 16 | 0 | 16
|  | g.3 |  | Additional 16 Amp Switch & socket outlet in G.I. Box on modular cover plate adjoining and looped from the existing point. (Note:-additional means switch socket in modular box and plate adjoining the existing one on the same circuit.) . Wire will be paid in Rmt separately | Nos |  | 0
|  | g.4 |  | Supply and Laying of Wiring for light/ power plug with 4X4 sq. mm FRLS PVC insulated copper conductor single core wire in surface/recessed medium class MMS PVC conduit alongwith 2 Nos. 4 sq. mm FRLS PVC insulated copper conductor single core cable for loop earthing as required. | Rmtr | 150 | 0 | 150
|  | h |  | Power Point wiring(MS conduit)
All switch socket wiring shall be carried out for primary point using 3x2.5 sq mm wire in "MS Conduit" for connection of 6/16amp socket. Individual junction/inspection boxes shall be provided for each Power Point for the purpose of looping with cheisling and scaffolding work if required .Inclusive of all G.I. Boxing and wire termination & MMS conduit etc. From DB to first switch socket will be termed as primary point and First socket to subsequent looping on the same circuit shall be as termed secondary point. Power point wiring shall excluded submains wiring from Panel to D.B. The scope of Power point wiring starts after DB where switching control is directly from DB.upto 10 Mt. wire length is inclusive.
|  | h.1 |  | First Point wiring with 6A,5pin wall socket outlet and controlled by a 6A switch | Nos | 3 | 0 | 3
|  | h.2 |  | Extra loop point wiring with 6A, 5 pin wall socket outlet and controlled by a 6A switch upto 6 mtr length | Nos | 4 | 0 | 4
|  | h.3 |  | First Point wiring with 16A,5pin wall socket outlet and controlled by a 16A switch | Nos | 2 | 0 | 2
|  | h.4 |  | Extra loop point wiring with 16A, 5 pin wall socket outlet and controlled by a 16A switch upto 6 mtr length | Nos | 2 | 0 | 2
|  | i |  | All switch socket wiring shall be carried out for primary point using 3X4 sq mm wire in "MS Conduit" for connection of 16 amp socket . Individual junction/inspection boxes shall be provided for each Power Point for the purpose of looping with cheisling and scaffolding work if required .Inclusive of all G.I. Boxing and wire termination & MMS PVC conduit etc. From DB to first switch socket will be termed as primary point and First socket to subsequent looping on the same circuit shall be as termed secondary point. Power point wiring shall excluded submains wiring from Panel to D.B. The scope of Power point wiring starts after DB where switching control is directly from DB.upto 12 Mt. wire length is inclusive.
|  | i.1 |  | First Point wiring with 16A, 3Pin combined shuttered wall socket outlet and controlled by a 16A one way switch with indicator. | Nos | 4 | 0 | 4
|  | i.2 |  | Extra loop point wiring with 16A, 3Pin combined shuttered wall socket outlet and controlled by a 16A one way switch with indicator.upto 6 mtr wiring | Nos | 3 | 0 | 2
|  | j | Conduiting | Supplying and fixing of following sizes of medium class PVC conduit along with accessories in surface/recess including cutting the wall/floor and making good the same in case of recessed conduit as required.
|  | j.1 |  | 20 mm | Rmtr | 0 | 0
|  | j.2 |  | 25 mm | Rmtr | 0 | 0
|  | j.3 |  | 32 mm | Rmtr | 0 | 0
|  | j.4 |  | 40 mm | Rmtr | 0 | 0
|  | j.5 |  | 50 mm | Rmtr | 0 | 0
|  | k |  | Supplying and fixing of following sizes of MS conduit along with accessories in surface/recess including painting in case of surface conduit, or cutting the wall and making good the same in case of recessed conduit as required.
|  | k.1 |  | 20 mm | Rmtr | 24 | 0 | 24
|  | k.2 |  | 25 mm | Rmtr | 30 | 0 | 30
|  | k.3 |  | 32 mm | Rmtr | 0 | 0
|  | k.4 |  | 40 mm | Rmtr | 0 | 0
|  | k.5 |  | 50 mm | Rmtr | 0 | 0
|  | l |  | Supplying & erecting MMS PVC flexible Conduit 25 mm dia.conforming to I.S. and approved make with required number of couplings, bushes, check nuts etc. | Rmtr | 0 | 0
|  | m |  | Supplying & erecting M.S flexible Conduit 25 mm dia.conforming to I.S. and approved make with required number of couplings, bushes, check nuts etc. | Rmtr | 10 | 0 | 10
|  | n |  | Supplying & erecting PVC flexible Conduit 50 mm dia.conforming to I.S. and approved make with required number of couplings, bushes, check nuts etc. | Rmtr | 8 | 0 | 8
|  | o |  | Supply, Installation, Testing & Commissioning of G.I Conduit 32mm dia with necessary accessories in wall/floor with chiselling appropriately as per specification. | Rmtr | 0 | 0
|  | p |  | Supply, Installation, Testing & Commissioning of G.I conduit 25 mm in dia with necessary accessories in RCC work/false ceiling/false flooring as per specification | Rmtr | 0 | 0
Sub Total of F.4.0 | [6 empty] | 0
| F.5.0 |  |  | LT CABLES & TERMINATIONS
|  | a | SUPPLY AND LAYING OF THE CABLES | Supply, Errecting, Termination & Commissioning of following sizes of 1.1 KV grade FRLS Armoured/Unarmoured Copper/ Aluminum conductor cables laid over MS supports cable racks/trays or fixing on walls including clamping the cable to supports cable racks or fixing on walls including lugs, double compression gland and joints complete in an approved manner as required .
|  | a.1 |  | 4Cx16 Sq.mm AL Arm. XLPE | Rmtr |  | 0
|  | a.2 |  | 4Cx25 Sq.mm AL Arm. XLPE | Rmtr |  | 0
|  | a.3 |  | 3Cx2.5 Sqmm Cu. Arm. XLPE | Rmtr |  | 0
|  | a.4 |  | 3Cx4 Sqmm Cu. Arm. XLPE | Rmtr |  | 0
|  | a.5 |  | 3.5Cx35 Sq.mm AL Arm. XLPE | Rmtr |  | 0
|  | a.6 |  | 3.5Cx50 Sq.mm AL Arm. XLPE | Rmtr | 0 | 0
|  | a.7 |  | 3.5Cx70 Sq.mm AL Arm. XLPE | Rmtr | 6 | 0 | 6
|  | a.8 |  | 3.5Cx95 Sq.mm AL Arm. XLPE | Rmtr |  | 0
|  | a.9 |  | 4Cx2.5 Sq.mm Cu. Arm. XLPE | Rmtr |  | 0
|  | a.10 |  | 4Cx4 Sq.mm Cu. Arm. XLPE | Rmtr |  | 0
|  | a.11 |  | 4C x 6 sq.mm Cu. Arm. XLPE | Rmtr | 0 | 0
|  | a.12 |  | 4Cx10 Sq.mm Cu. Arm. XLPE | Rmtr | 4 | 0 | 4
|  | a.13 |  | 4C x 16 sq.mm Cu. Arm. XLPE | Rmtr | 0 | 0
|  |  | CABLE TERMINATION | Supplying and making indoor Cable end Termination of following sizes 1.1kV grade LT XLPE insulated, HR PVC sheathed, stranded Aluminum/copper conductor, Armoured/ Unarmoured cables as per IS:7098 part-I including cost of tinned copper / Aluminium heavy duty crimpping lugs, double compression weatherproof glands, insulation tape, Name Plate at Both Ends and all necessary material to complete the termination.
|  | b |  | 2/3/3.5/4 CORES AL. CABLE WITH AL. LUGS
|  | b.1 |  | 35 sq.mm. | Jt | 0 | 0
|  | b.2 |  | 50 sq.mm. | Jt | 0 | 0
|  | b.3 |  | 70 sq.mm. | Jt | 0 | 0
|  | c |  | Multicore Flexible Cables : 1100 Volt Annealed Bare Electrolytic High, Conductivity Copper Conductor Flexible PVC Type 'A' Insulated & PVC ST-1 Sheathed Cables in existing Conduit. Conforming to IS: 694:1990 including Making Both End terminations with copper lugs. | Rmtr | 0
|  | c.1 |  | 3C x 2.5mm2 1100V grade flexible copper conductor sheathed FLRS PVC cable (P, N, IG)- IS 694/1990. | Rmtr |  | 0
|  | c.2 |  | 3C x 4.0mm2 1100V grade flexible copper conductor sheathed FLRS PVC cable (P, N, IG)- IS 694/1990. | Rmtr | 0 | 0
Sub Total of F.5.0 | [6 empty] | 0
| F.6.0 |  |  | EARTHING (In absence of D.G.Vendor)
|  | a.1 |  | Supply & Laying of 25mmX3mm GI strips with necessary G. I. Clamps fixed on wall/cable/ conduit with screws in an approved manner. | Mtrs | 0 | 0
|  | a.2 |  | Supply & Laying of 25mmX3mm CU strips with necessary G. I. Clamps fixed on wall/cable/ conduit with screws in an approved manner. | Mtrs | 0 | 0
|  | a.3 |  | 25X4 sqmm Earth Alu.Armd cable(For RoofTop) with necessary G. I. Clamps fixed on wall/cable/ conduit with screws in an approved manner. | Mtrs | 0 | 0
|  | a.4 |  | 35X4 sqmm Earth Alu.Armd cable(For RoofTop) with necessary G. I. Clamps fixed on wall/cable/ conduit with screws in an approved manner. | Mtrs | 0 | 0
|  | a.5 |  | 8 SWG GI Earth Wire with necessary G. I. Clamps fixed on wall/cable/ conduit with screws in an approved manner. | Mtrs | 0 | 0
|  | a.6 |  | 8 SWG Cu Wire with necessary G. I. Clamps fixed on wall/cable/ conduit with screws in an approved manner. | Mtrs | 0 | 0
|  | a.7 |  | Supply, Installation, Testing & Commissioning of long life, Maintenance Free advance chemical Earthing System with 20 year service warranty with 8 feet Vertical Pipe in pipe GI Not less than 1.5” (40mm) ID and not less than 1.5mm wall thickness, & 20x2mm tape inside, which does not require manual addition of water including earthing chamber (300m x 300mm x 300 deep)with cover. The complete systems supported by SEM-20 STRONG based certified advance soil enhancement material. Including all civil works for pit. UOM - Each. This should be done till upto 3 mtr.(Earth resistance value shall be <1 Ohm) | No.'s | 0 | 0
|  | a.8 |  | Supply, Installation, testing and commissioning of earth pits comprising 600x600x 3mm thick G.I. electrode/plate 25 mm dia medium class watering G.I. pipe, G.I. funnel with 20 gauge GI wire mesh, masonary chamber with concrete base, CI manhole cover with frame (300m x 300mm x 300 deep) strip from earth palte to link painted with bitumastic paint, test link joint packing the mixture with salt &charcoal 150 mm all around plate electrode complete as required as per IS:3043..(Earth resistance value shall be <1 Ohm) | No.'s | 0 | 0
|  | a.9 |  | 4.0 sq.mm. Cu. Flexible cable | Rmtr | 0 | 0
|  | a.10 |  | 6.0 sq.mm. Cu. Flexible cable | Rmtr | 0 | 0
|  | a.11 |  | 10 sq.mm. Cu. Flexible cable | Rmtr | 0 | 0
|  | a.12 | D.G Foundation | Generator bedding incl of floor raising with debris (4" to 6" )with necessary brickwork at all sides/ with 1:2:4 cement sand metal morter bed as PCC/ IPS/plaster on vertical edges, complete in all respects | Sqft | 0 | 0
Sub Total of F 6.0 | [6 empty] | 0
| F.7.0 |  |  | Cable Trays
|  | a.1 |  | Providing & erecting Hot deeped Galvanised Perforated type Cable tray manufactured from 18 swg (1.6 mm thick) GI sheet of 300 mm width & 50 mm height complete with necessary coupler plates & hardware in approved manner. Including Paints | Rmtr | 0 | 0
|  | a.2 | Cable Tray -Non Perforated for Kitchen | Providing & erecting Hot deeped Galvanised Non -Perforated type Cable tray manufactured from 18 swg (1.6 mm thick) GI sheet of 300 mm width & 50 mm height complete with necessary coupler plates & hardware in approved manner Including Paint | Rmtr | 32 | 0 | 32
|  | a.3 |  | Providing & erecting Hot deeped Galvanised Perforated type Cable tray manufactured from 18 swg (1.6 mm thick) GI sheet of 200 mm width & 50 mm height complete with necessary coupler plates & hardware in approved manner.Including Paint | Rmtr |  | 0
|  | a.4 | Cable Tray -Non Perforated for Kitchen | Providing & erecting Hot deeped Galvanised Non -Perforated type Cable tray manufactured from 18 swg (1.6 mm thick) GI sheet of 200 mm width & 50 mm height complete with necessary coupler plates & hardware in approved manner.Including Paint | Rmtr | 0 | 0
|  | a.5 |  | Providing & erecting Hot deeped Galvanised Perforated type Cable tray manufactured from 18 swg (1.6 mm thick) GI sheet of 100 mm width & 50 mm height complete with necessary coupler plates & hardware in approved manner.Including Paint | Rmtr |  | 0
|  | a.6 | Cable Tray -Non Perforated for Kitchen | Providing & erecting Hot deeped Galvanised Non- Perforated type Cable tray manufactured from 18 swg (1.6 mm thick) GI sheet of 100 mm width & 50 mm height complete with necessary coupler plates & hardware in approved manner.Including Paint | Rmtr |  | 0
|  | a.7 |  | Providing & erecting Hot deeped Galvanised Perforated type Cable tray manufactured from 18 swg (1.6 mm thick) GI sheet of 50 mm width & 50 mm height complete with necessary coupler plates & hardware in approved manner.Including Paint | Rmtr |  | 0
|  | a.8 | Cable Tray -Non Perforated for Kitchen | Providing & erecting Hot deeped Galvanised Non -Perforated type Cable tray manufactured from 18 swg (1.6 mm thick) GI sheet of 50 mm width & 50 mm height complete with necessary coupler plates & hardware in approved manner.Including Paint | Rmtr | 0 | 0
|  | b | Raceway | Provind and laying of 2MM thick GI factory fabricated raceways in partition of the following sizes including providing removable 3 mm thick GI cover knock our holes and fixing accessories complete required including floor supports, bends, access boxes and tap of boxes as per instruction from site supervision.
|  | b.1 |  | 300mm wide x 40mm deep | Rmtr |  | 0
|  | b.2 |  | 150mm wide x 40mm deep | Rmtr |  | 0
|  | b.3 |  | 100mm wide x 40mm deep | Rmtr |  | 0
|  | b.4 |  | 50mm wide x 40mm deep | Rmtr |  | 0
Sub Total of F.7.0 | [6 empty] | 0
| F.8.0 |  |  | Electrical Related Civil work
|  | a.1 |  | Excavation/ Cheselling under floor for laying cables/ conduits in wall or floor as per requirement, complete with finishing etc | Sq.Mtr | 21.0805 | 0 | 0
Sub Total of F.8.0 | [6 empty] | 0
| F.9.0 | a |  | Geyser
|  | a.1 |  | SITC of Digital instant GEYSER ABOVE SINK 3 ltr (Ao Smith or equivalent)instant with required accessories) | No. | 0 | 0
|  | a.2 |  | SITC of Storage Geyser (25 ltr) AO smith or equivalent used above 3 way sink with required accessories | No | 1 | 0 | 1
Sub Total of F.9.0 | [6 empty] | 0
| F.10.0 | a |  | Music System/ CONDUITING/WIRING FOR TELEPHONE/DATA/ MUSIC AND COMPUTER SYSTEM
|  | a.1 |  | SITC of Sony Music System (DAV DZ - 350) or Equivalent Make 5.1 | no | 0 | 0
|  | a.2 |  | Wiring to music speakers with 2 pairs 40/0.076 flexible wire (PVC insulator, annealed or surface mounted 20/25 mm PVC conduit as directed (from speaker outlet to music junction box). | Rmtr | 0 | 0
|  | a.3 |  | Two nos. telephone jack outlet in 2 module GI outlet -{Refer Details- Electrical (C) below} | Nos | 0 | 0
|  | a.4 |  | Providing and drawing RG-58 co-axial cable for computer system in existing PVC conduit. | Rmtr | 250 | 0 | 250
|  | a.5 |  | Cat-6 Cable for Switch to Camera inlcuding conduit. | Rmtr | 120 | 0 | 120
|  | a.6 |  | I O Plate including necessary Jack and connections | Nos | 4 | 0 | 4
|  | a.7 |  | VGA cable Including spliter | Rmtr | 75 | 0 | 75
|  | b | Data Modular Box
|  | b.1 |  | 150mm x 200 x 40mm (W x H) - (18 SWG - 2 mm) with cover with one partition. | Each | 2 | 0 | 2
|  | b.2 |  | 100 x 100 x 40mm deep with cover plate for makeline /Slap Table/Biometric | Each | 20 | 0 | 20
|  | b.3 |  | 300 x 300 x 100 mm deep boxes with cover plate for Electrical Panel | Each | 5 | 0 | 5
|  | b.4 |  | Supplying and fixing 1.6 mm thick MS junction/outlet 450X300X100 mm deep boxes with cover plate | Each | 0 | 0
Sub Total of F.10.0 | [6 empty] | 0

## Material Specifications
Dominos - Standard schedule of Materials
SR.NO | Item | Material Code | Materials | Size in MM | Vendor /Code (OPT-01) | Vendor / Code (OPT -02) | Refer dwg no
A | Floor Tiles
1 | Floor Tiles - (Customer Area) | FF01 | Vitrified Tiles | 600 x 600 | Kajaria -Fog Perla (Approved). Cool cement/ cool silver (Subject to POC approval) (Matt Finish) (Size-600x600)mm | Somany -Ethos grey 600 x 600 mm | Drawing no. -130
2 | Floor Tiles - (Kitchen & Back area) | FF02 | Polished Vitrified Tiles | 600 x 600 | Kajaria-Dessert grey (Approved). Cool gris/cairo gris -(Subject to POC approval) (Matt Finish) (Size-600x600)mm |  | Drawing no. -130
2(a) | Floor Tiles - (Kitchen & Back area) | FF02a |  |  | Kajaria- Terrazzo grey (Full Body) (Size-600x600)mm (Subject to POC approval) | Johnson Endura- Grey plus/ Coated Grey/ Coated grey plus (Size-300x300)mm -(Subject to POC approval)
3 | Floor Tiles | FF03 | Full bodied Vitrified Tiles | 300X1200(tread); 600X1200 (slab size) | Johnson Endura Stepping Stone -DONAPAULA PLAIN 600x600 | Somany - Largo Stepon Verde 300 x 1200 & Largo Riser Verde 200 x 1200 | Drawing no. -130
4 | Floor Tiles | FF04 | Vitrified Tiles | 130X800 | Kajaria - Shesham Rosewood 130 x 800 mm | Somany - Strio Hector Wood Teak 196x1200 | Drawing no. -130
5 | Floor Tiles | FF05 | Vitrified Tiles | 130X800 | Kajaria -Shesham Nero 130 x 800 mm | Somany - Strio Salis Wood Wange 196x1200 | Drawing no. -130
B | Wall Tiles
1 | Brick Tiles | BK01 | Exterior Grade-Aggregate Material-German Handmade | 12mmX8"X2.5" | Articlad - ACG 795 | Unistone (Zara cotswold) / MCM(Code -A Series Brick 54058) | Booth Seating Area Wall
2 | Brick Tiles | BK02 | Exterior Grade-Aggregate Material-German Handmade | 12mmX8"X2.5" | Articlad -ACG 555 | MCM Clay Tile(Code -K series ,facing brick /052)/Unistone (Dholpur) | Storefront
3 | Kitchen Wall tile | TL01 |  |  | Ceramic wall tile (Printed) With customize / Satin white 300x600mm line work Make : -Johnson
4 | Back Wall Tile | TL02 |  |  | Ceramic wall tile white/ Satin white 300x600mm (Plain) Make : -Johnson
C | Counter Cladding Tiles
1 | Tiles |  | Vitrified Tiles | 130X800 | Kajaria -Shesham Oak 130 x 800 mm | Somany - Strio Carrisa Wood Robble 196x1200 | Counter Fascia
2 | Tiles | FF05 | Vitrified Tiles | 130X800 | Kajaria -Shesham Nero 130 x 800 mm | Somany - Strio Salis Wood Wange 196x1200 | Counter & Floor
3 | Tiles |  | Vitrified Tiles | 130X800 | Kajaria - Mahogany 130 x 800 mm | Somany - Strio Rovver wood teak 196x1200 | Counter Fascia
4 | Tiles | FF04 | Vitrified Tiles | 130X800 | Shesham Rosewood 130 x 800 mm | Somany - Strio Hector Wood Teak 196x1200 | Counter & Floor
D | Toilet Tiles
1 | Floor Tile |  | Vetrified Tiles | 300X600 | Kajaria -Fog Perla , Cool cement/ cool silver (Matt Finish) (Size-600x600)mm | Somany -EC sapphire matt 300x300mm | Toilet Detail-770
2 | Wall Tile |  | Vetrified Tiles | 300X600 | Johson- Plain grey 200x300mm | Somany -EC sapphire matt 300x300mm | Toilet Detail-770
3 | Granite |  | Granite stone |  | Jet Black Granite/ Steel grey Granite |  | Toilet Detail-770
E | Corian
1 | Corian Counter |  |  |  | LG ASPEN SNOW - AS 610 | SAMSUNG ASPEN GLOW -AG 636 | REHAU -FORST WHITE 180L
G | Laminates / Veneer
1 | Laminate | LAM 01 | Laminate |  | 14554 RH Hooked Holz Acasia MERINOLAM (Subject to management approval) |  | Generic Drawing
2 | Laminate | LAM 02 | Laminate |  | 21141 Snow White MERINOLAM (Subject to management approval) |  | Generic Drawing
3 | Laminate | LAM |  |  | 5082 LOUSIANA OAK (Subject to management approval)
H | ACP Sheet
1 | ACP sheet for extrnal ceiling |  |  |  | Euro bond- Pure white , code- ER111/ Milky white ER908 (Matt) - Thk 4mm
Alu Décor- Milky white AD202 Matt finish- Thk 4mm
Alstrong-Pure White AL05 Matt finish
I | Paint
| Paint shade | WF 01 | Lustre paint |  | coal mine 8301 Asian Paints |  | Decoration Plan - 140
| Paint shade | WF 02 |  |  | Solemn Grey 8302 (Dark Shade) Asain paint
| Paint shade | WFO3 |  |  | Grey Mtter 8304 Light Shade Asain paint
| Texture | WF 02 | Lustre paint |  | Rain Drop L143, Nickle grey 6126, Grey tint 8435 Asian Paints |  | Decoration Plan - 140
| Metal Paint |  |  |  | Graphite black RAL 9011 Asain Paints (Woodtech spectra)
| Exterior Textured Paint |  | Lustre paint |  | Asain-Fine sand
Spectrum- Grani plast
Grey Mtter 8304 Light Shade
Sl. No. | Product Description | UOM | Qty. per Store | Approved Make | Approved Model No. | Approved Make | Qty per store
1 | 25x25x1500 mm ht. SS Brush finish square handle with lock | Nos. | 2 | Ozone | OGHC-S5(35X1500)SSS | Ozone | 2
2 | Top Pivot Fitting for Glass Door | Nos. | 2 | Ozone | OFS-ACC-TP | Ozone | 2
3 | Floor Spring | Nos. | 2 | Ozone | FS-9400 STD | Ozone | 2
4 | 100 mm wide Double Action SS Hinges | Nos. | 5 | Ozone | OZ-SSBH-SSS | Ozone | 5
5 | Door Closure | Nos. | RO | Dorma | TS 72 |  | RO
6 | Door Handle (22mm Ø x 300mm length) – Single Leaf Flush Door | Nos. | 1 | Dorma | ART No. TGDI30033S | Dorma | 1
7 | Door Lock (for flush doors other than Toilet) | Nos. | RO | Ozone | OZ-NL-22-STD SSS | Ozone | RO
8 | New Chrome Bathroom Vacant –Engaged Indicator Door Lock | Nos. | 1 | DOORCRAFT | SILVER LSTN-10 | Doorcraft | 1
9 | Tower Bolt | Nos. | RO | Ozone | OZ-B-SII | Ozone | RO
I | Adhesives
| Fevicol (Adhesive) | Make - Jivanjor (Multi-purpose Wood Adhesive for long lasting bonds)
| All Rounder (Synthetic Resin Adhesive) | Make - Jivanjor All Rounder is a ready to use premium quality white adhesive specially formulated to give unmatched bond strength, it is also enriched with special preservatives to prevent any bacterial growth during storage therefore providing it with a prolonged life.
| Termilok (Anti Termite wood Preservative) | (Prevents and kills Termites and Borers instantly,Penetrates deep into the wood Eco- Friendly and easy to apply product)
| Champion Super (Synthetic Rubber Adhesive) | Make - Jivanjor (Champion is a high performance synthetic rubber based adhesive with Solvent based Adhesive Fast curing & drying properties ,Delivers superior bond strength.)

## Fire Make
LIST OF APPROVED MAKES FOR FIRE FIGHTING
S.NO. | ITEMS | APPROVED LIST
A | FIRE ALARM SYSTEM
1 | SMOKE/HEAT DETECTOR WITH BASES (UL LISTED/ FM APPROVED) | APPOLO / SYSTEM SENSOR / APOLLO / RAVEL/
2 | FIRE ALARM PANEL (UL LISTED/ FM APPROVED) | AGNI / RAVEL
3 | MANUAL CALL POINT / HOOTER / RESPONSE INDICATOR (UL LISTED / FM APPROVED) | Agni or equivalent
4 | CABLE | POLYCAB / FINOLEX / RR KABEEL
5 | FIRE EXTINGUISHERS | MINIMAX / CEASE FIRE
6 | Hood supression system | Ceasefire/Swastik/Anshul

## Electrical ,CCTV & PA Make
Approved Make List for Electrical / Instrument works
Sr. No | Item Description | Approved Make
1 | Transformer / CSS | Volt amp/ ABB/ Kirloskar/ CG
2 | VCB /HT Breaker Panel | ABB / L&T /Megavin/ Siemens / Schneider
3 | RMU with Cubicle | ABB / L&T /Megavin/ Siemens / Schneider
4 | CT’s / PT’s | L&T/ Siemens/ AE / Indcoil / Kappa / Ricco / Pragati / Megavin
5 | HT Metering | Huphen
6 | LT panels | ABB/ L&T/ Seimens/ Schneider/ Legrand/ Rettal Urmi Technology/Kulaswaminee or Vendors Shall be CPRI / ERDA Approved)
7 | D.B. | Legrand,Schneider,Siemens
8 | Air circuit Breaker | L&T/ ABB / Legrand/ Schneider/ Seimens
9 | MCB / ELCB / RCCB / ISOLATORS / MCCB /DISTRIBUTION BOARDS | L&T/ ABB / Legrand/ Schneider/ Seimens
10 | Surge Protection Device | L&T/ABB/Legrand.
11 | SFU / Fuse Switch Unit | L&T/ ABB / Legrand/ Schneider/ Seimens / Crompton
12 | HRC Fuses | L&T/ ABB / Legrand/ Schneider/ Seimens / Crompton
13 | Capacitor | L & T / Malde/ Epcos/ Trinity
14 | APFC Relay | L & T / GEC / Emercon / Alstom
15 | Contactor / Timer / Starter | L & T / ABB
16 | Relays | L&T/ ABB / Legrand/ Schneider/ Seimens / Crompton
17 | Timer | L&T/ ABB / Legrand/ Schneider/ Seimens / Crompton
18 | Ammeter / Voltmeter / Power factor meter / Frequency meter / Energy meter | Elmeasure/ ABB/ L&T/ Legrand/ Trinity/ Schnieder
20 | Changeover Switch | L&T/ ABB/ C& S
21 | Rotary Switch / Selector Switch | Siemens / L & T / GE / Kaycee
22 | Lightning Pro. System | ABB/ Synergy / Indelec / Stormaster(LPI)/ JEF
23 | UPS | Eaton/ Emerson/ Socomech
24 | Batteries | Exide / Amaron / Panasonic
25 | HT /LT Cables | Polycab/ RR/ KEI/havells
26 | Cables & Wires | Polycab/ RR/ KEI/havells/panasonic
27 | Fire survival cable | AFW / FR Tek / Ravin / Bontn / Tyco
28 | Cable Glands- Double Compression | Dowels / Bracco / Comet
29 | Cable Jointing | Raychem / M Seal
30 | Copper multi-strand wires | Polycab / KEI / RR /Finolex / Gloster
31 | Lugs | Dowels / Bracco / Comet
32 | Cable Tray & Race Ways (Factory Fabricated)& JB | Indiana/ Legrand/ MK/ Globe / Rico Steel
33 | PVC pipes and accessories | Precision / Avonplast / AKG / Modi / Polycab
34 | GI pipes | Zenith / Tata / Jindal
35 | GI Octagonal Poles | Bajaj / Aster / KL Industries
36 | High mast | Bajaj / Transrail
37 | Switches / Sockets / TV, Telephone Socket, etc. (modular)- | L&T/ Legrand / Indoasian/ Anchor ( Wood/Roma ) / MK (Wrapround) / Crabtree (Anthena)
38 | Fan Regulator | MK /Legrand/MDS (To match with the switch / sockets)
39 | Outdoor Boxes | MK/ Clipsal / Henzel / Hunter / Sintex / National
40 | Thermometers
41 | Indicating Meters
42 | Signal Lamps
43 | Push Buttons
44 | Motor / Motor Used in Air wahser | Siemens/ ABB/ Crompton/
45 | Main Fire Alarm Panel (UL / FM / LPCB Approved) | Notifier/Edwards/Simplex/Apollo
46 | Smoke / Heat Detectors with Base (UL / FM / LPCB Approved) | Notifier/Edwards/Simplex/Apollo
47 | Devices & Modules (UL / FM / LPCB Approved) | Notifier/Edwards/Simplex/Apollo
48 | Ceiling fans | Crompton / Havells/ Bajaj / Anchor / Orient / Usha / Khaitan
49 | Exhaust / Pedestal Fan | Crompton / Bajaj / Anchor / Orient / Usha / Khaitan
50 | Fixture | Philips / Crompton /Bajaj / Wipro / LT/ Sudhir
ELV
51 | Telephone Wire / Cables | Finolex / Tata (Lucent) / ITL / Skytone / Gemscab / Delton / National / L&T / Polycab
52 | Television Coaxial Cable | Polycab/ Finolex / RR /RPG / L&T
53 | Network cable | Digisol / Schneider / Avaya/ Systemec / Finolex / Legrand / Dlink
54 | Telephone Instrument | BPL / Tata / Siemens /Avaya / Beetel
55 | Telephone Tag Box | ITL or any equivalent approved make
56 | Automatic Voltage Corrector | Jindal / GES / Muskaan
57 | Annunciator | Areva/ Minilec / Alan
58 | Terminal Blocks | Connect well/ Elmex / Technoplast
59 | Ethernet switch | Sony / Bosch / AVAYA/ Cisco/ Dlink / DigiSol
60 | Patch Panel | AVAYA/ Siemens / Dlink / DigiSol / Legrand
61 | Rack for patch panel & switches | HCL/ Rittal / President / Valrack / Legrand / Digilink
62 | Occupancy Sensor / Day Light Sensor | Siemens, Legrand
63 | BMS system | Siemens.
64 | Cat 6 UTP wire | Legrand, d-link, amps, polycab
65 | Telephone/data wiring accessories | Legrand, d-link, amps, polycab,
66 | 24 port Patch Panel | D-LINK or any other equivalent make
67 | UTP Patch cord | D-LINK or any other equivalent make
68 | Telephone/ TV/ Network poert (modular)- | Legrand/L&T/systimax or Equivalent
69 | Telephone Wire / Cables | L&T / Polycab/ Finolex/ D-link or equivalent
70 | Television Coaxial Cable | Polycab/ Finolex / RR /RPG / L&T
71 | Network cable | Legrand / Dlink/ Digisol / Schneider / Avaya/ Systemec / Finolex /
72 | EPABX | Panasonic/ Systimax/ Avaya / NEC / LG Aria / Siemens / Alcatel
73 | Telephone Instrument | Panasonic/ Systimax/Avaya / Beetel
74 | Telephone Tag Box | ITL or any equivalent
75 | Terminal Blocks | Connect well/ Elmex / Technoplast
76 | Ethernet switch | Sony / Bosch / AVAYA/ Cisco/ Dlink / DigiSol
77 | Patch Panel | AVAYA/ Siemens / Dlink / DigiSol / Legrand
78 | Rack for patch panel & switches | HCL/ Rittal / President / Valrack / Legrand / Digilink
79 | Cat 6 UTP wire | Legrand, d-link, amps, polycab
80 | Telephone/data wiring accessories | Legrand, d-link, amps, polycab,
81 | Conduit | Panasonic/AKG
CCTV
82 | IP IR Box/Bullet Camera | Bosch / Panasonic/ Sony/ Honey well
83 | IP IR Fixed Dome Camera | Bosch / Panasonic/ Sony/ Honey well
84 | IP PTZ Camera | Bosch / Panasonic/ Sony/ Honey well
85 | Network Video Recorder | Bosch / Panasonic/ Sony/ Honey well
86 | POE layer 2 Switch | CISCO/ D-LINK/ ALLIED TELESIS
87 | UTP networking Cat-6 cable | MOLEX/ DLINK/COMSCOPE
88 | Hard disk | WD/ SEAGATE/ Honey well
89 | 40" LED Monitor, Display Resolution : Full HD | LG/ Samsung / Sony
90 | I.S.I. mark Rigid P.V.C. conduit | Precision
91 | POE injector | CISCO or any other equivalent make
92 | Router | D-LINK or any other equivalent make
Emergency Items
93 | Rechargeable torch | Energizer,prolite
94 | Exit signage | Prolite,philips, bajaj
95 | Main Fire Alarm Panel (UL / FM / LPCB Approved) | Notifier/Edwards/Simplex/Morley/System Sensor/Apollo/Ravel
96 | Smoke / Heat Detectors with Base (UL / FM / LPCB Approved) | Simplex /Notifier/Edwards /Morley/ System Sensor/Apollo/Ravel

## Toilet Specs
Dominos Toilet Specifications
Regular Stores
| Current Specs | Alternative 1 | Alternative 2
Faucet | Hindware Quadra | CERA-Ruby -Single Lever Faucets - F1005451 | Parryware VERVE (Ref:T3914A1)
Bottle trap | Quadra | Cera Auxiliaries - Bottle trap | Parryware VERVE (Ref:T3914A1)
Soap Dispenser | Dolphy | Dolphy-Automatic Soap Dispenser -DSDR0112-S | Jaquar Automatic Soap Dispenser Code :SDR-BLC-DJ0160AS
Paper Dispenser/ Hand Dryer | Dolphy | EURONICS-Hand Dryer Metal-EH25NW | Kimberly-Clark Aquarius Multi Fold Paper Towel Dispenser 70220
Wash Basin | Aquant 1719/Hindware Magna | CERA - Casket (New Cat No: S2020108) | Parryware VERVE (Ref:C0453)
WC | Hindware Enigma | Cera EWC - Cambell Clean Rim (Cat. No. S1043136) | Parryware ORRISA (Ref:C021I)
Health Faucet | Hindware ABS | CERA Health Faucet - F8030106AB | Parryware (Ref:T9804A1)
Angle Cock | Hindware Quadra | Cera Angle Valve (Cat No: F1019201) | Parryware - Star Angle valve