## PLUMBING
|  |  | R1 | Date: | 14.03.2024
INTERNATIONAL FOOD HALL @ T1 DELHI -PHE BOQ
SR. No. | DESCRIPTION | UNIT | QUANTITY | RATE (RS. / Unit) | AMOUNT (Rs)
1 | WATER SUPPLY PIPING
Providing & fixing CPVC piping with SDR 11 grade including cutting the pipes to correct length, jointing as per manufacturer recommendation, fixing with ms clamps, including necessary fittings like elbows ,tees,unions reducers,coupling, pipe nipples etc.complete, (Cold and RO water)
1.1 | 20 mm Dia | R.mt | 90
1.2 | 25 mm Dia | R.mt | 15
1.3 | 32mm Dia | R.mt | 25
2 | Copper pipes and tubes shall be hand tempered conforming to requirements of EN 1057 ( formerly BS 2871) Table X , half and the fittings shall confirm the EN-1254-I ( Formerly BS 864: part-02). The fittings shall be end feed capillary fittings within wall/ceiling / floor including cutting & chasing the wall/ floor, jointing, making connection to fixtures, equipment and piping with purposes made connectors, etc. including insulation of closed cell elastomeric nitrile rubber. thermal conductivity of elastometric nitrile rubber shall not exceed 0.038w/m deg K. The insultaion should have fire performance and thickness of nitrile rubber should be 9mm (for hot water piping)
2.1 | 20mm Dia | R.mt | 30
2.2 | 25mm Dia | R.mt | 20
3 | Providing & Fixing of forged brass lever operated Ball Valves (10Kg/Sq.cm). Valve shall have with unions.
3.1 | 20mm Dia | Nos. | 13
3.2 | 25mm Dia | Nos. | 3
3.3 | 32mm Dia | Nos. | 1
4 | Providing ,fixing, testing and commissioning Water Meter as per requirement of IS 779:1994 including providing & fixing matching Isolation valves ,strainer, non-return valve,complete with all necessary fittings etc screwed type(15Kgs/Sq.cm). Valve shall have with union.
4.1 | 32 mm Dia incoming line | Nos. | 1
4.2 | 25 mm Dia incoming line | Nos. | 1
5 | Supply, installation,testing & commissioning of Storage Type Electric Hot Water Generator of mentioned capacity, suitable for 3 KG/cm2 pressure, Wall Mounted / Floor standing type, with Auto Shut-off Thermostat, along with isoltion Valves, Air Release valve, SS flexible connections andall other std accessories
5.1 | 100 L Capacity- | Nos. | 1
5.2 | 25 L Capacity- | Nos. | 1
6 | SITC of Eco smart RO-100 with all required accessories and inbuild storage | Nos | 1
7 | SITC of Eco smart RO-50 with all required accessories and inbuild storage | Nos | 2
8 | RO PACKAGE PLANT-Supply , installations, testing and comminissioning of Package RO plant 200 Lit/Hr including required pressure pumps /panel/ pressurised tank if any , all assesories, valves and membrance cleaning system, ultra-violet sterilizer, internal piping, presure gages etc (System shall be Auto fill stop and Auto empty start mechanisam) | Nos. | 0
9 | Supply, Installation, Commissioning & Testing for Booster pump for Ro water supply WITH FLOW SWITCH GRAVITATIONAL FLOW (top to bottom flow) with both side Sensor operations- A) 3CUM PER HR. B) HEAD: 25M, C) PHASE: SINGLE PHASE, D) PROTECTION: IP55, E) MONOBLOCK TYPE, with sensors cabling & Control panel.(Pump shall be Auto fill stop and Auto empty start mechanisam)
9.1 | 1 HP | Nos. | 0
9.2 | 1.5 HP | Nos.
10 | Supply, Installation of sintex loft mounted water tank of 500 Ltrs | Nos. | 0
11 | P/F water level Indicator on loft water tank by means of a transparent clear tube fixed along height of the water tank hence making water level visible | Nos. | 0
A | TOTAL OF WATER SUPPLY
B | DRAINAGE
1 | UPVC-SWR pipes (working pressure 10kg/cm2) conforming to IS 13592/92 and IS 14735-type-B solvent posted ( for Dia above 50mm) and for ( Dia below 50mm) shall be as per IS 4985 and 7834 Class-05 (10 kg/cm2) including cutting the pipes to required lengths, laying in the position to required grade and level, jointing, supporting with PVC cleat,hot deep galvanised bracket supports,hot deep galvanised nut-bolts, anchor fastners, PVC coated U-clamp, testing and rectifying leakages for piping within vertical shafts / supported on wall / hung below slab etc. with all material & labor complete and as directed. [The Rate shall include supply and fixing of nesessary items] Vertical line bracket shall be fixed at every 0.8 mtr to 1.00 mtr.]
1.1 | 32mm Dia | R.mt | R.O.
1.2 | 40mm Dia | R.mt | 5
1.3 | 50mm Dia | R.mt | 10
1.4 | 65mm Dia | R.mt | 35
1.5 | 75mm Dia | R.mt | 30
1.6 | 100 mm Dia | R.mt | 70
2 | Supply, Install PVC multi floor Traps including fixing with necessary consumables with Circular SS Grating with anti cockroach jali Suitable for taking 40mm Dia / 50mm Dia Back Inlet Connection with 75mm Dia outlet | Nos. | 20
3 | Supply, Install PVC floor Traps including fixing with necessary consumables with Circular SS Grating with anti cockroach jali Suitable for 75mm Dia outlet | Nos. | 8
4 | Supply, Install PVC clean out plugs including fixing with necessary consumables
4.1 | 50mm Dia | Nos. | R.O.
4.2 | 40mm Dia | Nos. | R.O.
5 | Supply, Installalation , testing commissioning of S.S. Grease trap nurgreen Make -NGT 70 ( 104 lit) | Nos. | 0
6 | Supply, Installalation , testing commissioning of S.S. Grease trap nurgreen Make -NGT 50 ( 72 lit) | Nos. | 2
7 | Supply, Installalation , testing commissioning of S.S. Grease trap nurgreen Make -NGT 20 ( 34.3 lit) | Nos. | 5
A | TOTAL OF DRAINAGE
7 | S .S Grating - Only Installation
a | Only installation of S.S Grating size, 300mm x 300mm, in 16 swg 25mm x25mm Square Pipe around the Frame and 20mmX 20mm Square pipe in center of frame with SS perforated tray (304 SWR). Complete as per architectural detail drawing & Site Engineer's instruction. (100 mm Dia S.S 304 grade finish unions reducers/coupling or 75mm Dia S.S 304 grade finish unions reducers/coupling or 50mm Dia S.S 304 grade finish unions reducers/coupling) | Nos. | 8
b | Only installation of S.S Grating size, 600mm x 300mm, in 16 swg 25mm x25mm Square Pipe around the Frame and 20mmX 20mm Square pipe in center of frame with SS closed tray (304 SWR). Complete as per architectural detail drawing & Site Engineer's instruction. (100 mm Dia S.S 304 grade finish unions reducers/coupling or 75mm Dia S.S 304 grade finish unions reducers/coupling or 50mm Dia S.S 304 grade finish unions reducers/coupling) | Nos. | 4
c | Only installation of S.S Grating size, 1200mm x 300mm, in 16 swg 25mm x25mm Square Pipe around the Frame and 20mmX 20mm Square pipe in center of frame with SS perforated tray (304 SWR). Complete as per architectural detail drawing & Site Engineer's instruction. ( at hook up point) | Nos. | 1
d | Only installation of S.S Grating size, 600mm x 600mm, in 16 swg 25mm x25mm Square Pipe around the Frame and 20mmX 20mm Square pipe in center of frame with SS perforated tray (304 SWR). Complete as per architectural detail drawing & Site Engineer's instruction. (100 mm Dia S.S 304 grade finish unions reducers/coupling or 75mm Dia S.S 304 grade finish unions reducers/coupling or 50mm Dia S.S 304 grade finish unions reducers/coupling) | Nos. | 2
d | Only installation of S.S Grating size, 600mm x 600mm, in 16 swg 25mm x25mm Square Pipe around the Frame and 20mmX 20mm Square pipe in center of frame with SS perforated tray (304 SWR). Complete as per architectural detail drawing & Site Engineer's instruction. (100 mm Dia S.S 304 grade finish unions reducers/coupling or 75mm Dia S.S 304 grade finish unions reducers/coupling or 50mm Dia S.S 304 grade finish unions reducers/coupling) | Nos. | 2
B | TOTAL OF DRAINAGE
C | SANITARY AND C. P. FITTINGS & FIXTURES
Only installation, testing and commissioning of sanitary and C.P. fittings (Model no. to be specified by Arch)
1.1 | EWC with seat cover | Nos | 0
1.2 | Concealed flush tank | Nos | 0
1.3 | Concealed flush valve | Nos | 0
1.4 | Health Faucet | Nos | 0
1.5 | 2 Way Bib-Cock with connection for Health Faucet | Nos | 0
1.6 | Bided | Nos | R.O.
1.7 | Under Counter Wash Basin including waste Coupling | Nos | 0
1.8 | Wash Basin Cock | Nos | 0
1.9 | shower and mixer | Nos | 0
1.1 | Jet Spray | Nos | 0
1.11 | Bath Tub including waste Coupling and nessessary connections | Nos | 0
1.12 | Under Counter Sink including waste Coupling | Nos | 10
1.13 | Sink Pillar Cock | Nos | 10
1.14 | Bottle Trap for WHB/ sink and urinal with all connecting pipes | Nos | 10
1.15 | Angle Cock with PVC pipe connection upto WHB/sink/Geyser connection | Nos | 32
1.16 | Urinal | Nos | 0
1.17 | Auto Flush Valve & Sensor with connecting piping & spreader for urinal(DC) | Nos | 0
SUB TOTAL -C-SANITARY AND C. P. FITTINGS & FIXTURES ( ONLY INSTALLATIONS)
GRAND - TOTAL A , B, AND C
NOTES :
1) Taxes and duties shall be Extra as actual
2) Contractor to read the drawings with BOQ and quote accordigly, Deviation if any shall be confirmed by contcator prior to finalise the order.