## TechItemDoc
ItemCode | Item Name | UOM | Qty | Unit Price | Remarks
I | PANEL & SWITCHGEAR
1 | Supply, installation, testing & commissioning of free standing, floor mounting compartmentalized panels fabricated out of CRCA sheet steel sections after carrying out 7 tank cleaning process and duly powder coated using Siemens Grey Shade No. RAL 7032. The frame structure, doors and gland plates shall have 2.0 mm thick sheets and partitions shall be with 1.6 mm thick CRCA sheet. Base channel size 75 x 40 x 6 mm of ISMC shall be provided. The panel shall be dust and vermin proof with neoprene gasket. The doors shall be provided with concealed hinges and with brazing wherever required to avoid deformation and shall be earthed. The bus bar shall be of tinned Copper with epoxy supports and shall be insulated with colour coded heat shrink sleeves. The control wiring min. 2.5 Sq.mm shall be FRLS type. The Panel shall be provided with CTs, phase indication lamps, meters, relays and all switchgear, etc. as per the SLD. The panel shall be complete in all aspects as per the final approval of the Consultant.
Special Note: Both the main panels of zone-1 & 2 shall be provided with CQRS (Ceasefire Quick Response System with 2 kg FM-200 gas flooding system complete with sensors located in the panels. Make - Ceasefire/Kalpex / Eqv.
A | Providing & installing MAIN PANEL (ZONE-1) as per SLD & Spec.: | Set | 1
100 Amps 4 pole, 25kA MCCB as a Incomer with MP based LSIG protection, Conserv make (or eqv.) EM6400 Energy manager with 4A SP MCB with 100/5A-3 Nos., 10VA, CL-1 CT's for metering & AE make and indicating lamps for RYB and on-off-trip etc. for detail refer the SLD.
Busbar chamber - 1 set, 4 pole 200A Tinned AL. Busbar with necessary
OUTGOINGS:
i) 63A 4P MCCB with electromagnetic LSIG protections– 3 Nos.
ii.) 40A 4P MCCB with electromagnetic LSIG protections – 4 Nos.
iii.) 32A 4P MCCB with electromagnetic LSIG protections – 1 Nos.
iv) 32A 4P ELMCB with 30 mA sensitivity – 1 Nos.
v.) 32A 2P MCCB with electromagnetic LSIG protections – 1 Nos.
vi.) DOL stsrters, 1.1 kW as indicated in the SLD and with a provision to connect a Start-Stop push button station from remote. - 2 Nos.
vii.) DOL stsrters, 5.5 kW as indicated in the SLD and with a provision to connect Start-Stop push button station from remote. - 1 Nos.
B | Providing & installing MAIN PANEL (ZONE-2) as per SLD & Spec.: | Set | 1
320 Amps 4 pole, 25kA MCCB as a Incomer with MP based LSIG protection, Conserv make (or eqv.) EM6400 Energy manager with 4A SP MCB for control circuit with 320/5A-3 Nos., 10VA, CL-1 CT's for metering & AE make and indicating lamps for RYB and on-off-trip etc. for detail refer the SLD.
Busbar chamber - 1 set, 4 pole 400A Tinned AL. Busbar with necessary supports etc.
OUTGOINGS:
i) 100A 4P MCCB with electromagnetic LSIG protections– 1 Nos.
i) 63A 4P MCCB with electromagnetic LSIG protections– 5 Nos.
ii.) 40A 4P MCCB with electromagnetic LSIG protections – 1 Nos.
iii.) 32A 4P MCCB with electromagnetic LSIG protections – 1 Nos.
iv) 63A 4P ELMCB with 30 mA sensitivity – 1 Nos.
iv) 32A 4P ELMCB with 30 mA sensitivity – 1 Nos.
vi) 25A 4P ELMCB with 30 mA sensitivity – 1 Nos.
vii) 16A 4P ELMCB with 30 mA sensitivity – 1 Nos.
viii.) DOL stsrters, 0.75 kW as indicated in the SLD and with a provision to connect a Stsrt-Stop push button station from remote. - 1 Nos.
ix.) DOL stsrters, 1.1 kW as indicated in the SLD and with a provision to connect a Stsrt-Stop push button station from remote. - 2 Nos.
vii.) DOL stsrters, 5.5 kW as indicated in the SLD and with a provision to connect a Stsrt-Stop push button station from remote. - 1 Nos.
1 | Supply, installation, testing & commissioning of Switchgears. (Standard Product)
a | 100 amps 4P MCCB with thermal magnetic releases in FRP enclosure, IP-65, complete with all mounting accessories – for 34 TR VRF ODU | Nos. | 1
b | 32 amps 4P MCB 'C' TYPE in FRP enclosure, IP-65, complete with all mounting accessories – for 3.5 TR DX ODU. | Nos. | 1
d | 63 amps 4P MCB with 63A 5 Pin Industrial Socket complete with all mounting accessories (for induction cook top) | Nos. | 1
e | 32 amps 4P MCB with 32A 5 Pin Industrial Socket complete with all mounting accessories (for Pasta Cooker & Electric Fry Top) | Nos. | 2
II | UPS & BATTERY
1 | Supply, Installation, testing and commissioning of 4.0 KVA UPS System with 1-Phase I/C & 1-Phase O/G complete with 30 Minutes Battery Back-up and the required accessories as specified in the drawings & the specifications. | Set | 1
III | DISTRIBUTION BOARDS
Supply, installation, testing & commissioning of Distribution Boards surface / flush mounted with Double door containing MCB/ELMCB as incomer and SPMCB as outgoing. All MCBs are of 10KA breaking capacity and ELMCBs/RCCB should be of 30mA/100 MA sensivity. The DB shall have appropriate no. of top and bottom knock outs for outgoing circuits and shall be complete with necessary busbars, interconnection terminals and earth studs. All terminations in DB shall be complete with ferulling, dressing and all circuits shall be properly labeled with PVC strip (sticker type) having identification as per the final approval of Consultant. For UPS DB MCB shall be 'D' type and other MCBs shall be 'C' category for lighting and raw power DB LEGRAND/HAGER/SCHNEIDER.
1 | VTPN DB | Nos. | R.O.
4 way TPN DB
Incomer:
63A 4P MCB 10kA – 1no.
Outgoings 63/25 SP MCB, 'C' Type – 4 Nos
2 | Lighting Distribution Board (LDB) | Nos. | 2
8+2 way TPN PPI DB
Incomer:
32/40A 4P MCB 10kA – 1no.
Subincomer:
32A DP ELCB 30mA - 3 nos
Outgoings :6/10 SP MCB, 'B' Curve Type – 24 Nos
2 | Small Power Distribution Board (For small power and SPA) | Nos. | 3
6+2 way TPN PPI DB
Incomer:
32/40A 4P MCB 10kA – 1no.
Subincomer:
40A DP ELCB 30mA - 3 nos
Outgoings :10/16/20 SP MCB, 'C' Type – 18 Nos
3 | Power Distribution Board (For Bar/Office/Store, Buffet Counter-1 & 2) | Nos. | 3
8+2 way TPN PPI DB
Incomer:
63A 4P MCB 10kA – 1no.
Subincomer:
63A DP ELCB 30mA - 3 nos
Outgoings: 10/16/20 SP MCB, 'C' Type – 24 Nos
4 | Power Distribution Board (For Beaverage Station and Sports Lounge) | Nos. | 1
6+2 way TPN PPI DB
Incomer:
63A 4P MCB 10kA – 1no.
Subincomer:
63A DP ELCB 30mA - 3 nos
Outgoings: 10/16/20 SP MCB, 'C' Type – 18 Nos
5 | UPS LDB | Nos. | 1
12 way SPN DB
Incomer: 25A DP MCB
Outgoings :6/10A SP MCB, 'C' Type – 8 Nos
TOTAL FOR DISTRIBUTION BOARDS
IV | CABLES & ACCESSORIES
Note : Make a provision for suspenders as per site ceiling requirement.
Supply & installation of following armoured LT cables (XLPE insulated, Cu/Al conductor, ST-2 rated inner FR PVC sheath and FRLS PVC outer sheath) rated for 1100 volts AC as per IS standard 1554 Part 1 and IS: 7098, Part-1. with necessary M.S. clamps. All cables shall be properly clamped or tied when run on cable trays. All such cables shall be provided with temporary labelling at every 20 mtrs and ten finally with metal identification tags showing the size and the location from/to the specific Panel/DB at both ends.
4 | 4C x 16 Sq. mm CU. Armoured XLPE CABLE (For VRF ODU, PDB for Beverages/Sports) | Mtr. | 125
5 | 4C x 10 Sq. mm CU. Armoured XLPE CABLE (for induction cook top, DBs, Buffet counter KPDB) | Mtr. | 135
6 | 4C x 6 Sq. mm CU. armoured XLPE Cable (For electric fry top, SPA DB, SPA Geyser, LDB, small power DB etc) | Mtr. | 225
7 | 4C x 4 Sq. mm CU. armoured XLPE Cable (For DX ODU, 20 TR CSU, Pasta Cooker, Induction WOK, Floor AHU etc,)) | Mtr. | 275
8 | 4C x 2.5 Sq. mm CU. armoured XLPE Cable (Exhaust, FA fans, CSUs etc) | Mtr. | 250
10 | 3C x 6 Sq. mm CU. Unarmoured XLPE Cable (For UPS I/P and output upto the isolator) | Mtr. | 35
13 | 3Rx1Cx6 Sq.mm YY FRLS Cable (Cu) (For UPS I/P, O/P from isolator) in flexible metallic conduit. | Mtr. | 35
B | Termination of following sizes of cables with Single compression cable gland.
1 | 3.5C x 185 Sq. mm AL. Armoured XLPE CABLE | Nos. | 2
2 | 3.5C x 120 Sq. mm AL. Armoured XLPE CABLE | Nos. | 2
4 | 4C x 16 Sq. mm CU. Armoured XLPE CABLE (For VRF ODU, PDB for Beverages/Sports) | Nos. | 6
5 | 4C x 10 Sq. mm CU. Armoured XLPE CABLE (for induction cook top, DBs, Buffet counter KPDB) | Nos. | 8
6 | 4C x 6 Sq. mm CU. armoured XLPE Cable (For electric fry top, SPA DB, SPA Geyser, LDB, small power DB etc) | Nos. | 8
7 | 4C x 4 Sq. mm CU. armoured XLPE Cable (For DX ODU, 20 TR CSU, Pasta Cooker, Induction WOK, Floor AHU etc,)) | Nos. | 8
8 | 4C x 2.5 Sq. mm CU. armoured XLPE Cable (Exhaust, FA fans, CSUs etc) | Nos. | 8
9 | 3C x 4 Sq. mm CU. armoured XLPE Cable | Nos. | 8
10 | 3C x 6 Sq. mm CU. Unarmoured XLPE Cable (For UPS I/P and output upto the isolator) | Nos. | 4
13 | 3Rx1Cx6 Sq.mm YY FRLS Cable (Cu) (For UPS I/P, O/P from isolator) in flexible metallic conduit. | Nos. | 6
TOTAL FOR CABLES & ACCESSORIES
V | POINT WIRING & ACCESSORIES
Note : Make a provision for suspenders as per site ceiling requirement.
1 | Wiring of circuit mains from DB to the switchboards or power points.
a | 3RX2.5 sq.mm FR-LSH insulated multistrand copper conductor wires, 1.1 kV grade, in G.I. Conduits of 20 mm dia | Mtrs. | 1750
b | 2RX4 sq.mm + 1R X 2.5 sq. mm. FR-LSH insulated multistrand copper conductor wires, 1.1 kV grade in G.I. Conduits of 20 mm dia | Mtrs. | 2750
2 | SWITCH OPERATED LIGHT POINT WIRING
Supply, installation, testing & commissioning of point wiring for lights / plug points / bell point etc. in G.I. conduit of suitable diameter, surface or recessed mounted complete with junction box, joints, bends, switch box, cover plate etc. including 1.1kV grade 2 x 2.5+ 1 x 1.5 sq.mm. (Primary Points) Copper multi-stranded PVC insulated FRLS wires and 2 x 1.5 + 1 x 1.5 sq.mm. (Secondary Points) Copper multi-stranded PVC insulated FRLS wires, along with 6A modular surface/ recessed mounted switch, ceiling rose, connectors switch boxes etc. The work shall be completed with all material, labour, chiselling, making good surface etc. in cordination with civil agency complying with IE rules, regulations, standards & local supply authority requirements. All G.I. conduit pipes, FRLS wires shall be considered) Note: 1) The cost of Circuit Wiring from DB to switch board and switch board to switch board shall be covered by wiring of circuit mains
a | Primary point | Each | 55
b | Secondary point | Each | 85
3 | MCB OPERATED LIGHT POINT WIRING (DIRECT FROM LDB)
Supply, installation, testing & commissioning of point wiring for lights / plug points / bell point etc. in G.I. conduit of suitable diameter, surface or recessed mounted complete with junction box, joints, bends, switch box, cover plate etc. including 1.1kV grade 2 x 2.5+ 1 x 1.5 sq.mm. (Primary Points) Copper multi-stranded PVC insulated FRLS wires and 2 x 1.5 + 1 x 1.5 sq.mm. (Secondary Points) Copper multi-stranded PVC insulated FRLS wires, along with 6A modular surface/ recessed mounted switch, ceiling rose, connectors switch boxes etc. The work shall be completed with all material, labour, chiselling, making good surface etc. in cordination with civil agency complying with IE rules, regulations, standards & local supply authority requirements. All G.I. conduit pipes, FRLS wires shall be considered) Note: The first point shall be considered in running meters with 3X2.5 sq. mm wires. The loop poins shall be considered as secondary point shall be with 3X1.5 sq.mm wires with an average length of 10 metres.
a | Primary point | Each | 35
b | Secondary point | Each | 77
POWER POINT WIRING
4 | Supplying, erecting , testing & commissioning independent surface or recessed mounting modular 5A switch & 5/15A sockesocket complete with switch box, internal wiring with required chiseling making good surface etc...in coordination with civil agency complying with IE rules, regulations, standards & local supply authority requirements. as per final approval of Architect/Consultant. (3X2.5 sq.mm wires for primary shall be multistrand copper conductor, FR-LSH type in G.I. conduit) Excluding of switch socket. (First power point shall be measure as per circuit mains wiring. The secondary is power point shall be about 5Mtr.
| Secondary point | Nos. | 35
5 | Supplying, erecting , testing & commissioning independent surface or recessed mounting modular 15A switch & socket complete with switch box, internal wiring with required chiseling making good surface etc...in coordination with civil agency complying with IE rules, regulations, standards & local supply authority requirements. as per final approval of Architect/Consultant. (4sq.mm Wires shall be for primary FRLS type & G.I. conduit ) Excluding of switch socket. (First power point shall be measure as per circuit mains wiring. The secondary is power point shall be about 5Mtr.
| Secondary point | Each | 30
6 | Supply and installation of Perforated Cable Tray out of 14 gauge GI sheet complete with necessary fixing arrangement with Anchor Fastener and all other accessories as per the final approval of the Consultant/Architect. Note: Make a provision for suspenders as per site ceiling requirement.
a | 450 x 50 x 2mm | Mtr. | 30
7 | Supply and installation of AL raceway with 2 mm thickness & proper ties/clamps at appropriate intervals & as per the route approved by Architect/Consultant. (Cost of cutting the floor for laying of raceways to be included).
a | 2 runs of underfloor AL raceways of size 100 x 40 mm (Type-A) | Mtr. | 47
b | 1 runs of underfloor AL raceways of size 100 x 40 mm | Mtr. | 5
c | 1 runs of underfloor AL raceways of size 85 x 38 mm | Mtr. | 18
d | 1 runs of underfloor AL raceway of size 65 x 38 mm | Mtr. | 75
e | 2 runs of underfloor HMS grade uPVC Conduit Pipes 25 mm dia | Mtr. | 72
8 | Supply & installation of GI junction boxes with 2 mm thickness, 2mm thick SS cover with 2” extra on all sides SS cover on top and having screw fixed plates on all four sides with knock out holes for conduits. The plates shall be retained on the sidezs having no conduit or raceway so as to avoid the entry of any unwanted material. Earth stud to be provided for all Junction boxes for earthing. Junction box to be prepared as per the final approval of Architect/Consultant. The junction boxes shall be protected from the entry of unwanted material till the completion of the project & the SS plates shall be installed after the final polishing of flooring.
Note:
a | 450 x 450 x 50 mm | Nos. | 5
b | 50 x 350 x 50 mm | Nos. | 5
c | 250 x 250 x 50 mm | Nos. | 25
d | 150 x 150 x 50 mm | Nos. | 38
e | Waterproofing of Junction Boxes in the planter box area by applying Sealing compound, NEER of Emerson make (or eqv.) | Nos. | 10
9 | Supply, installation of temporary lighting & power arrangement for construction purpose of with industrial type switch & sockets/MCB's/ELCB's & lighting fittings as required to finish the work for interior contractor & necessary electrical protections throughout the site for construction work till the handover of site. Contractor shall maintain the saftey rules & regulations as per Airport Security Department. The material shall be taken back by the contractor, also included scaffolded work at site during excution. | Job | 1
10 | Supply, installation, testing & commissioning of modular type flush mounted plate type switch and switch + sockets with hot dipped GI box complete as per the final approval of Architect/Consultant
a | 6A one way plate type switch | Nos. | 55
c | 6A 5pin switch socket outlet (Raw/UPS power) + USB | Nos. | 36
c | 6/16A 5pin switch socket outlet (Raw/UPS power) + USB | Nos. | 40
d | 2nos 6/16A 5pin switch socket outlet (Raw power) | Nos. | 18
e | 3 nos. 6/13A socket controlled by 1no 16A switch + USB | Nos. | 12
g | 1 nos. 16A socket controlled by 1nos 16A switch | Nos. | 6
h | RG6 coaxial TV outlet | Nos. | 12
11 | Supply, installation, testing & commissioning of industrial type plug and sockets conforming to IEC-60309 of Make-C & S / Legrand / Havells or eqv.
h | Industrial Socket, panel/surface mounting type, IP-67, 63 Amps, 5-Pin, 3P+N+E, 415 V, 3-Ph, with 4-P MCB of 63A (For Induction Cook Top) | No. | 1
i | Industrial Socket, panel/surface mounting type, IP-67, 32 Amps, 5-Pin, 3P+N+E, 415 V, 3-Ph with 4-P MCB of 32A. (For Pasta Cooker, Elect. Fry Top & Induction WOK) | Nos. | 3
j | Industrial Socket, panel/surface mounting type, IP-67, 32 Amps, 3-Pin, 2P+E, 230 V, 1-Ph with 2-P MCB of 16/20/32A. (For Kitchen and Buffet Counter as required) | Nos. | 10
12 | Supply & installation of G.I. conduit with pull box / junction box & all accessories.
13 | Providing Television wiring inside 25mm dia GI conduit from each TV outlet to LV Shaft by using coaxial cable of type RG 6. Tinned copper conductor with necessary accessories viz. deep junction boxes, inspection boxes bends, termination etc. | RM | 450
14 | SITC of following Splitter unit in Metal enclosure for Cable TV.
14.1 | 4 way Splitter | Nos. | 1
14.2 | 6 way Splitter | Nos. | 1
TOTAL FOR WIRING & ACCESSORIES
EARTHING
1 | Supply & erection of G.I. strip of 25 x 3 mm used for earthing of DBs, AHUs, ODUs etc. by laying on wall, cable trays with necessary clamps fixed on wall painted with bituminous paint in an approved manner. | Mtr. | 350
2 | Supply & erection of G.I. strip of 40 x 5 mm used for earthing of Main Panels by laying on wall, cable trays with necessary clamps fixed on wall painted with bituminous paint in an approved manner. | Mtr. | 450
3 | 1 no. 4 sq. mm YY cable in 25mm G.I. conduit for earthing forUPS, networking and other ELV applications.etc | Mtr. | 250
4 | Supplying & erecting bare copper conductor of 8 swg for earthing purpose. As required. | Mtr. | 50
5 | Supplying & erecting bare GI conductor of 8 swg for earthing purpose | Mtr. | 125
7 | SITC of Earthing terminal Box for distribution with 40X5 mm G.I. strip of 300 mm length. | Nos. | 1
8 | SITC of Earthing terminal Box for distribution with 25X6 mm Copper strip of 300 mm length. | Nos. | 1
TOTAL FOR EARTHING
MISCELLANEOUS
1 | Supply, fabrication and erection of M.S. Structural steel such as base mounting frames, brackets & supports for installation of panels, cable tray etc.from M.S channel, angle, flats as per the requirement with painting of one coat of red oxide primer and two coats of approved shade of epoxy paint. | kgs. | 1500
1 | Supply & fixing of the best quality LT Danger Boards(415V) for of approved shape and size as specified by the local electrical authorities written in English, and local Language | Nos. | 2
2 | Supply & handed over to client of First Aid Box | Set | 2
3 | Supply of 2M x 1M Rubber mat as per IS 15652:2006, 2mm thick, suitable upto 3.3 KV, fire retardant, no effect of acids, alkalies and transformer oils, moisture proof, high tensile strength and texture finish / cloth impression (Anti slip, marking on top) . Make – DOZZ or equivalent | Nos. | 4
| Supply & fixing in position approved shock treatment chart written in English, Hindi and Gujarati. These charts shall be put in wooden frame & covered with clear glass. | No. | 2
| Fire Extinguisher 4.5 Kg (BCE Type). | No. | 2
| Liaisoning with electrical inspector for necessary approvals of electrical installations. | LS | 1
II | PA & MUSIC SYSTEM CONTAINMENT (BIAMP - 8600)
Note: The PA system shall be integrated with Fire Alarm System to activate evacuation message at preset loud volume in case of emergency
1 | Supply, Installation, Testing & Commissioning of 6 Zone Controller (Make - BIAMP), Location - Reception | Nos. | 1
2 | Supply, Installation, Testing & Commissioning of 6W ceiling mount speaker. (Make - BIAMP) | Nos. | 30
3 | Supply, Installation, Testing & Commissioning of 12W Wall Mounted Speaker. (Make - BIAMP) | Nos. | 6
4 | Supply, Installation, Testing & Commissioningof 300W Booster amplifier with zone controller (BIAMP), Location - Reception | Nos. | 1
5 | Audio Message Manager | No. | 1
6 | Desk Microphone, (6-Zone Call Station), Location - Reception | No. | 1
7 | Supply and laying of 2 Core Speaker Cable including 25mm G.I. conduit. | Mtr | 1250
8 | Required connectors, jumper patch cables etc & other accessories required. | Lot | 1
I | DATA, WIFI & TELEPHONE SYSTEM
1 | Supplying,Installation,Testing and Commissioning of CAT 6 cable for & Data connectivity pulled in G.I. conduit. | Rmt | 2150
2 | Supplying,Installation,Testing and Commissioning of CAT 6 cable for Telephone & Data connectivity pulled in Al raceways laid already. | Rmt | 1880
3 | Supply, Installation of CAT 6 Information Outlet
a | DATA OUTLET | Nos. | 48
b | WI-FI | Nos. | 10
c | CCTV | Nos. | 33
4 | Supply, installation & Configuration of Network Switch EX 4200, 24-port 10/100/1000BaseT (24 ports PoE+) with 1x930W AC PS PART NO. EX4200-24PX. | Nos | 2
5 | Supply, installation & Configuration of Network Switch EX 4200, 48-port 10/100/1000BaseT (48 ports PoE+) with 1x930W AC PS PART NO. EX4200-48PX. | Nos. | 1
6 | Supply, installation of 27 U Wall Mount Rack with Std. Accessories & required mounting Hardware ( WQ ) Black | Nos | 1
8 | Supply, installation of Dual band (5 GHz and 2.4 GHz concurrent) Mid – Range 802.11n Wireless Access Point + Power Adaptor + PoE Injector + Ceiling Mounting Kit. | Nos | 10
Distributed Antenna System (DAS)
10 | SIGNAL MAP ANALYSIS TEST FOR MOBILE NETWORK : Carry out tests for signal strength to plan DAS network. | LS | 1
10.1 | Supply, installation, testing and commissioning of Antenna points suitable for 4-Band coverage, low or medium power as shown in the layout. | Nos. | 8
10.2 | Supply, installation and termination of RG-6 coaxial cable in GI conduits of 25 mm dia | Mtrs. | 530
10.3 | Termination and integration at the main existing DAS antenna point | LS | 1