## Plumbing
TFS DWARKA BASE KITCHEN MATIYALA
SUB HEAD A: SANITARY FIXTURES & FITTINGS
S.NO. | DESCRIPTION | QTY | UNIT | RATE | AMOUNT
SUB-HEAD E : PUMPS & EQUIPMENTS
1 | Supplying, installing, testing & commissioning Horizontal centrifugal pump set with C.I. casing, Bronze Impeller, SS shaft suitable for operation on 400/440 volts, 3 phase 2900 RPM electric motor,100 mm dia pressure guage, G.M. isolation cock complete as required. Cyclic operations shall be provided for each set of two pumps.Cost shall included electrical control panel with wiring/cabelling/control cabelling.
a) | Raw Water Pumps
Location - Plant room at terrace level
Number of Pumps = 2 Nos
Capacity 2 LPS each
Head 25 Mts
| RPM 2900 | 1 | SET |  | 0
NOTES FOR ALL PUMPS :-
a) Level Controller with sufficient nos. of low / high level alarms, contacts with electrodes and control wiring for the automatic operation of all water supply pumps to achieve the functional requirement shall be provided. Control wiring between these pumps and water tanks shall be provided. Raw water pumps must start at low level of water in domestic water tank & stop at high water level in that tank. Dry running protection shall be provided for the pumps.
2 | Supplying, installing, testing & commissioning vertical inline pumps with S.S. casing, S.S. impeller. mechanical seal, S.S. Shaft directly coupled to motor suitable for operation on 400/440 volts, 3 phase 2900 RPM. TEFC electronic motor mounted on a common channel baseplate 150mm dia pressure gauge, G.M. gauge, G.M. isolation cock.Location Plant Room at terrace level.
i) | Control panel with pressure switch, electrical wiring, cabling from panel to pumps, level controller complete with all accessories.
ii) | CPVC-SDR-11 suction and discharge header with valves & vibration isolator at suction side of header & discharge side of header.
iii) | Set of accessories such as Pressure Switches, Connecting Power & Control Cabling etc.
Hydropneumatic system for Domestic water supply system with 1 No. Precharged vessel of minimum capacity of 100 Lts(minimum) with interchangeable butyl rubber membrane connected to outlet header with necessary flanges, gaskets, isolation valves, nuts, bolts etc. complete.-For feeding Domestic water. Variable Speed.
Capacity 2 LPS (each pump)
Head 20 Mts.
RPM 2900
No. of pumps 2
| Hydropneumatic system as described above | QR | SET
3 | Providing, fixing, testing & commissioning of vertical FRP pressure filter complete with initial charge of filter media frontal piping with valves including testing kit, complete as required.(Location plant room at terrace level).
a) Filter for Domestic Water.
Tested pressure 6Kg/Sq.cm
| Capacity 2 LPS. | 1 | SET |  | 0
4 | Supply, installation, testing & commissioning of chlorine dosing system consisting of one FRP/ HDPE tank of 100 liters capacity with a positive displacement diaphragm Dosing pump with a variable flow rate of 0-12 LPH. The motor shall be suitable for operation at 240 V /one phase/ 50 Hertz supply. The pump shall be supplied complete with necessary poly propylene piping, valves, strainers & injection fittings for system to dose solution to the feed line. The pump shall be Asia LMI make. (Location plant room at terrace level). | 1 | SET |  | 0
5 | Providing, fixing, testing & commissioning of FRP body water softener with frontal piping valves complete with Resin, Hydraulic Brine Injector, HDPE Brine tank of capacity one generation,Remi make mixing motor and all other accessories complete as required.
a) Softner for domestic water. Location -Plant Room at terrace level.
Input water Hardness(appx) =700 Mg/L ( Max )-Exact hardness will be after receiving water analysys report.
Output water Hardness 70 ppm
Regeneration Period After 1.0 lac lts
Operating Pressure 3.5 Kg. per sq.cm
Test Pressure 6 Kg. Sq.cm.
| Capacity 2 LPS | 1 | SET |  | 0
6 | Providing & fixing packaged Reverse Osmosis System skid mounted complete with pre and post water treatment plant, RO plant feed pumps(2nos.)CIP system, pipes ( SS -High pressure, PVC- low Pressure ) , dosing units,TDS meter, valves, control wiring, electrical panel, instrumentation input/output water quality monitoring meters/indicators, fully automated. -Location-Plant room at terrace level.
TDS of Input(raw) water as per water test report= 600 ppm.
Permeate flow rate 1000 LPH (TDS at output after blending will be below 70ppm).
Water Test Report-to be obtained from site before finalising technical details of RO plant.
| RO Plant as mentioned above | 1 | NO |  | 0
|  |  |  | Total | 0