## Summary
ANNEXURE I (Description and Unit Rates)
S No | Description TACO BELL @ TERMINAL 1, DELHI | Amount
1 | SECTION - I - WIRING | 0
2 | SECTION - II - SUPPLY & INSTALLATION OF SWITCH SOCKET OUTLETS | 0
3 | SECTION - III - TELEPHONE / DATA SYSTEM AND TV | 0
4 | SECTION - IV - INSTALLATION OF LIGHTING FIXTURES | 0
5 | SECTION - V - PANELS, DISTRIBUTION BOARDS | 0
6 | SECTION - VI - CABLING & EARTHING | 0
7 | SECTION - VII - CONVENTIONAL FIRE DETECTION SYSTEM | 0
8 | SECTION - VIII - MUSIC SYSTEM | 0
9 | SECTION - IX - SERVO STABILIZER/ UPS | 0
10 | SECTION - X - CCTV SYSTEM | 0
11 | SECTION - XI - MISCELLANEOUS | 0
| GRAND TOTAL | 0
8% | IGST@18% | 0
0
| TOTAL | 0

## Electrical BOQ
Electrical & Allied Services
TACO BELL @ TERMINAL 1, DELHI
S. No | Description | Unit | Qty | Rate | Amount
SECTION-I- WIRING & CONDUTING
1.1 | Supply and Installation of all materials, accessories and labour for wiring for light/ equipment circuit main using PVC insulated stranded copper conductor FRLS wires of 650V grade drawn through heavy gauge rigid MS conduit ( The cost of the conduit will be taken separately ) using necessary conduit accessories, pull/junction boxes, G.I. fish wire etc. The rate shall include the cost of providing PVC insulated stranded copper conductor earth wire in each conduit alongwith other circuit main wires. Lugs to be use at both the ends. FRLS Type only.
1.1.1 | Supply & Installation of 1.5 Sq.mm copper FRLS wires | Rmt | 1200 |  | 0
1.1.2 | Supply & Installation of 2.5 Sq.mm copper FRLS wires | Rmt | 2000 |  | 0
`
1.1.3 | Supply & Installation of 4 Sq.mm copper FRLS wires | Rmt | 550 |  | 0
1.1.4 | Supply & Installation of 6 Sq.mm copper FRLS wires | Rmt | 350 |  | 0
1.1.5 | Supply & Installation of 10 Sq.mm copper FRLS wires | Rmt | 40 |  | 0
1.1.6 | Supply & Installation of 16 Sq.mm copper FRLS wires | Rmt | 150 |  | 0
1.2 | Supplying and installing all materials, accessories and labour for conduiting & the accessories for light/ Equipment circuit main.The conduit should be Medium gauge rigid 1.6 mm thick FRLS PVC conduits conforming to IS-2509 of 1973 . The conduits shall be clamped by G.I./ PVC saddles of minimum 20 gauge or be clamps fabricated from M.S. strips of minimum 25 mm x 3 mm. The M.S. clamps/supports shall be duly painted with 2 coats of red oxide and 2 coats of black enamelled paint.The clamps/supports shall be fixed to the underside of the ceiling by means of nylon rawl plugs and brass screws of 3 mm size. Anchor fasteners of suitable sizes shall be provided if necessary.The conduits shall be supported at regular intervals of 500 mm. Additional supports shall be provided on either side of bends, JB's & terminations. The conduits shall be bent with bending springs to provide smooth bends. Use of ready made bends shall be kept to a minimum. The jointing of PVC conduits shall be done with couplers and PVC solvent cement. Conduits to be terminated in M.S. Boxes shall be terminated with female adaptors with bushes. All conduits assembled (PVC & M.S.) without wiring shall be provided with G.I. pull wire of minimum thickness of 14SWG. And end portion of the conduit to be provided with end caps where ever necessary. The cost should include the cost of heavy gauge rigid PVC conduit with necessary conduit accessories, PVC pull/junction boxes, G.I. fish wire etc & laying of the same. FRLS Only
1.2.1 | 20mm FRLS PVC Conduit | Rmt | R.O.
1.2.2 | 25mm FRLS PVC Conduit | Rmt | R.O.
1.2.3 | 32mm FRLS PVC Conduit | Rmt | R.O.
1.2.4 | 40mm FRLS PVC Conduit | Rmt | R.O.
1.2.4 | PVC Flexible Conduit Dia 20 mm | Rmt | R.O.
1.2.5 | PVC Flexible Conduit Dia 25 mm | Rmt | 150
1.2.6 | PVC Flexible Conduit Dia 32 mm | Rmt | R.O.
1.2.7 | 20mm MS Conduit | Rmt | 200
1.2.8 | 25mm MS Conduit | Rmt | 1800 |  | 0
1.2.9 | 32mm MS Conduit | Rmt | 250 |  | 0
1.2.10 | 40mm MS Conduit | Rmt | 125 |  | 0
1.2.11 | G.I. Flexible Conduit Dia 20 mm | Rmt | 100
1.2.12 | G.I. Flexible Conduit Dia 25 mm | Rmt | 150 |  | 0
1.2.13 | G.I. Flexible Conduit Dia 32 mm | Rmt | R.O.
| TOTAL OF SECTION I |  |  |  | 0
SECTION-II-SUPPLY & INSTALLATION OF SWITCH SOCKET OUTLETS
2.1 | Supply & Installation of the following MDS make Metra Plug & Socket DBs
2.1.1 | 6A TP Metal Clad switch socket with tP MCB | Nos. | R.O.
2.1.2 | 10A TP Metal Clad switch socket with TP MCB | Nos. | R.O.
2.1.3 | 16A TP Metal Clad switch socket with TP MCB | Nos. | R.O.
2.1.4 | 25A TP Metal Clad switch socket with TP MCB cat no. 6078 50 | Nos. | 0
2.1.5 | 32A TP Metal Clad switch socket with TP MCB cat no. 6078 51 | Nos. | R.O.
2.1.6 | 32A 4P Metal Clad switch socket with TPN MCB | Nos. | R.O.
2.1.7 | 40/63A 4P Metal Clad switch socket with TPN MCB | Nos. | 3
2.1.8 | 40A 2Pole Metal Clad Switch Socket | Nos | R.O.
2.1.9 | 40A TP Metal Clad switch socket with TP MCB | Nos. | 0
2.1.10 | 50A TP Metal Clad switch socket with TP MCB | Nos. | R.O.
2.1.11 | 20A DP Metal Clad switch socket with DP MCB | Nos. | R.O.
2.1.12 | 25A DP Metal Clad switch socket with DP MCB | Nos. | R.O.
2.1.13 | 32A DP Metal Clad switch socket with SP MCB | Nos. | R.O.
2.1.14 | 40A DP Metal Clad switch socket with DP MCB | Nos. | R.O.
2.1.15 | 63A DP Metal Clad switch socket with DP MCB | Nos. | R.O.
2.1.16 | 63A FP Metal Clad switch socket | Nos. | R.O.
2.1.17 | 10/16/20/25/32A SP Metal Clad switch socket cat no. 6078 41 | Nos. | 15 |  | 0
2.1.18 | 40A TP Metal Clad switch socket | Nos. | R.O.
2.1.19 | 32A TP Metal Clad switch socket cat no. 6078 51 | Nos. | R.O.
2.2 | Supply & Installation of the following Sockets, Switches including the front plate & Back boxes and all accessories
2.2.1 | 6A, Switch for lighting control. | No. | 0 |  | 0
2.2.2 | 6A, 5 Pin Switch socket outlet | No. | 32 |  | 0
2.2.3 | 3 nos. 6 A, 5 Pin Socket Outlets with 1 Nos. 16A switch (UPS) | Nos. | 3 |  | 0
2.2.4 | 2 nos. 6 A, 5 Pin Socket Outlets with 1 Nos. 16A switch (UPS) | Nos. | 0 |  | 0
2.2.5 | 2 nos. 6 /16A 6 Pin Switch Socket Outlets (UPS)Black colour | Nos. | 18 |  | 0
2.2.6 | 2 nos. 6 /16A 6 Pin Switch Socket Outlets (Raw Power) | Nos. | R.O.
2.2.7 | 1 no. 6 /16A 6 Pin Switch Socket Outlets (Raw Power) | Nos. | 10 |  | 0
2.2.8 | 1 no. 6 /16A 6 Pin Switch Socket Outlets (UPS) Black Colour | No. | 6 |  | 0
2.2.9 | 25A, 3 Pin switch socket outlet | Nos. | R.O.
2.2.10 | 16A Flat pin switch socket outlet (white colour) | Nos. | R.O.
2.2.11 | 16A Flat pin switch socket outlet (Black colour) | Nos. | R.O.
2.2.12 | Bell Switch | Nos. | 1 |  | 0
2.2.13 | Water Level Controller | Nos. | 1 |  | 0
2.2.14 | Timer for external Signage | Nos. | 0 |  | 0
2.2.15 | Pressure Pump Connections | Nos. | 0 |  | 0
2.2.16 | 32A 4P Industrial Type Switch Socket Outlets (Raw Power) | Nos. | R.O.
2.2.17 | 32A DP Industrial Type Switch Socket Outlets (Raw Power) | Nos. | R.O.
2.2.18 | 40A DP Industrial Type Switch Socket Outlets (Raw Power) | Nos. | R.O.
2.2.19 | 50A Industrial Type Switch Socket Outlets | Nos. | R.O.
2.2.20 | 63A Industrial Type Switch Socket Outlets | Nos. | R.O.
2.3 | Supply & Installation of the following Schneider make Industrial Plug & Socket DBs
2.3.1 | 63A SP Metal Clad socket cat no. 81378 | Nos. | R.O.
2.3.2 | 63A SP Metal Clad switch cat no. 81178 | Nos. | R.O.
2.3.3 | 63A DP Metal Clad switch cat no. 81178 | Nos. | R.O.
| TOTAL OF SECTION II |  |  |  | 0
SECTION III-TELEPHONE / DATA SYSTEM AND TV
3.1 | Supply & Installation of the Avaya make CAT-6 information outlet with face plate. (For data) | Nos. | 30 |  | 0
3.2 | Supply & Installation of clipsal make RJ11 telephone outlet with front plate | Nos. | 2 |  | 0
3.3 | Supply & Installation of CAT-6 Data cable in 20mm/25mm dia M.S. conduits | Mts. | 600 |  | 0
3.4 | Supply & Installation of CAT-5 telephone cable in 20mm/25mm dia MS conduits | Mts. | 100 |  | 0
3.5 | Supply & Installation of 10pair Telephone Tag block with enclosure | No. | 1 |  | 0
3.6 | TV boxes with 4 way connector | No. | 0 |  | 0
3.7 | Supplying and fixing of television socket outlet in MS boxes | No. | 1 |  | 0
3.8 | Supply & Installation of RG-6 TV cable in 20mm/25mm dia M.S. conduits | Mts. | 0 |  | 0
3.9 | Supply & Laying of Fiber optical cable | Mts. | 0 |  | 0
3.10' | Supply & Installation of Black Spiral 1" 2 Rolls | Mts. | 25 |  | 0
| TOTAL OF SECTION III |  |  |  | 0
SECTION-IV-SUPPLY & INSTALLATION OF LIGHTING FIXTURES
4.1 | Installation of the following light fittings
4.1.1 | Recessed downlighter (1x6W/7W/15W LED Warm white) | Nos | 22 |  | 0
4.1.2 | Recessed mounted luminaire suitable for grid ceiling | Nos | 0 |  | 0
4.1.3 | Batten Type luminaire with 1x28W T5 FTL | Nos | 4 |  | 0
4.1.4 | Patti Type luminaire with 1x14W T5 FTL | Nos | 0 |  | 0
4.4.5 | LED spot light on cable tray | Nos | 0 |  | 0
4.4.6 | Decorative tubelights with 8mm thick acrylic on both sides fitted with aluminum extrusion channel. colours :yellow,red,green,blue,white, | Nos | R.O.
4.4.7 | Recessed mounted wall washer luminaire | Nos | R.O.
4.2 | Installation, testing and commissioning of following type of light fixtures as per drawings and specifications with all other accessories such as supporting rods / frames, anchor fasteners, necessary hardware etc. The rate shall include for installing the chokes ignitor complete set.
4.2.1 | Decorative Hanging Lights | Nos | 1 |  | 0
4.2.2 | Picture Lights | Nos | R.O.
4.2.3 | External Wall light , Up & Down light 35w | Nos | R.O.
4.2.4 | Pole lights | Nos | R.O.
4.2.5 | Outdoor luminaire Lamp70/150W MH for Top compartment & Flurorescent 36WT-8,for the pole compartment.protection:- IP55. | Nos | R.O.
| TOTAL OF SECTION IV |  |  |  | 0
SECTION-V PANELS, DISTRIBUTION BOARDS
5.1 | Installation, Testing & Commissioning of following Panels including placemnt on point (same floor), proper cable dressing upto satisfaction of site incharge
5.1.1 | Installation, Testing & Commissioning of Main LT Panel. | No. | 1 |  | 0
5.1.2 | Installation, Testing & Commissioning of SUB LT Panel. | No. | R.O.
5.1.3 | Installation, Testing & Commissioning of SERVO BY PASS Panel. | No. | 0 |  | 0
5.1.4 | Installation, Testing & Commissioning of AC Panel. | No. | R.O.
5.2 | Supply Installation Testing & Commissioning of following Distribution boards/ Starters of following wall mounted (flush / surface) as per drawings and specifications and as required. The distribution board shall be of sheet steel enclosure powder coated with all accessories and hardware as required complete. ( Double Door Type ).The DB shall have suitable insulated fork type indipendent neutral bus bars for each phase and earth terminal block to facilitate easy termination of wires. All wires inside the DBs shall be terminated using copper end terminations. ( Standard Prefebricated DB to be use.) (With necessary dummy plate as required, with cable gland plate at top and bottom with knockouts provided with hinged lockable covers
5.2.1 | 6 Way TPN with 32 A TPN MCB + 25 A DP ELCB (300 mA) as incomer and 12 nos 6-32 A SP MCB as Outgoings | No. | R.O.
5.2.2 | 8 Way TPN (PDB1,PDB2,LDB1,LDB2) with 32 A TPN MCB + 3 nos 25 A DP ELCB (30 mA) as incomer and 18 nos 6 to 16 A SP MCBs as Outgoings as per SLD & load sheet | No. | 0
5.2.3 | 10way SPN DB with 32A DP MCB+ Timer + Contactor as incomer & 1 nos. of32A DP ELCB, 100mA & 6 Nos. 16/20/25A sp MCB's as outgoings (SDB) | No. | 1
5.2.4 | 6 way TPN (UPSDB ) with 63 DP MCB + ELCB as Incomer and 24 nos 10/16A SP MCBs as outgoings | No. | 0
5.2.5 | 16 way SPN with 40 A DP MCB + ELCB ( 30 mA) as Incomer and 12 nos 10 10 32 A SP MCBs as Outgoings | No. | 1
5.2.6 | 4 way SPN with 25 A DP MCB + ELCB as Incomer and 4 nos 6A SP MCBs as Outgoings | No.. | 0
5.2.7 | 4 way TPN DB with 40A TPN MCB 3 nos. of 40 A DP ELCB, 100mA & 1 nos 32 4 P MCB , 1No. 32 DP MCB and 6 Nos. 10/20/25A sp MCB's as outgoings (SDB) | No.. | 0
5.2.8 | L&T make MF1 DOL stater (1PH) | Nos. | R.O.
5.2.9 | L&T make MK1 DOL stater (3PH) | Nos. | R.O.
5.2.10 | L&T make DOL starter in SS Housing for 3.8KW Fan with auxilliary contactor arrangement for tripping/switching On fan in case of fire | Nos. | R.O.
5.2.11 | L&T make star/delta starter in SS Housing for 5.7KW Fan with auxilliary contactor arrangement for tripping/switching On fan in case of fire | Nos. | R.O.
5.2.12 | KDB-1 with 1 nos 100A TPN MCCB,Three (3) - phase indicating lamps with MCB. 13nos 10/16/20/25 A SP MCBs,3 nos 25A DP MCBs, 6 nos 32A DP MCBs & 2 nos 32ATPN MCBs as Outgoings | No.. | R.O.
5.2.13 | 1 Phase 6 Way External DB with 1 nos 32A DP MCB as Incomer and 6 nos 16A SP MCBs as Outgoings | No. | R.O.
5.2.14 | 12way SPN (ELDB) with 1 nos 32 A DP MCB as Incomer and 12 nos 10A SP MCBs as Outgoings | Nos. | R.O.
5.2.15 | 12Way TPN with 1 nos 63A TPN MCB as Incomer, 3 nos 63A DP RCCB as Sub-Incomer & 30 nos 16/20/25/32 A SP MCB as Outgoings. | No. | R.O.
5.2.16 | 12Way TPN with 1 nos 32A FP MCB as Incomer, 3 nos 25A DP ELCB(100mA) as Sub-Incomer & 30 nos 10A SP MCB as Outgoings. | No.. | R.O.
5.2.17 | 8 Way 7 Segment DB with 1 no 40A FP MCB as Incomer & 3nos 32A DP ELCB, 30mA as Sub-Incomer, 24 nos 1-63A SP MCB and as outgoings (Phase Segregated DB) | Nos | 0
5.2.18 | 12 Way 7 Segment DB with 1 no 40A FP MCB as Incomer & 3nos 40A DP ELCB, 100mA as Sub-Incomer, 20 nos 20A SP MCB and 10 nos 10A SP MCB as outgoings (Phase Segregated DB) | Nos | R.O.
5.2.19 | 12Way VTPN with 1 nos 100A FP MCCB as Incomer, 4 nos 32/40A TP MCB as Sub-Incomer & 24 nos 16/20/25/32 A SP MCB as Outgoings. | Nos | R.O.
5.2.20 | 4Way VTPN with 1 nos 40A FP MCB as Incomer, 1 nos 40 A FP RCCB as Sub-Incomer & 1 no. 32 4P MCB, 9 nos 16/20/25/32 A SP MCB as Outgoings. | Nos | R.O.
5.3 | Supply Installation Testing & Commissioning of following MCB in Enclosures
5.3.1 | 50/63A TPN MCB in Weather Proof Enclosure | Nos. | 0
5.3.2 | 40/63A FP ELCB in Weather Proof Enclosure | Nos. | R.O.
5.3.3 | 32A TPN MCB in Weather Proof Enclosure | Nos. | 0
5.3.4 | 25A TPN MCB in Enclosure | Nos. | R.O.
5.3.5 | 16/20/25A TPN MCB in Weather Proof Enclosure | Nos. | 0
5.3.6 | 50A DP MCB in Enclosure | Nos. | R.O.
5.3.7 | 40A DP MCB in Enclosure | Nos. | R.O.
5.3.8 | 32A DP MCB in Enclosure | Nos. | R.O.
5.3.9 | 25A DP MCB in Enclosure | Nos. | R.O.
5.3.10 | 20A DP MCB in Enclosure | Nos. | R.O.
5.3.11 | 20A/25/32A DP MCB in Weather Proof Enclosure | Nos. | 0 |  | 0
5.3.12 | 25A TPN MCB in Weather Proof Enclosure | Nos. | R.O.
5.3.13 | 16A TPN MCB in Weather Proof Enclosure | Nos. | R.O.
5.3.14 | 32A DP ELCB in Weatherproof Enclosure | Nos | R.O. |  | 0
5.3.15 | 32A FP ELCB in Weatherproof Enclosure | Nos | 0 |  | 0
5.3.16 | 40/63A FP ELCB in Weatherproof Enclosure | Nos | 0
5.3.17 | 63A DP MCB in Enclosure | Nos. | R.O.
| TOTAL OF SECTION V |  |  |  | 0
SECTION-VI -CABLING & EARTHING
All Cables Should be FRLS
6.1 | Supply of Installation of Following cables 1.1 KV grade PVC/XLPE insulated Armoured Aluminium /Copper conductor cables. The cables shall be laid as per dwgs or on cable trays laid over MS supports cable racks or fixing on walls including clamping the cable to supports in an approved manner as required complete with earthing as specified for continuous earthing along with cable . (The cost of the cable trays or ladders, excavation and back filling of trenches will be measured separate. The unit cost of the cable shall include clamps, fasteners etc. as required for proper installation. Earthing will be measured separately and need not be quoted under this item). All complete as required and as per final instruction as given by consultant/site engineer. The cables should be properly dressed and to be tied to the cable trays using appropriate cable ties.
6.1.1 | 3.5 C X 150 Sq.mm AL. XLPE Armoured Cable- | Mts. | 0 |  | 0
6.1.2 | 3.5 C X 95 Sq.mm AL. XLPE Armoured Cable | Mts. | R.O. |  | 0
6.1.3 | 3.5 C X 70 Sq.mm AL. XLPE Armoured Cable-MAIN CABLES | Mts. | 0 |  | 0
6.1.4 | 3.5 C X 50 Sq.mm AL. XLPE Armoured Cable-MAIN CABLES | Mts. | 0 |  | 0
6.1.5 | 4 C X 10 Sq.mm AL.XLPE Armoured Cable | Mts. | 0
6.1.6 | 4 C X 6 Sq.mm AL.XLPE Armoured Cable | Mts. | R.O. |  | 0
6.1.7 | 4 C X 4 Sq.mm AL.XLPE Armoured Cable | Mts. | R.O.
6.1.8 | 4 C X 2.5 Sq.mm AL.XLPE Armoured Cable | Mts. | R.O.
6.1.9 | 4 C X 16 Sq.mm CU PVC Armoured Cable | Mts. | 0 |  | 0
6.1.10 | 4 C X 10 Sq.mm CU PVC Armoured Cable | Mts. | 25 |  | 0
6.1.11 | 4 C X 6 Sq.mm Cu PVC Armoured Cable | Mts. | R.O. |  | 0
6.1.12 | 4 C X 4 Sq.mm Cu PVC Armoured Cable- | Mts. | 160 |  | 0
6.1.13 | 3 C X 6 Sq.mm Cu PVC Armoured Cable | Mts. | R.O.
6.1.14 | 3 C X 4 Sq.mm Cu PVC Armoured Cable- | Mts. | 60
6.1.15 | 4 C X 2.5 Sq.mm Cu PVC Armoured Cable | Mts. | 0
6.1.16 | 3 C X 4 Sq.mm Cu XLPE armoured | Mts. | 0 |  | 0
6.1.17 | 3 C X 16 Sq.mm Cu XLPE Unarmoured | Mts. | R.O.
6.1.18 | 4 C X 25 Sq.mm Cu XLPE Armoured | Mts. | R.O.
6.1.19 | 4 C X 16 Sq.mm Cu XLPE Unarmoured | Mts. | 0
6.1.20 | 4 C X 10 Sq.mm Cu XLPE Unarmoured | Mts. | 0
6.1.21 | 3 C X 6 Sq.mm Cu XLPE Armoured | Mts. | R.O.
6.1.22 | 3 C X 2.5 Sq.mm Cu XLPE Armoured | Mts. | R.O. |  | 0
6.1.23 | 3 C x 10 Sq mm XLPE AL. Cable | Mts. | R.O.
6.1.24 | 3.5 C x 35 Sq mm XLPE AL. Cable | Mts. | R.O.
6.1.25 | 4 C x 25 Sq mm XLPE AL. Cable | Mts. | R.O.
6.1.26 | 4 C X 25 Sq.mm Cu XLPE Armoured | Mts. | R.O.
6.1.27 | 3.5 C x 120 Sq mm XLPE AL. Cable | Mts. | R.O.
6.1.28 | 3.5 C x240 Sq mm XLPE AL. Cable | Mts. | R.O.
6.1.29 | 4C x 1.5sqmm Cu Ar Cable | Mtrs | R.O.
6.1.30 | 4 C X 1 Sq.mm Cu Armoured cable | Mts. | R.O.
6.1.31 | 1C x 16sqmm Cu Cable | Mtrs | R.O.
6.2 | Supply of Installation of Following cable Terminations including Single/Double compression type chrome plated brass glands and lugs(crimping type), PVC taping as required and all accessories complete.
6.2.1 | 3 C x 2.5 sq mm CU PVC Armoured | No. | R.O. |  | 0
6.2.2 | 3 C x 4 sq mm CU PVC Armoured | No. | 4 |  | 0
6.2.3 | 3 C x 6 sq mm CU PVC Armoured | No. | R.O.
6.2.4 | 3 C x 10 sq mm CU PVC Armoured | No. | R.O.
6.2.5 | 4 C x 2.5 sq mm CU PVC Armoured | No. | 0
6.2.6 | 4 C x 4 sq mm Cu. PVC Armoured | No. | 8 |  | 0
6.2.6 | 4 C x 2.5 sq mm AL PVC Armoured | No. | R.O.
6.2.6 | 4 C x 6 sq mm AL PVC Armoured | No. | R.O. |  | 0
6.2.7 | 4 C x 6 sq mm Cu. PVC Armoured | No. | R.O. |  | 0
6.2.8 | 4 C x 10 sq mm AL PVC Armoured | No. | R.O. | 0 | 0
6.2.9 | 4 C x 16 sq mm AL PVC Armoured | No. | 0
6.2.10 | 3.5 C x 25sq mm AL. XLPE Armoured | No. | R.O.
6.2.11 | 3.5 C x 35sq mm AL. XLPE Armoured | No. | R.O. |  | 0
6.2.12 | 3.5 C x 95 sq mm AL. XLPE Armoured | No. | 0 |  | 0
6.2.13 | 3.5 C x150 sq mm AL. XLPE Cable | No. | 0
6.2.14 | 3.5 C x185sq mm AL. XLPE Cable | No. | R.O.
6.2.15 | 3 C X 4 Sq.mm Cu XLPE armoured | NOS. | R.O.
6.2.16 | 3 C X 16 Sq.mm Cu XLPE Unarmoured | NOS. | R.O.
6.2.17 | 4 C X 25 Sq.mm Cu XLPE Armoured | NOS. | R.O.
6.2.18 | 4 C X 16 Sq.mm Cu XLPE armoured | NOS. | 0
6.2.19 | 4 C X 10 Sq.mm Cu XLPE armoured | NOS. | 2
6.2.20 | 3 C X 6 Sq.mm Cu XLPE Armoured | NOS. | R.O.
6.2.21 | 3 C X 2.5 Sq.mm Cu XLPE Armoured | NOS. | R.O. |  | 0
6.2.22 | 3 C x 10 Sq mm XLPE AL. Cable | NOS. | R.O.
6.2.23 | 3.5 C x 70 Sq mm XLPE AL. Cable | NOS. | 1
6.2.24 | 4 C x 25 Sq mm XLPE AL. Cable | NOS. | R.O.
6.2.25 | 4 C X 25 Sq.mm Cu XLPE Armoured | NOS. | R.O.
6.2.26 | 3.5 C x 120 Sq mm XLPE AL. Cable | NOS. | R.O.
6.2.27 | 3.5 C x240 Sq mm XLPE AL. Cable | NOS. | R.O.
6.2.28 | 4C x 1.5sqmm Cu Ar Cable | NOS. | R.O.
6.2.29 | 4 C X 1 Sq.mm Cu Armoured cable | NOS. | R.O.
6.2.30 | 1C x 16sqmm Cu Cable | NOS. | R.O.
6.3 | Supply of Installation of Following Cable Trays of 2mm thick MS steel fabricated ladder type cable trays of the following sizes.Ladder type cable trays shall be fabricated from 50 x 50 x 5 mm M.S. angles on the sides with 25 x 6 mm M.S. strips welded at intervals of 300 mm. The trays shall be painted with 2 coats of red oxide & 2 coats of synthetic enamel paint of approved colour. All trays should have coupler plates with 4 number of bolt and nuts of galvanized hardware.Trays should be supported at ecvery 1.5 mtr interval.
6.3.1 | 150mm wide ladder type Cable tray with support | Mts. | 20 |  | 0
6.3.2 | 300mm wide ladder type Cable tray with support | Mts. | 20 |  | 0
6.3.3 | 300mm wide Perforated Cable tray with support | Mts. | R.O.
6.3.4 | 150mm wide Perforated type Cable tray with support | Mts. | R.O.
6.3.5 | 450mm wide Perforated Cable tray with support | Mts. | R.O.
6.3.6 | 50 mm wide x 50 H Perforated Cable tray with support | Mts. | 0 |  | 0
6.4 | Supply of Installation of Following Earthing Material wire including necessary accessories, clamping to walls, cables etc. as required and interconnection between lengths as per specifications and as per good installation practice. The rate shall include all supports, accessories and hardware necessary for proper installation. (All GI strips should be welded on a lap joint practice and two coats of bitumin paint of should be applied on the same to avvoid corrosion in future. And all copper strips should be brazed on a lap joint parctice and should be insulated with PVC sleeve while running on cable trays / wall.) And GI / Al / Cu SWG wires should be terminared using ring types lugs.
6.4.1 | 25 x 6 mm cu. Strip | Mts. | 0 |  | 0
6.4.2 | 25 x 6 mm GI. Strip | Mts. | 15 |  | 0
6.4.3 | 25 x 3 mm cu. Strip | Mts. | R.O.
6.4.4 | 25 x 3 mm GI. Strip | Mts. | R.O.
6.4.5 | 8 SWG hard drawn bare GI wire | Mts. | 200 |  | 0
6.4.6 | 12 SWG hard drawn bare GI wire | Mts. | R.O
6.4.7 | Providing and laying 1C x 6 sqmm insulated copper wire as earthing conductor including necessary accessories, clamping to walls, cables etc. as required and interconnection between lenghts as per specifications and as per good installation practice. | Mts. |  |  | 0
6.4.8 | Providing and laying 1C x 10 sqmm insulated copper wire as earthing conductor including necessary accessories, clamping to walls, cables etc. as required and interconnection between lenghts as per specifications and as per good installation practice. | Mts. | 120 |  | 0
6.4.9 | Providing and laying 1C x 4 sqmm insulated copper wire as earthing conductor including necessary accessories, clamping to walls, cables etc. as required and interconnection between lenghts as per specifications and as per good installation practice. | Mts. | 100 |  | 0
6.4.10 | Providing and laying 1C x 25 sqmm insulated copper wire as earthing conductor including necessary accessories, clamping to walls, cables etc. as required and interconnection between lenghts as per specifications and as per good installation practice. | Mts. | R.O.
6.4.11 | Supply, installation, connection, testing and commissioning of Earthing station, eas per specification and IS: 3043 - 1985 for equipment earthing with :
1) | Excavation in hard marrum
2) | Watering pipe
3) | Earthing strip / earthing cable
4) | Plate / pipe electrode
5) | Hardware
6) | Brick masonry chamber with C.I. hinged cover and funnel
7) | Charcoal and salt fill
8) | Equipotential bar
| 600 x 600 x 3 mm. thick Cu.. earth electrode type earth station | NOS. | 0
6.4.12 | Supply, installation, connection, testing and commissioning of Earthing station, eas per specification and IS: 3043 - 1985 for equipment earthing with :
1) | Excavation in hard marrum
2) | Watering pipe
3) | Earthing strip / earthing cable
4) | Plate / pipe electrode
5) | Hardware
6) | Brick masonry chamber with C.I. hinged cover and funnel
7) | Charcoal and salt fill
8) | Equipotential bar
| 600 x 600 x 6 mm. thick GI. earth electrode type earth station | NOS. | R.O.
6.4.13 | Supply and Installation of 25x6mm GI Earth Bus in Powder coated Box | NOS. | R.O.
6.4.14 | Supply and Installation of 25x4mm CI Earth Bus in Powder coated Box | NO. | R.O.
| TOTAL OF SECTION VI |  |  |  | 0
SECTION-VII - FIRE ALARM SYSTEM ADDRESSABLE TYPE
FIRE ALARM SYSTEM ADDRESSABLE TYPE
7.1 | Supply, installation, testing and commissioning of Addressable 1 loop fire Pannel Make Johnson Control or equivalent make as per the airport authority approved list
7.2 | Supply, installation, testing and commissioning of Addressable type , ceiling / recessed mounted smoke detector. | Nos | 8 |  | 0
7.3 | Supply, installation, testing and commissioning of Addressable type , ceiling/ recessed mounted heat detector. | Nos | 4 |  | 0
7.4 | Supply, installation, testing and commissioning of manual break glass unit including the mounting box. | Nos | 1 |  | 0
7.5 | Supply, installation, testing and commissioning of electronic alarm hooters. | Nos | 1 |  | 0
7.6 | Supply, installation, testing and commissioning of Response Indicator | No | 6 |  | 0
7.8 | Supply, installation, testing and commissioning of 2c x 1.5 sqmm armoured fire survival cable | RM | 200 |  | 0
7.9 | Addressable Fault isolator module | No | 2 |  | 0
7.1 | Providing AHU/AC cut off modules | No | 2 |  | 0
7.11 | Monitor Modules | No. | 1 |  | 0
7.12 | Control Module for Integration of Fire System with other security system | No | 1 |  | 0
7.13 | Fas System Integration with Module | No. | 0 |  | 0
| TOTAL OF SECTION VII |  |  |  | 0
| TOTAL OF SECTION VIII |  |  |  | 0
SECTION-IX-SERVO STABILIZER/ INVERTOR/UPS
8.1 | Installation of125KVA Single Phase Servo Stabilizer-Online systems | No. | 0
8.2 | Installation of 1.5KVA Invertor with 20 minutes battery back up-Online Systems | No. | R.O. |  | 0
8.3 | Installation of6 KVA Single Phase UPS with 20min battery back-up- make Online Systems | No. | 0 |  | 0
8.4 | Installation of 3KVA Online Single Phase UPS with 20min battery backup with suitable size of rack make APC/ Eaton | No. | 1 |  | 0
| TOTAL OF SECTION IX |  |  |  | 0
SECTION-XI-CCTV SYSTEM
9.1 | Supply of Installation of Following Items
9.2 | RG6 Co-axial cable | Rm | 200 |  | 0
9.3 | 2 Core 1.5 sqmm cable | Rm | 180 |  | 0
9.4 | 20/25mm M.S. conduit | Rm | 150
Installation of Following Items
10.1.4 | CBC Make 16ch MPEG4 w/DVD-RW, MPEG4 Compression C-MPDVR8 | Nos. | R.O.
10.1.5 | Color Dome Camera-CBC Make 380TVL, 3.6mm MIL 0.4 MDC-P36S | Nos. | R.O.
10.1.6 | 12V SMPS for Camera | Nos. | R.O.
10.1.7 | Converter | Nos. | R.O.
10.1.8 | 15" TFT Monitor -Samsung Make | No. | R.O.
| TOTAL OF SECTION X |  |  |  | 0
SECTION-XI-MISCELLANEOUS
10.1 | Supplying the following data prior to handing over the installation to the owner. | job | 1 |  | 0
i) Megger Test Results in quadruplicate of all mains/submains/circuits/load feeders in tabulated format
i) In quadruplicate all`As built' drawings on blue prints, separate for
a | indoor lighting
b | outdoor lighting
c | Electrical cable system with sizes and routes
d | Main Earthing grid
f | conduit layout-to all the points from controlling DB's to be drawn along with indoor lighting
In general the drawings should show the sizes of cables, conduits and number of wires laid in conduit, outlets and lighiting layout,earthing conductor sizes, single line diagrams of each panel. Any other data like specifications, test certificates and maintenance manual of panels, Main LT panel etc. should also be furnished in quadriplicate
10.2 | Provision of ample amount of Temporary lights & sockets during construction stage | LS | 1 |  | 0
10.2.1 | Fixing of Hand Drier | Nos | R.O.
11.3.3 | Fixing of Pest-O-Flash | Nos | R.O.
11.3.4 | Supply & fixing of 100 x 100mm PVC Truff | Mtrs | R.O.
11.3.5 | Supply & fixing of Bulk Head Fitting | Nos | R.O.
11.3.6 | Fixing of Aircurtain | Nos | R.O.
11.3.7 | Supply & Laying of Rubber Mat | Nos | R.O.
11.3.8 | Supply & fixing of 40A DP ELCB in Weatherproof Enclosure | Nos | R.O.
11.3.9 | Supply & fixing of 63A DP ELCB in Weatherproof Enclosure | Nos | R.O.
11.3.10 | Supply & fixing of 32A DP MCB in weather Proof Enclousure | Nos | R.O.
11.3.11 | Fixing of Wall Mounting Fan | Nos | R.O.
11.3.12 | Fixing of Heavy Duty Exhaust Fan | Nos | R.O.
11.3.13 | Supply and Installation of DMB Brackets | Nos | R.O.
11.3.14 | Addition man power cost-Skilled | Days | R.O.
11.3.15 | Addition man power cost-Unskilled | Days | R.O.
11.3.16 | Price of hiring of temporary DG during construction | Days | R.O.
| TOTAL OF SECTION XI |  |  |  | 0

## Make
List of Approved Brands
S No. | Item | Make
1 | MS Conduits | AKG/ BEC
2 | FRLS PVC Conduits | Precision/ AKG/ BEC
3 | FRLS Wires | Finolex / Havells/ KEI/ Polycab
4 | Cables | Polycab/ Havells/ Finolex
5 | Switches | Clipsal/ Opale/ Crabtree/ Northwest
6 | Distribution Boards | Siemens/ MDS/ legrand
7 | MCB’s /ELCB’s | Siemens/ MDS/ legrand
8 | Telephone Wires | Finolex/ Polycab/ ITL
9 | T.V.Wires | Comscop/ Finolex
10 | Switch Fuse Units/ Starters | L&T/ Siemens
11 | Fire Alarm System | Apollo/ System Sensor/ Agni
12 | Data Cable | Amp (TE)
Notes:-
[1] The Contractor should quote the tender rates considering First make of materials given in above list.
[2] Wherever contractor proposes to use `equivalent' makes (i.e. other than specified) he shall obtain Client's prior approval. Client may consult Consultants before giving approval to the same. Any additional cost and time lost due to this will be on Contractor's account and no claims will be entertained.
[3] The contractor should take approval for make & manufacturer from the Client before using any material, which does not appear in the list of approved manufacturers.
1. DB have per phase RCBO protection.
2. Minimum wire size shall be 2.5 Sq. mm and power circuits wire size should be 4.0 sq.mm.
3. All equipment’s above 1 KW shall be provided with ELCB & shall run/operated through industrial type switch socket only.
4. Only GI conduit will be used.
5. Equipment protection devices and appropriate earthing as per approved load to be provided.
6. All DB and panel have dual Earthing connection.
7. All internal wires / cables shall be FRLSH/FRLSZH.
8. Main distribution board will not be fixed on wooden material.
9. IT , Data and low voltage wires shall be drawn In Separate
10. Switch/ Sockets Outlets Will Not Be Over Loaded With Multiple Connection Conduit And Not With Electrical
11. All lights shall be LED.
12. Provision of Emergency light should be there.
13. No combustive material are to be store under/closed the electrical switch board/distribution board/meter etc.
14. The concessioner should install suitable type & rated fire extinguisher near electrical panel.
15. Shutter type switch socket outlet on suitable MS box shall be used with proper earthing.
16. All electrical equipment shall be proper earthed and connected to main earthing with suitably sized earthing conductor.
17. Single line diagram sealed in a plastic folder shall be provided inside each electrical panel.
18. Load balancing to be done.
19. Power connection for Existing BTU meter & Water meter to be provided from concessionaire DB.
20. All electrical source to be enclosure with IP65 Device with louvered openable cabinet and all fire protection.
21. Panel GA drawing to be share with DIAL for approval.
22. CO2, FM-200/HFC-227ea gas based automatic tube detection & suppression system needs to be installed for Electrical Panel with Incomer rating equal to or more than 200Amps.