## Fire Fighting
Fire fighting work Taco Bell
SR. NO. | DESCRIPTION | UNIT | QTY | RATE (Rs.) | AMOUNT (Rs.)
A. | PIPING & VALVES
1 | Providing and fixing M.S. pipe to I.S. 1239 (Heavy class) complete with all supports & fittings like, unions, couplings, bends, elbows, tees, offsets,reducers, flanges as per table 'E' etc. to complete the work as per the requirement at site including painting with one coat of primer after surface preparartion and two coats of synthetic enamel paint, cutting and making good the walls good complete. Pipe upto 40 mm dia threaded joints using Cast Steel fittings with holdtite, 50 mm dia and above should be welded joint ( all type ) ( internal works/External Works)
a. | 25 mm dia. | RM | 0 |  | 0
b. | 32 mm dia. | RM | 0 |  | 0
c. | 40 mm dia. | RM | 0 |  | 0
d. | 50 mm dia. | RM | 0 |  | 0
e. | 65 mm dia. | RM | 0 |  | 0
f. | 80 mm dia. | RM | 0 |  | 0
g. | 100mm dia | RM | 0 |  | 0
A. | PIPING & VALVES |  |  |  | 0
2 | Providing and fixing GI pipe to I.S.15105 (Heavy class) complete with all supports & fittings like, unions, couplings, bends, elbows, tees, offsets,reducers, flanges as per table 'E' etc. to complete the work as per the requirement at site including painting with one coat of primer after surface preparartion and two coats of synthetic enamel paint, cutting and making good the walls good complete. Pipe upto 40 mm dia threaded joints using Cast Steel fittings with holdtite, 50 mm dia and above should be welded joint ( all type ) ( internal works/External Works) |  |  |  | 0
a. | 25 mm dia. | RM | 72 |  | 0
b. | 32 mm dia. | RM | 0 |  | 0
c. | 40 mm dia. | RM | 7.5 |  | 0
d. | 50 mm dia. | RM | 6 |  | 0
e. | 65 mm dia. | RM | 0 |  | 0
f. | 80 mm dia. | RM | 0 |  | 0
g. | 100mm dia | RM | 0 |  | 0
3 | Providing and fixing cast iron dual plate wafer type non return valves of PN1.6 including nuts, bolts,1.5mm thick compressed asbestos gasket including matching flanges as per table "E" complete. |  |  |  | 0
a. | 80 mm dia | Each | 0 |  | 0
b. | 100 mm dia | Each | 0 |  | 0
4 | Providing and fixing cast iron double flanged horizontal/vertical non return valves of PN1.6 including nuts, bolts, 3mm thick compressed asbestos gasket including matching flanges as per table "E" complete as per IS:5312 swing type.(For Pumps Only) |  |  |  | 0
a. | 100 mm dia. | Each | 0 |  | 0
5 | Providing and fixing C.I. butterfly valves PN 1.6 complete with bolts, nuts 1.5mm thick compressed asbestos gasket companion flanges as per table "E" complete. Make- ENOLGAS, RB, LEHREY ,AIP |  |  |  | 0
a. | 100 mm dia with lever | Each | 0 |  | 0
b. | 80 mm dia with lever | Each | 0 |  | 0
c. | 65 mm dia with lever | Each | 0 |  | 0
6 | Providing and fixing brass ball valve (full bore type) with plastic coated lever and screwed female ends tested to 20 Kg/ cm2 of approved quality as specified. Make- ENOLGAS, RB, LEHREY ,AIP |  |  |  | 0
a. | 25 mm dia. | Each | 0 |  | 0
b. | 50 mm dia. | Each | 0 |  | 0
7 | Providing and fixing dial type pressure gauge with isolation cock and copper pipe at hydrant station. |  |  |  | 0
a. | Dial diameter 100 mm calibration 0-15 kg/ sq.cm. | Each | 0 |  | 0
8 | Providing and fixing gunmetal single acting air release valve with screwed inlet 25 mm dia. Make- CIM/RB/ENOLGAS | Each | 0 |  | 0
B. | FIRE HYDRANT ACCESSORIES |  |  |  | 0
9 | Providing and fixing SS304 Single headed landing valve conforming to IS -5290 (Type-A) with 63 mm dia. single instantaneous female coupling on the outlet SS304 metal blank cap and chain, necessary companion flanges, nuts, bolts, washer and gasket complete as per specification. (ISI marked). All parts and body shall be of SS304 as per IS:5290. Make -Safedge/Lifeguard/Omex |  |  |  | 0
a. | Single outlet | Each | 0 |  | 0
10 | Providing and fixing first aid fire hose reel drum wall mounting, swinging type(Powder coated finish in fire red) fitted with 20 mm dia. 30 m long high pressure hose(IS:12585, Type-2) with 5 mm outlet SS nozzle with shut off valve (IS:8090). Name of Manufacturer should be embossed on the drum and complete hose reel drum shall be conforming to IS:884) -Make -swastik/Lifeguard/Kalpex | Each | 0 |  | 0
11 | Providing and fixing 63 mm dia. 15m long rubberized lined hose including SS304 male and female instantaneous type coupling approved by fire authority, machine wound with copper wire complete in all respects. Hose shall conform to IS 636 Type-A and coupling to IS 903 -1975 ( ISI marked) | Each | 0 |  | 0
12 | Providing and fixing standard short size SS304 branch pipe with gunmetal nozzle 16 mm dia. outlet with standard instantaneous type 63 mm dia. coupling. (ISI marked, IS:903) Make:- GURU/KARTAR | Each | 0 |  | 0
13 | Providing and fixing fire hose cabinet fabricated from 16 gauge M.S. Sheet with single or double glazed front door and locking arrangement, painted "Fire Red" with powder coated paint "Fire Hose" written on front including suitable supports to place 600 mm above ground level, approximately size 1200x1000x600 mm deep for internal hydrants. | Each | 0 |  | 0
14 | Providing and fixing gunmetal fire brigade inlet head as per IS:904 Specification tested for 20 Kg/cm2 with 63 mm dia. instantaneous type inlet and 100/150mm dia.. flanged outlet with built-in check valve for fire brigade connection to under ground tanks and fire risers including companion flanges as portable " E" including nuts, bolts & washers etc. |  |  |  | 0
a. | Three way | Each | 0 |  | 0
15 | Supplying and fixing of Fire Man's Axe with heavy insulated rubber tested upto 20 KV and confirming to IS :926. | Each | 0 |  | 0
16 | Air Cushion Tank for Risers |  |  |  | 0
| Providing and fixing of air vessel of the following specifications fabricated with MS Pipe of thickness specified specifications. |  |  |  | 0
| a. Diameter : 200 mm |  |  |  | 0
| b. Shell Thickness: 6.35 mm |  |  |  | 0
| c. Dish Ends : 10 mm |  |  |  | 0
| d. Height : 1000 mm |  |  |  | 0
| e. Finishing: Two coats of red enamal |  |  |  | 0
| paint over primer out side and two |  |  |  | 0
| coats of epoxy coating inside. |  |  |  | 0
| f. Material of construction: M.S |  |  |  | 0
| g. Test Pressure: 20 Kg/Sq.Cm. |  |  |  | 0
| h. Height of supporting legs: 400 mm |  |  |  | 0
| i. Quantity | Each |  |  | 0
| Note: Contractor should submit general arrangement drawings before fabrication of vessel and ultrosonic test report to be submitted on supply of vessel and test to be conducted at the presence of Plumbing-In-Charge. Also cost shall include two nos. Gunmetal NRV(ISI Marked) |  |  |  | 0
C. | SPRINKLERS & ACCESSORIES |  |  |  | 0
17 | Providing and fixing 15 mm gunmetal sprinkler head with quartz bulb and set to operate at specified temperature pendent/ upright/ side wall /quick response as per instruction fixed with loctite. Temperature of operation 68 deg.C K-80 Make: Ansul, Buckeye, Smog Hog, Gem-Tyco, Spray safe or equivalent |  | 16 |  | 0
a. | Normal response Pendent type | Each |  |  | 0
18 | Providing & fixing 25mm dia. UL listed gunmetal inspector test and drain valve with integral sight glass connected to drain line complete in all respects. | Each | 1 |  | 0
19 | Providing and fixing electrically operated flow indicating switches model System Sensor in sprinkler branch line on each floor with necessary junction box installed in accessible place (Wiring from switches to panel and stair case pressurization not included) Make-System sensor/grinnel. |  |  |  | 0
a. | 80/65/50 mm dia. | Each |  |  | 0
20 | Providing and fixing UL/Fm listed powder coated finish Escutcheon plate complete including fixing in position on pipe and ceiling complete in all respects. (Size=15NB) Make: Ansul, Buckeye, Smog Hog, Gem-Tyco, Spray safe or equivalent | Each | 16 |  | 0
21 | Providing and fixing UL/Fm listed SS braided flexible pipe with accessories complete with all accessories specified in technical specifications(Size=15NB) Make: Ansul, Buckeye, Smog Hog, Gem-Tyco, Spray safe or equivalent |  |  |  | 0
a. | 780mm long | Each |  |  | 0
b. | 1000mm long | Each | 8 |  | 0
c. | 1500 mm long | Each |  |  | 0
D. | FIRE PUMPS & ACCESSORIES |  |  |  | 0
22 | Supplying, installing, testing & commissioning of electric driven automatic pressurisation pump set with motor control panel with DOL starter, MCB, cabling etc. consisting of the following : |  |  |  | 0
| Horizontally mounted centrifugal split casing type Terrace pump complete for delivery of 900 ltrs/minute against a total head of 35 metres approx complete with arrangement for testing of the working of the pumping set as required. Rate shall also include Mechanical Seal. |  |  |  | 0
| Squirrel cage induction motor suitable for 415 V, 50 Hz, AC supply of suitable 15 HP rating for the above pump with synchronous speed of 2900 RPM T.E.F.C. type such as confirming to IPL55 and flexible coupling and coupling guard with the pump. Make :- Krilosker |  |  |  | 0
| Common bed plate of fabricated mild steel channel or cast iron type. |  |  |  | 0
| Suitable cement concrete pump foundation with cushy foot, MS bolts, washers as requiried. | Each |  | 0 | 0
23 | Providing and fixing dual type pressure switch suitable for 1-20 Kg/cm2 including electrical connections setting of Cut-In and cut-Off pressure complete in all respects. | Each |  | 0 | 0
| TOTAL |  |  |  | 0
LIST OF APPROVED MAKES FOR FIRE FIGHTING SYSTEM
SL. NO. | MATERIAL DESCRIPTION | NAME OF MANUFACTURER
1 | G.I./ M.S Forged Steel fittings IS:1239 (Part-II) | VS / DRP / True Forge / Simless
2 | MS Pipe | HSL, Mukut, Lalit steel or equivalent
3 | Ball valve | Enolgas/RB/AIP/Lehrey
4 | Butterfly Valve | Enolgas/RB/AIP/Lehrey
5 | Air Release Valve | Enolgas/RB/CIM
6 | Fire Extinguishers | Kanex or as recommended by GHIAL-ARFF
7 | Fire fighting first-aid hose reel | Kalpex/Lifeguard/Swastik
8 | Hose Reel | Kalpex/Lifeguard/Swastik
9 | Rubber Tubing | Kalpex/Lifeguard/Swastik
10 | Thermo Plastic Hose Reels | Kalpex/Lifeguard/Swastik
11 | R.R.L. Hose | Kalpex/Lifeguard/Swastik
12 | Fire Fighting Equipment not covered else where | Kalpex/Lifeguard/Swastik
13 | Landing Valves | Safedge/Lifeguard/Omex
14 | Welding rods | Adore/Ishab
15 | Flow Switch | System Sensor/Grinnel
16 | Motor Control Panel | Risha/Application/Adlec/Tricolite
17 | Fire Fighting Pumps | Marther & Platt/Lubi/Grundfoss
18 | Motor for Fire Pumps | ABB/Siemens/Lubi
19 | Sprinklers/Escutcheon plate/Flexible Pipes | Ansul, Buckeye, Smog Hog, Gem-Tyco, Spray safe or equivalent
20 | Cables/Wires | Finolax/Polycab/RR KABELS/KEI OR EQUIVALENT
21 | Cable Glands | Dowells/Gripwell/HMI
22 | Dash fasteners | Hilti/Fischer
23 | Clamps | Chilly/Lovely/Camery
24 | Y Strianers | WJ/Strainwell
25 | Foot Valve | Kirloskar/LEADER
26 | Fire Rated Paint | Temperkote, Flamex, Hy-Tech, Hilti, Birla, 3M
NOTES :-
1 | Contractor has to take approval from consultant/Architects for using any one of the above Approved Makes as mentioned above.
2 | In case, any other item/ material required to complete the work for which makes are not specified above, the Contractor shall take prior approval of the Architects/Consultants.