## FIRE FIGHTING
TFS DWARKA BASE KITCHEN MATIYALA
SUB-HEAD - A ( Fire Piping, Hydrants, Sprinklers and Accessories)
S.NO | DESCRIPTION | QTY | UNIT | RATE | AMOUNT
1 | Providing, laying, jointing and testing of following sizes of pipes conforming to IS-1239 with all accessories like all fittings (upto 50mm dia threaded M.S.forged fittings and above 50 mm dia MS fittings with welded joints shall be used)fittings including tees, elbows, reducers, flanges, rubber gaskets, nuts bolts, washer. And fixing the pipe on floor / wall /ceiling with suitable size clamps, hangers, structural steel supports as per specification. And PVC pipe sleeve to be provided wherever the pipes are crossing the walls/floors and sealing the sleeves as per consultants requirements including cutting holes and chases in brick, R.C.C work and making good the same to original conditions complete in all respects.Arrows showing direction of flow to be marked(with paint of approved colour) on each pipe at locations as decided at site.
(a) | For Fire fighting & sprinkler System - M.S. `C' Heavy class pipe
| a)25 mm dia(4.04mm thickness) screwed joint | 90 | RM |  | 0
| b)32 mm dia(4.05mm thickness)screwed joint | 10 | RM |  | 0
| c) 40 mm dia(4.05mm thickness)screwed joint | 20 | RM |  | 0
| d) 50 mm dia(4.5mm thickness)screwed joint | 15 | RM |  | 0
| e) 65 mm dia(4.5mm thickness) | 20 | RM |  | 0
| f) 80 mm dia(4.85mm thickness) | 100 | RM |  | 0
| g)100 mm dia(5.4mm thickness) | 10 | RM |  | 0
2 | Providing two coats of synthetic enamel paint of approved shade over a coat of primer. Including painting of legends both direction arrow as per the approval of the architects / consultants.
| a)25 mm dia | 90 | RM |  | 0
| b)32 mm dia | 10 | RM |  | 0
| c) 40 mm dia | 20 | RM |  | 0
| d) 50 mm dia | 15 | RM |  | 0
| e) 65 mm dia | 20 | RM |  | 0
| f) 80 mm dia | 100 | RM |  | 0
| g)100 mm dia | 10 | RM |  | 0
3 | Providing and fixing gun metal ball valve suitable for pressure 15 Kg/Cm2 and confirming to IS: 778 of the following size including providing necessary union / flange.
| a) 25 mm dia | 1 | NO. |  | 0
| b) 50 mm dia | 1 | NO. |  | 0
4 | Providing & fixing of butterfly valve suitable for pressure 15 Kg/Sqcm. with flanges, nut bolts & gaskets complete required.
| a) 65 mm dia | 1 | NO. |  | 0
| b) 80 mm dia | 3 | NOS |  | 0
| c) 100 mm dia | 2 | NOS |  | 0
5 | Providing and fixing of C.I. wafer type check valve suitable for pressure 15 Kg/Sqcm. with flanges, Nut, bolts & washers, painting etc. complete as required.
| a) 80 mm dia | 1 | NOS. |  | 0
| b) 100 mm dia | QR | NOS.
6 | Providing and fixing C.I.`Y' strainer with bronze perforated sheet basket tested to a pressure of 15 Kg/sqcm including rubber gasket, flanges, nuts, bolts and washers, complete as required.
| b) 100 mm dia | 1 | NO. |  | 0
7 | Providing & fixing gun metal fire hydrant valve with 80 mm N.B. flanged inlet, brass spindal, one no. 63 mm dia female instantaneous outlet type. G.M. coupling,blank cap, chain. Conforming to IS:5290. Including tapping from wet riser complete as required. | 1 | NOS |  | 0
8 | Providing & fixing swinging type First Aid hose reel in red colour with 36 mts long and 20 mm dia dia heavy duty rubber water hose, 20 mm dia globe valve stop cock, terminating with G.M. coupling & nozzle of 5mm outlet with shut off valve confirming to IS 8090 - 1976 complete with drum and brackets for fixing on wall, bolts & nuts conforming to IS:884-1969 complete as required. | 1 | NOS |  | 0
9 | Providing and Fixing Hose pipe, 63 mm dia and 15 mts long, duly reinforced, rubber lined suitable for brusting pressure not less than 22 Kg/Sqcm. conforming to IS 636-1988 type A with gun metal heavy duty instantaneous type coupling ( Pair male & female parts) conforming to IS 903. Complete as required (two nos. for each hydrant) | 2 | NOS |  | 0
10 | Providing and Fixing 63 mm dia instantaneous pattern branch short gunmetal pipe, 16 mm dia nozzle conforming to IS 903, suitable for inter connection to hose pipe coupling complete as required. | 1 | NOS |  | 0
11 | Providing and fixing standard firemans axe with heavy rubber handle. | 1 | NOS |  | 0
12 | Providing and fixing inlet breaching having C.I. body Two way gun metal 63 mm dia instantaneous inlets conforming to IS 903 fitted with non return valves, 25 mm dia gun metal drain cock, blank cap, brass chains and 100 mm dia flanges with all accessories suitable for local fire tender complete as required. | 1 | NO |  | 0
13 | Providing and fixing 4 mm thick glass door of size 2.1 m x 1.2 m with anodized aluminium frame of size 0.10 x 0.05 M with centre opening for fire hose cabinet. Suitably marked on the outside with the letters "FIRE HOSE" including locking arrangement. All aluminium work to be in Red P.O. colour. | 1 | NOS |  | 0
14 | Providing and fixing ISI Marked of approved make Fire Extinguishers complete with all accessories as per manufacturer's specifications.
| a) CO2 gas nozzle type - 4.5kg capacity (IS:15683). | 10 | NOS |  | 0
| b) Mechanical Foam gas cartridge type. 6 lts capacity (IS:15683). | 6 | NOS |  | 0
| c) ABC dry powder stored pressure type 9 kg capacity (IS:15683). | 10 | NOS |  | 0
15 | Supplying, installing, testing and commissioning of HDPE water storage tank including holes for inlet, outlet, overflow level indicator drain and vent points, manhole cover suitable supporting structure complete.
| a) Capacity 5000 Lts. | 4 | NOS |  | 0
16 | Approval of fire (NOC) system from local fire authority at initial & various other stages of works, including preperation of report / integration with Fire alarm system and preparation of drawings as per local fire authority. Contractor shall include cost of all liasion works which are not explicity mentioned above but are mendatory to have fire authority approved. | 1 | No |  | 0
17 | Providing & fixing C.P.brass quartzoid bulb sprinklers of size 15mm dia to be operated at 68Deg.C complete.Make of rosette plate- Veekay/Sainath fire/Safeworld/approved equal.
| a) Pendant type with heavy duty adjustable SS rosette plate | 44 | NOS. |  | 0
| b) Side wall extended throw type with heavy duty adjustable SS rosette plate | 2 | NOS. |  | 0
| c) Concealed type | QR | NOS.
| d) Upright type | QR | NOS.
18 | Providing & Fixing of installation control valve with turbine type automatic Alarm Gong to be connected with control valve, drain & test valve as per manufacturer's specifications complete.
| a) 80 mm dia | 1 | NO |  | 0
19 | Providing, jointing and testing of sprinklers through flexible connections(internal diameter 25mm & outlet connection15mm dia.) as per requirement at site.Make-SeungJin-Korea.The flexible connectors shall be supported through false ceiling through clamps or as directed at site.The flexible connector shall be suitable for working pressure12 kg/sqcm . | 44 | NOS |  | 0
20 | Providing & installing MS 24 gauge fire buckets ( capacity of each bucket = 9 lts) filled with sand including MS stand for hanging the buckets.All MS items shall be painted with two coats of primer & two coats of paint of approved colour.
| Set of four buckets with stand | 2 | NOS |  | 0
21 | Supply, installation, testing and commissioning of Down comer pump comprising of the following:
(a) | Horizontally mounted centrifugal pump, suitable for operation on 415 volts ± 10%, 3 phase, 50 HZ A.C supply. Fire pump having C.I. body, bronze impeller and S.S. Shaft with mechanical seal, capable for deliverying 900 LPM of water at 35 mts. head. Complete with necessary pressure gauge with gun metal shut off cock and syphon on delivery side. The pump should meet the condition of Local fire Authority. Cost shall include electrical control panel with wiring/cabelling /control cabelling complete to make the system operational as per requirement of Fire Authorities.
(b) | Squirrel cage induction motor TEFC type for operation on 415 V, 3 phase 50 HZ AC supply for the above pump with a synchronous speed of 2900 R.P.M. with flexible coupling and coupling guard etc. as required.
(c) | Common base plate for (a) and (b) from M.S. channel as required size.
(d) | Suitable cement concrete foundation with plaster, Antivibration arrangement of cushy foot mounting. | 1 | NO |  | 0
| TOTAL CARRIED TO SUMMARY |  |  |  | 0

## MAKES
PLUMBING
S No. | Item | Make
1 | Vitreous China Sanitaryware | As Approved
2 | C.P. Brass fittings | Jaquar/Hindware/ as approved
3 | Cast iron pipes & fittings, Manhole covers and frames. | NECO/RIF
4 | G.I. pipes. | Tata/Jindal Hissar/Prakash Surya
5 | G.I. pipes fittings. | K.S. / Unik / `R’ Brand
6 | R.C.C pipe | K.K. / App. Equivalent ISI marked
7 | Stoneware pipes, Gully traps | Perfect potteries, Jabalpur / Approved equivalent ISI marked
8 | Valves | Zoloto / Leader/ C & R / Advance
9 | Paints | Asian Paints / Shalimar Paints /Berger
10 | Pressure Gauge | H Guru/Fiebig
11 | Pumps | Grundfoss/ITT/Kirloskar/KSB
12 | Level Controller & Indicator (Water) | Advance Auto/Technika / Minilec
13 | PVC Pipes | Supreme / Prince/Astral
14 | Urinal Sensor | UTEC System/Jaquar/Hindware
15 | Geyser | Venus/Racold/AO Smith
16 | Sink | Neelkanth/Kobra/Hindware
17 | Water purifier | Eureka Forbes/Kent
18 | HDPE Water tanks | Sintex/Frontier
19 | CPVC Pipes | Aashirwad/Finolex/Astral
20 | Gratings,Cleanouts,Funnels | GMGR/Neer/Jayna
ELECTRICAL
S No. | Item | Make
1 | Conduits | Precision/ AKG/ BEC
2 | FRLS Wires | Finolex / Havells/ KEI/ Polycab
3 | Cables | Polycab/ Havells/ Finolex
4 | Switches | Legrand /Roma / Clipsal/ Opale/ Crabtree/ Northwest
5 | Distribution Boards | Siemens/ MDS/ legrand / L&T
6 | MCB’s /ELCB’s | Siemens/ MDS/ legrand / L&T
7 | Telephone/Speaker Wires | Finolex/ Polycab/ Falcon
8 | T.V.Wires | Comscop/ Finolex
11 | Switch Fuse Units/ Starters | L&T/ Siemens
12 | Fire Alarm System | Apollo/ System Sensor/ Agni/ Honeywell/ Ravel
13 | Data Cable / IO | Amp (TE)/ D Link
14 | Light Fittings | Havells/Wipro/Philips
Notes:-
[1] The Contractor should quote the tender rates considering First make of materials given in above list.
[2] Wherever contractor proposes to use `equivalent' makes (i.e. other than specified) he shall obtain Client's prior approval. Client may consult Consultants before giving approval to the same. Any additional cost and time lost due to this will be on Contractor's account and no claims will be entertained.
[3] The contractor should take approval for make & manufacturer from the TFS before using any material, which does not appear in the list of approved manufacturers.
FIRE FIGHTING
S No. | Item | Make
1 | G.I./M.S pipes. | Tata/Jindal Hissar/Prakash Surya
2 | MS Forged fittings. | VS/KS
3 | Valves | Zoloto / Leader/ C & R / Advance
4 | `Y' strainer | Emerald Enterprises / Zoloto/Kartar
5 | Level Controller & Indicator (Water) | Advance Auto/Technika / Minilec
6 | Paints | Asian Paints / Shalimar Paints /Berger
7 | Pressure Gauge | H Guru/Fiebig
8 | Flexible Rubber Expansion Joint | Kanwal Easyflex/Resistoflex
9 | Pumps | Kirloskar/Mather & Platt /KSB
10 | Fire Fighting Equipments | Minimax/Safeguard/Getech
11 | Sprinklers | Tyco/Grinnel/Best/HD
12 | Welding Rods | Advani/Victor
13 | GI Hangers | Chilly/GMGR