## HVAC
SCHEDULE OF QUANTITIES (as on 26-09-24)-R0
S. NO | ITEM DESCRIPTION | UNIT | QTY. | RATE | AMOUNT | REMARKS
SECTION 'A' - HVAC WORK
1.0 | EQUIPMENT
1.1 | SPLIT UNITS
Supply , Installation, Testing and Commissioning of split units, each comprising of an outdoor and a single indoor unit as shown on the drawings and as per the specifications. Enclosures shall be factory fabricated and painted to a smooth finish. Oudoor unit shall consist of hermatically sealed/ semi- hermatic scroll/rotary compressor/s, air cooled condenser with fan. Indoor unit shall consist of fan section with dynamically balanced centrifugal fan/s driven by FHP/TEFC squirrel cage induction motor, multirows deep DX- copper cooling coil with aluminium fins, thermostatic expansion valve, synthetic fibre filters, insulated drain pan, safety controls, safety controls, thermostat all complete in a unit. The quoted price shall be inclusive of full charge of refrigerant gas, vibration isolation arrangement.
Refrigerant Shall be R-32/R410A/R407C
A. | Three phase ductable split units with Scroll compressor :
Unit should be suitable to handle total 35-40RM inter
unit referigerant piping inlcuding 12-15RM vertical length.
a. | 11.0TR nominal capacity, split unit with single ductable type indoor unit and factory fitted electrical arrangement & corded remote. | No | - |  |  | Rate Only
b. | 8.5TR nominal capacity, split unit with single ductable type indoor unit and factory fitted electrical arrangement & corded remote. | No | 1 |  | 0
c. | 5.5TR nominal capacity, split unit with single ductable type indoor unit and factory fitted electrical arrangement & corded remote. | No | - |  |  | Rate Only
d. | 4.0TR nominal capacity, split unit with single ductable type indoor unit and factory fitted electrical arrangement & corded remote. | No | - |  |  | Rate Only
e. | 3.5TR nominal capacity, split unit with single ductable type indoor unit and factory fitted electrical arrangement & corded remote. | No | - |  |  | Rate Only
B. | Three phase non-ductable split units with rotary compressor (Three Star Rating) :(Units should be suitable to handle piping length upto 24-25 RM)
a. | 2.5TR nominal capacity, split unit with single Cassette type indoor unit and cordless control . Price shall be inclusive of copper power cabling from indoor to outdoor unit as required. | No | - |  |  | Rate Only
C. | Single phase Non-ductable split units with Rotary compressor (Three Star Rating) :(Units should be suitable to handle piping length upto 24-25 RM)
a. | 1.5TR nominal capacity, split unit with single Wall Mounted type indoor unit and cordless control . Price shall be inclusive of copper power cabling from indoor to outdoor unit as required. | No | 2 |  | 0
b. | 1.5TR nominal capacity, split unit with single Cassette type indoor unit and cordless control . Price shall be inclusive of copper power cabling from indoor to outdoor unit as required. | No | - |  |  | Rate Only
1.2 | Supply, Installation , Testing and
Commissioning of PLC for Auto Sequencing
of Split units with micrprocessor based
controller along with enclosure/accessories & Control wiring
having facility for configuration of the same
as per requirement for sequenced Start/Stop
for following split units :
a. | Three number Split units including one standby for Server Room. | Sets | - |  |  | Rate Only
1.3 | REFRIGERANT PIPING
Supply, Installation,Testing & Commissioning of copper refrigerant piping complete with copper fittings & charge of regrigerant gas for the above split units. Piping associated with split units to be insulated with 19mm thick closed cell elastomeric insulation with Class 'O' in tubing form as required. Piping shall be laid over duly painted slotted angle trays fixed with GI clamps. Quoted Price shall be inclusive of UV protection paint for all exposed pipes of approved make. Price shall be inclusive of copper power cabling from indoor to outdoor unit as required. Referigerant piping shall be epoxy coated to prevent erosion.
a. | Pair of hard drawn copper refrigerant piping for the above split units with scroll compressor. | RM | 25 |  | 0
b. | Pair of Soft refrigerant piping for non ductable split units with rotary compressor. | RM | 55 |  | 0
1.4 | STABILISERS
Supply, Installation,Testing & Commissioning of automatic voltage stabilisers suitable for operation on 140-280 V incoming supply supply with time delay relay for single phase split units.
| a. 4 KVA Capacity | No | - |  |  | Rate Only
| b. 5 KVA Capacity | No | - |  |  | Rate Only
1.5 | DRAIN PUMP
Supply, Installation,Testing & Commissioning of drain pump for Hi-wall split units complete with all accessories as required. Drain Pump shall be suitable for operation on 220+6 % volts 50 Hz,1phase AC power supply.
a. | Drain pump for Hi-wall split units (Server Room / UPS Room) | Nos. | - |  |  | Rate Only
1.6 | MS FRAME FOR ODUs
Supply and Erection of MS base frame duly
applied with red-oxide primer & followed by
| black enamel paint for mounting of outdoor units. | Kg | 55 |  | 0
SUB TOTAL (EQUIPMENT) Rs. | TOTAL ITEM NO. 1 (EQUIPMENT) |  |  | Rs. | 0
2.0 | PIPING
2.1 | CONDENSATE DRAIN PIPING
2.1.1 | USING GI PIPING
Supply, Installation , Testing and Commissioning of GI medium class (Class 'B') pipes cut to requird lengths and installed with all screwed joints for condensate drain. Quoted price shall be inclusive of supply and fixing in position the necessary fittings like elbows, tees reducers etc., and supporting arrangement in accordance with the approved shop drawings and specifications.Pipes shall be insulated with 9mm thick closed cell elastomeric insulation with class 'O' fire retardant properties in tubing form . Pipes shall be of following sizes :
a. | 65mm dia | RM | - |  |  | Rate Only
b. | 50mm dia | RM | - |  |  | Rate Only
c. | 40mm dia | RM | - |  |  | Rate Only
d. | 25mm dia | RM | - |  |  | Rate Only
2.1.2 | CONDENSATE DRAIN PIPING -cPVC
Supply, Installation, Testing and Commissioning of cPVC pipes cut to required lengths and installed for condensate drain. Quoted price shall be inclusive of supply and fixing in position the necessary fittings like elbows, tees reducers etc. and supporting arrangement in accordance with the approved shop drawings and specifications. Pipes shall be insulated with 9mm thick closed cell elastomeric insulation with class 'O' fire retardant properties in tubing form . Pipes shall be of following sizes :
a. | 50mm dia | RM | 5 |  | 0
b. | 40mm dia | RM | 10 |  | 0
c. | 32mm dia | RM | 2 |  | 0
d. | 25mm dia | RM | 5 |  | 0
| TOTAL ITEM NO. 2 (PIPING ) |  |  | Rs. | 0
3 | DUCTWORK/AIR TERMINALS
3.1 | FACTORY FABRICATED DUCTING
Supply , Installation and Testing of factory fabricated GSS ducting complete with vanes, splitter dampers, fire retardant gaskets hanging arrangement including fully threaded GI rods and GI "C" channels, GI "C" channels etc. as approved by clients/consultants in accordance with the approved shop drawings and specifications. Quoted price shall be inclusive of necessary scaffolding charges towards installation of supply/exhaust air ducts outside or within building wherever required. Quoted price should also include necessary charges towards duct supporets including MS angle/channel arrangement as required for ducts being installed outside or within building wherever required.
Spacing between duct supports should not exceed 2m. All duct support to be provided with check nuts (lock nuts).
While selecting the duct supports vendor shall ensure vibration free installation.Quoted price shall be inclusive of smoke test using smoke bombs.
a. | 1mm to 899mm -- 26G GSS with TDC Joints | SqM | 5 |  | 0
b. | 900mm to 1200mm -- 24G GSS with TDC Joints | SqM | 10 |  | 0
c. | 1201mm to 1800mm - 22G GSS with TDC Joints | SqM | 5 |  | 0
d. | 1801mm to 2100mm - 20G GSS with TDC Joints | SqM | - |  |  | Rate Only
e. | 2101mm to 2700mm - 18G GSS with TDC Joints | SqM | - |  |  | Rate Only
3.2 | SITE FABRICATED DUCTING
Supply, Fabrication, Installation and Testing of sheet
metal ducts complete with vanes, splitter dampers,
hanging arrangement including check nuts in
accordance with the approved shop drawings
and specifications
| a. 0.63mm (24 gauge) GSS | SqM | 10 |  | 0
| b. 0.8 mm (22 gauge) GSS | SqM | 5 |  | 0
| c. 1.0mm (20 gauge) GSS | SqM | - |  |  | Rate Only
| d. 1.25mm (18 gauge) GSS | SqM | - |  |  | Rate Only
3.3 | FLAT OVAL SPIRAL DUCT
Supply, Installation and Testing of factory fabricated & factory internally insulated GSS flat oval spiral ducting complete with vanes,splitter dampers, fire retardant gaskets hanging arrangement including fully threaded GI rods , GI straps and GI "C" channels/ rolled steel wires or Gripple Wire Rope Hangers & Supports complete with end fixing, GI "C" channels etc. as approved clients/consultants in accordance with the approved shop drawings and specifications.Quoted price shall be inclusive of necessary scaffolding charges towards installation of supply/exhaust air ducts outside or within building wherever required.
Duct Insulation shall be as follows :
20mm thick open cell nitrile rubber insulation of density within 140-180 Kg/m3 with perforated aluminium foil.
Ducts shall be factory powder coated of colour and
shade as approved by the Architects for exposed spiral
ducts. Quoted price shall be inclusive of powder coating.
Necessary compliance to be submitted by vendors.
Without Powder Coated-With 9mm thick insulation
a. | 1mm to 600mm -- 24G GSS | SqM | - |  |  | Rate Only
b. | 601mm to 1200mm -- 22G GSS | SqM | - |  |  | Rate Only
c. | 1201mm to 1700mm -- 20G GSS | SqM | - |  |  | Rate Only
Without Powder Coated-With 13mm thick insulation
a. | 1mm to 600mm -- 24G GSS | SqM | - |  |  | Rate Only
b. | 601mm to 1200mm -- 22G GSS | SqM | - |  |  | Rate Only
c. | 1201mm to 1700mm -- 20G GSS | SqM | - |  |  | Rate Only
3.4 | ENAMEL PAINT (For Exposed Duct) - LOW VOC
| Supply and Application of minimum two coats of Enamel of colour and shade as approved by the Architects for exposed ducts. Quoted price shall be inclusive of primer before paint and all neceesary arrangement as required for providing the paint over duct. | SqM | - |  |  | Rate Only
3.5 | FLEXIBLE CANVASS CONNECTIONS
| Supply, Installation, Testing of 125mm deep antivibration flexible joints at the outlet of air handling units/ductable split units//inline fans. Flexible connections shall be constructed using imported fire retardant fabric with extruded aluminium frame/flange on both sides of approved make. | RM | 4 |  | 0
3.6 | SUPPLY AIR DIFFUSERS
3.6.1 | Supply, Installation, Testing and Balancing of square supply air diffusers with removable key operated volume control dampers with opposed blades as per the approved shop drawings and specifications.The diffusers shall be anti-smudge ring type/flat type as approved by the interior designer. Diffusers shall be with removable core for the following neck sizes. The diffusers shall be suitable for fixing in the gypsum ceiling. The diffusers shall be of regular type and with outer dimension of 450 x 450mm, 375mmx375mm & 300mmx300mm.
| Powder coated extruded aluminium diffusers of approved colour & shade. | SqM | - |  |  | Rate Only
3.5.2 | Supply, Installation, Testing and Balancing of square supply air diffusers with removable key operated volume control dampers with opposed blades & 150mm high GSS plenum as per the approved shop drawings and specifications.The diffusers shall be anti-smudge ring type/flat type as approved by the interior designer. Diffusers shall be with removable core for the following neck sizes. The diffusers shall be suitable for fixing in the gypsum/grid ceiling. The diffusers shall be of regular type and with outer dimension of 600 x 600mm.
| 600x600 Powder coated extruded aluminium diffusers of approved colour & shade suitable for fixing in grid ceiling. | No | - |  |  | Rate Only
3.6 | RETURN AIR DIFFUSERS
3.6.1 | Supply, Installation,Testing and Balancing of square return air diffusers same as supply air diffusers but without volume control dampers as per the approved shop drawings and specifications. The diffusers shall be anti -smudge ring type.
| Powder coated extruded aluminium diffusers of approved colour & shade. | SqM | - |  |  | Rate Only
3.6.2 | Supply, Installation,Testing and Balancing of square return air diffusers same as supply air diffusers but without volume control dampers as per the approved shop drawings and specifications. The diffusers shall be anti -smudge ring /flat type.
| 600x600 Powder coated extruded aluminium diffusers of approved colour & shade suitable for fixing in grid ceiling. | No | - |  |  | Rate Only
3.7 | LINEAR GRILLES
Supply, Installation , Testing and Balancing of one way blow linear supply cum return air grilles complete with fixed core as per approved shop drawings and specifications. The grilles shall be of approved colour & shade.
Powder coated aluminium grilles of extruded sections with integral flanges on both sides & ends as required complete with corner pieces.
| i. 100/150/200/250 mm High grilles | SqM | 1 |  | 0
3.7 | DOUBLE LOUVERED GRILLES
Supply, Installation ,Testing and Balancing of double
louvered supply air grilles as per approved shop drawings
and specifications complete with key operated aluminium
volume control dampers.
| a. Powder coated extruded aluminium grilles. | SqM | 0.5 |  | 0
3.8 | AIR TRANSFER GRILLES
| Supply, Installation and Testing of extruded aluminium powder coated air transfer grilles to be provided at the door of toilets/pantry. | SqM | 0.2 |  | 0
3.9 | Supply, Installation, Testing and Balancing of linear slot diffusers with Hit & Miss type extruded aluminium volume control dampers at supply air outlets as per the approved shop drawings and specifications.
a. | 3 slot/2slot, powder coated extruded aluminium diffusers of approved colour & shade for supply air with Hit & Miss type dampers | SqM | - |  |  | Rate Only
b. | 3 slot/2slot, powder coated extruded aluminium diffusers of approved colour & shade for return air without Hit & Miss type dampers | SqM | - |  |  | Rate Only
3.1 | ROUND DIFFUSERS
Supply, Installation, Testing and Balancing of
round supply air diffusers with removable key operated
butterfly volume control dampers as per the approved shop
drawings and specifications.The diffusers shall be anti-
smudge flush type as approved by the interior designer.
Diffuser shall be complete with GI cone with circular
connection at the rear.
Powder coated extruded aluminium diffusers of
approved colour & shade :
3.10.1 | With Volume Control Dampers
a. | 400mm dia round diffuser with GI cone | No | - |  |  | Rate Only
b. | 300mm dia round diffuser with GI cone | No | - |  |  | Rate Only
c. | 200mm dia round diffuser with GI cone | No | - |  |  | Rate Only
3.10.2 | Without Volume Control Dampers
a. | 400mm dia round diffuser with GI cone | No | - |  |  | Rate Only
b. | 300mm dia round diffuser with GI cone | No | - |  |  | Rate Only
c. | 200mm dia round diffuser with GI cone | No | - |  |  | Rate Only
3.11 | Supply, Installation,Testing and Balancing of
flexible ducting comprising of inner as well as outer
skin constructed out of aluminium & fibre glass
insulation 25mm thick of minimum 24 kg/cu.m density
insulation sandwitched in between. Duct should confirm
to fire rating standards BS-476 part 5, 6 & 7. Flexible
Ducts of following sizes as per approved shop drawings,
specifications :
a. | 300 mm dia | RM | - |  |  | Rate Only
b. | 250 mm dia | RM | - |  |  | Rate Only
c. | 200 mm dia | RM | - |  |  | Rate Only
d. | 150 mm dia | RM | - |  |  | Rate Only
3.12 | Supply, Installation and Testing of single
piece GI round spigot made out of spinning process
with 50mm height and having grooves on both sides
and circular flanges. Spigots shall be installed on main
ducts to facilitate connection of flexible ducts.
a. | 300 mm dia | No | - |  |  | Rate Only
b. | 250 mm dia | No | - |  |  | Rate Only
c. | 200 mm dia | No | - |  |  | Rate Only
d. | 150 mm dia | No | - |  |  | Rate Only
3.13 | Supply, Installation and Testing of Butterfly damper
of aluminium sheet construction with two flap with
sleeve as per thespecifications and shop drawings.
a. | 200 mm dia | No | - |  |  | Rate Only
b. | 250 mm dia | No | - |  |  | Rate Only
c. | 300 mm dia | No | - |  |  | Rate Only
d. | 375 mm dia | No | - |  |  | Rate Only
3.14 | Supply, Installation and Testing of GI box type
volume control dampers as per the specifications
| and shop drawings.- For Rectangular Duct | SqM | 0.5 |  | 0
3.15 | Supply, Installation and Testing of GI box type
volume control dampers as per the specifications
| and shop drawings.- For Flat Oval Ducts | SqM | - |  |  | Rate Only
3.16 | Supply, Installation and Testing of GI multi blade
type louver dampers as per the specifications
| and shop drawings. | SqM | 1 |  | 0
3.17 | Supply, Installation,Testing and Commissioning
of motorised fire dampers suitable for at least
90 minutes fire rating as per the specifications
and approved shop drawings. Quoted price shall
be inclusive of copper control wiring as required.
a. | Bare Fire Dampers | SqM | - |  |  | Rate Only
b. | Spring return action type actuator complete with
| control panel and temperature sensor. Torque not less | No | - |  |  | Rate Only
than 16NM
3.18 | Supply, Installation and Testing of fresh air
grilles of powder coated / anodised extruded
aluminium with GI wire mesh, inlet louvers,
Box type VCD & bird screen, as per the approved
| shop drawings and specifications. | SqM | -- |  |  | Rate Only
3.19 | Supply, Installation and Testing of extruded aluminium
powder coated louver with GI wire mesh to be installed
outside for discharge of exhaust air from exhaust fans
as per the specifications and shop drawings.
Sample of louvers to be got approved from consultants
| and Clients prior to procurement. | SqM | -- |  |  | Rate Only
3.2 | Supply, Installation and Testing of Bird Screens with GI
wire mesh to be installed at the suction of fresh air/discharge
of Exhaust air as per the specifications and shop drawings.
Sample of bird screen to be got approved from consultants
| and Clients prior to procurement. | SqM | -- |  |  | Rate Only
3.21 | Supply, Installation and Testing of non return dampers.
NRDs to be installed in the ducts as per
the specifications and shop drawings.
Sample of NRDs to be got approved from consultants
| and Clients prior to procurement. | SqM | -- |  |  | Rate Only
3.22 | Motorised VCD
a. | Supply, Installation and Testing of multiblade box type zero leakage extruded aluminium dampers for ducts to be provided with suitable links, levers and quadrants for manual control of volume of air flow and for proper balancing of the air distribution system as per the approved shop drawing and specifications. | SqM | -- |  |  | Rate Only
b. | Supply and fixing of actuators of suitable rating of torque complete with, conrtrol panel, transformer, copper wiring from the junction box and actuator associated with the above VCDs.
| Actuator shall be suitable for duct size as shown in the drawing. | No | -- |  |  | Rate Only
TOTAL (AIR DISTRIBUTION) Rs. | TOTAL ITEM NO.3 (Ducting & Air Terminals) |  |  | Rs. | 0
4 | INSULATION
4.1 | ACOUSTIC LINING OF DUCTS
4.1.1 | Using Open Cell Nitrile Rubber
Supply and Application of internal acoustic lining of supply air ducting using open cell nitrile rubber insulation with density within 140-180 Kg/m3 as per the approved shop drawings and specifications. Insulation material shall be bonded with the ducts using metal screw and washers to facilitate grip to the GI sheet. Adhesive used shall be Low VOC type.
a. | 10mm thick lining | SqM | 5 |  | 0
4.1.2 | Using Fibre Glass
Supply and Application of internal acoustic
lining of supply/return air ducting using resin bonded
fibre glass insulation of density not less than 32Kg/CuM
as per the approved shop drawings and specifications.
Quoted price shall be inclusive of GSS channel, metal
screws, washers, fibre glass tissue, perforated sheet
etc. as required for complete installation.
a. | 25mm thick lining | SqM | 10 |  | 0
4.2 | THERMAL INSULATION OF DUCTS
(Using Factory Laminated aluminium foil faced,
Class 'O' Closed Cell Elastomeric insulation)
Supply and Application of internal / external thermal insulation of
supply /return air ducting using closed
cell elastomeric insulation with class 'O' fire retardant
properties as per the specifications and drawings.
Adhesive used shall be Low VOC type.
a. | 9mm thick insulation- S/Air Duct in contact with R/Air | SqM | -- |  |  | Rate Only
b. | 13mm thick insulation | SqM | 30 |  | 0
c. | 16mm thick insulation (Fresh air duct in ac area) | SqM | -- |  |  | Rate Only
TOTAL (AIR DISTRIBUTION) Rs. | TOTAL ITEM NO. 4 (INSULATION) |  |  | Rs. | 0
SECTION "B" : KITCHEN VENTILATION SYSTEM
S.NO | ITEM DESCRIPTION | UNIT | QTY. | RATE | AMOUNT | AMOUNT
1 | EQUIPMENT
1.1 | DOUBLE SKIN AIR COOLING MACHINES - With Fresh Air Intake Section
(AIR WASHERS)
Supply , Installation, Testing and Commissioning of
double skin type evaporative air cooling machines
(packaged type) each comprising of following as
per the specifications :
a. | Casing of air washer shall be in double skin
construction. Inner skin shall be constructed out of
24 gauge plain GS sheet & outer skin in 24 gauge
pre-plasticized GS sheet sandwitched between
50mm thick injected PU foam insulation of density
not less than 40 Kg /CuM and complete with marine light,
limit switch & inspection doors including control wiring
as required. Air washer shall have access for all parts.
b. | Fan section complete with backward curved DIDW
type centrifugal fan/s, EFF1, IE3, IP-55, rated TEFC squirrel cage
induction motor suitable to operate on 415+10%V, 50Hz,
3 phase AC power supply and belt drive package.
Centrifugal fans shall be coated with epoxy paint as specified.
Fan outlet velocity shall not be more than 2000 FPM
(10.16 MPS).
All fans should be AMCA certified.
c. | AirWasher shall be provided with Intake Section with
F/A openings as per approved shop drawing.
d. | Air washer wet section shall be complete with 300mm
thick cellulose based paper fills, drift eliminators,
water distribution system complete with FRP spray
headers, strainer of fine mesh brass screen, globe valve,
float valve, quick fill, over flow & drain
connections, GI medium class piping and 3/1 phase
monobloc pumps of 1HP/ 1.5HP/2HP motor rating
as required according to the capacity of air cooling
machines. Inner skin of wet section including fills
mounting frame shall be constructed out of stainless
steel SS- 304 A grade of appropriate thickness .Sump
shall be made out of 1.25mm thick SS-304 A grade
stainless steel .Velocity across the paper fills not to
exceed 500 FPM.
e. | Filter section complete with 50mm thick aluminium
wire mesh viscous metallic filters. Velocity across
the filters shall not exceed 500 FPM.
Airwasher should be provided with adequate space between eliminator & fan to avoid water carryover.
The Evaporative Air Cooling Machines (EAC) shall
be of following duty parameters :
M/c No Capacity S.P Motor Area to
(Cfm) (mmWG) Rating be fed
(HP)
| EAC-1 1x22500 58-60 1x15.0 Kitchen | No | 1 |  | 0
1.2 | SCRUBBER (For Kitchen Exhaust)
1.2.1 | WET TYPE SCRUBBER
Supply , Installation , Testing and Commissioning of
wet type scrubber (packaged type) comprising
of following as per the specifications :
a. | Fan section complete with backward curved DIDW
type centrifugal fan/s, TEFC squirrel cage induction
motor suitable to operate on 415+10%V, 50Hz,
3 phase AC power supply and belt drive package.
Casing of wet type scrubber shall be constructed
out of 16 gauge GS sheet complete with inspection
doors as required. Centrifugal fans shall be coated
with epoxy paint as specified. Fan outlet velocity
shall not be more than 2000 FPM (10.16 MPS).
b. | Wet section complete with double bank spray header in
GI construction and nozzles, louvers PVC mist eliminators
& mist collection tray made out of 16G GSS,
strainer of fine mesh brass screen, globe valve,
float valve, quick fill, over flow & drain
connections, GI medium class piping and 3 phase
monobloc pump of 1.5HP motor rating
as required according to the capacity of scrubber
machines. Wet section including sump will be made of
1.25mm thick SS-304 A grade stainless steel .
c. | In addition to the above, scrubber shall be
provided with adequate vibration isolation pads
and fire retardent flexible canvass connections made
out of canvass sleeve.
The Scrubber Machines (EAC) shall be of following
duty parameters :
M/c No Capacity S.P Motor Area to
(Cfm) (mmWG) Rating be fed
(HP)
| WS-1 28000 68-70 20.0 Kitchen Area | No | 1 |  | 0
1.3 | AIR CURTAIN
Supply , Installation and Testing of
air curtains with noiseless, statically & dynamically
balanced aluminium blowers, cleanable type
pre-filters, motor & powder coated
aluminium enclosure as per the specifications.
Unit shall be complete with Plug Top & necessary
power cable.
a. | 2.4 M long air curtain | No | - |  |  | Rate Only
b. | 2.1 M long air curtain | No | 1 |  | 0
c. | 1.5 M long air curtain | No | 2 |  | 0
d. | 1.2 M long air curtain | No | -- |  |  | Rate Only
(Actual size & qty of air Curtain shall be as per approved shop drawing)
1.4 | VENTILATION FANS
1.4.1 | INLINE FANS (Single Phase)
Supply, Installation, Testing & Commissioning of circular /rectangular inline fans for exhaust air complete with sheet metal casing, direct driven centrifugal fan, motor with proper protection and inspection door. Fan shall be suitable for operation on 220+6 % volts, 50 Hz,1phase AC power supply. Fan shall be installed as shown in the drawings and will be of following characteristics : All single phase inline fans shall be provided with factory fitted speed regulators. All Fans Should be complete with Plug Top & necessary power cable.
Fan Capacity S.P Area to
No. (Cfm) (mmWG) to be exhausted
| IF-1(Circular) 300 14-15 Pantry | No | 1 |  | 0
| TOTAL ITEM NO. 1 (EQUIPMENT) |  |  | Rs. | 0
2 | DUCTWORK/AIR TERMINALS - INCLUDING IN SECTION 'A'
2.1 | FACTORY FABRICATED DUCTING
Supply, Installation and Testing of factory fabricated GSS ducting complete with vanes,splitter dampers, fire retardant gaskets, hanging arrangement including fully threaded GI rods and GI "C" channels/ rolled steel wires or Gripple Wire Rope Hangers & Supports complete with end fixing, GI "C" channels etc. as approved by clients/consultants in accordance with the approved shop drawings and specifications. Quoted price shall be inclusive of necessary scaffolding charges towards installation of supply/exhaust air ducts outside or within building wherever required.
Spacing between duct supports should not exceed 2m in both cases i.e GI rods with GI "C" channels & Gripple Wire Rope Hanger support . In case of Gripple Wire Rope Hanger support for duct sizes above 1800mm, MS angles duly painted with black enamel paint should be used along with neoprene pad in between the duct & MS angle. All duct supports shall be provided with check nuts (lock nuts).
While selecting the duct supports vendor shall ensure
vibration free installation.Quoted price shall be inclusive of smoke
test using smoke bombs.
For Air-Cooling ducts
a. | 1mm to 899mm -- 24G GSS with TDC Joints | SqM | 50 |  | 0
b. | 900mm to 1500mm -- 22G GSS with TDC Joints | SqM | 50 |  | 0
c. | 1501mm to 2100mm - 20G GSS with TDC Joints | SqM | 10 |  | 0
d. | 2101mm to 2700mm - 18G GSS with TDC Joints | SqM | -- |  |  | Rate Only
2.2 | DUCO PAINT (For Exposed Duct)
| Supply and Application of minimum two coats of Duco of colour and shade as approved by the Architects for exposed ducts. Quoted price shall be inclusive of primer before paint and all neceesary arrangement as required for providing the paint over duct. | SqM | -- |  |  | Rate Only
2.3 | SITE FABRICATED DUCTING
Supply, Fabrication, Installation and Testing of sheet metal ducts complete with vanes, splitter dampers, hanging arrangement including check nuts in accordance with the approved shop drawings and specifications.
| a. 0.63mm (24 gauge) GSS | SqM | 15 |  | 0
| b. 0.8 mm (22 gauge) GSS | SqM | 5 |  | 0
| c. 1.0mm (20 gauge) GSS | SqM | 5 |  | 0
| d. 1.25mm (18 gauge) GSS | SqM | - |  |  | Rate Only
2.4 | For Kitchen Exhaust
Supply, fabrication, Installation and testing of MS ducting
for kitchen exhaust contructed out of 2mm thick
MS sheet using MS angle iron flanges in line with
good engineering practice. Entire ducting shall be
applied with minimum two coats of red oxide primer.
| Duct shall be provided with oil trap as required | SqM | 140 |  | 0
2.5 | FLEXIBLE CANVASS CONNECTIONS
| Supply, Installation, Testing of 125mm deep antivibration flexible joints at the outlet of air handling units/ductable split units//inline fans. Flexible connections shall be constructed using imported fire retardant fabric with extruded aluminium frame/flange on both sides of approved make. | RM | 8.5 |  | 0
2.6 | LINEAR GRILLES
Supply, Installation , Testing and Balancing of one way blow linear supply cum return air grilles complete with fixed core as per approved shop drawings and specifications. The grilles shall be of approved colour & shade.
Powder coated aluminium grilles of extruded sections with integral flanges on both sides & ends as required complete with corner pieces.
| i. 100/150/200/250 mm High grilles | SqM | 8 |  | 0
2.7 | AIR TRANSFER GRILLES
| Supply, Installation and Testing of of extruded aluminium powder coated air transfer grilles to be provided at the door of toilets/pantry. | SqM | - |  |  | Rate Only
2.8 | Supply, Installation and Testing of GI box type
volume control dampers as per the specifications
| and shop drawings. | SqM | 3.5 |  | 0
2.9 | Supply, Installation and Testing of Aluminium multi blade
type louver dampers as per the specifications
| and shop drawings. | SqM | 6 |  | 0
2.1 | Supply, Installation and Testing of fresh air
powdered coated / anodised extruded aluminium
louvers to be installed outside for suction ( airwashers),
as per approved shop drawings and specifications.
Sample of louvers to be got approved from consultants
| and Clients prior to procurement. | SqM | 1 |  | 0
2.11 | Supply, Installation and Testing of Bird Screens with GI
wire mesh to be installed at the suction of fresh air/discharge
of Exhaust air as per the specifications and shop drawings.
Sample of bird screen to be got approved from consultants
| and Clients prior to procurement. | SqM | 1 |  | 0
2.12 | Supply, Installation and Testing of non return dampers.
NRDs to be installed in the ducts as per
the specifications and shop drawings.
Sample of NRDs to be got approved from consultants
| and Clients prior to procurement. | SqM | - |  |  | Rate Only
| TOTAL ITEM NO. 2 (Ducting & Air Terminals) |  |  | Rs. | 0
3.0 | INSULATION
3.1 | THERMAL INSULATION OF DUCTS-(FOR AIR SCRUBBER DUCT)
(Using Factory Laminated fibre glass insulation)
Supply and Application of external thermal
insulation of supply /return air ducting using
aluminium foil faced fibre glass insulation of density
not less than 24Kg/CuM and aluminium foil thickness of 22
microns as per the specifications and drawings. Quoted
price shall be inclusive of Low VOC adhesive as required,
aluminium tape straps.
a. | 25mm thick insulation | SqM | - |  |  | Rate Only
b. | 50mm thick insulation | SqM | 140 |  | 0
3.2 | THERMAL INSULATION OF DUCTS-(FOR AIR SCRUBBER DUCT) - EXPOSED
(Using Factory Laminated fibre glass insulation)
Supply and Application of external thermal
insulation of supply /return air ducting using
aluminium foil faced fibre glass insulation of density
not less than 24Kg/CuM and aluminium foil thickness of 22
microns as per the specifications and drawings. Quoted
price shall be inclusive of Low VOC adhesive as required,
aluminium tape straps. Insulation shall be covered necessary
glass cloth & UV protection paint.
a. | 25mm thick insulation | SqM | - |  |  | Rate Only
b. | 50mm thick insulation | SqM | 15 |  | 0
3.3 | THERMAL INSULATION OF DUCTS - Air Washer
(Using aluminium foil faced Class 'O' Fire Retardant Properties Closed Cell Elastomeric insulation)
Supply and Application of external thermal insulation of supply /return air ducting using factory laminated aluminium foil faced closed cell elastomeric nitrile rubber insulation with class 'O' fire retardant properties as per the specifications and drawings. aluminium foil face shall provide protection from mechanical impact, and Scratches etc. Both insulation & aluminium foil layer should have built in antimicrobial protection. Expose insulation shall be covered with necessary glass cloth & UV protection paint. Adhesive - AC Duct King Eco Fresh
a. | 25mm thick insulation - For AC Duct in Kitchen | SqM | 135 |  | 0
TOTAL (AIR DISTRIBUTION) Rs. | TOTAL ITEM NO. 4 (INSULATION) |  |  | Rs. | 0
4 | ELECTRICAL WORKS
4.1 | Panels
Supply,Installation,Testing and Commissioning of the following cubical type panels made out of 14 guage CRCA structure, base channel, complete with, moulded case circuit breakers, meters, indicating lamps, current transformer etc. Complete in all respects, insulated bus bars with heat shrinkable PVC sleeve in suitable bus chambers , interconnection, small wiring, name plate, danger plate, earth bus etc. & comprising of compartments with hinged door for each feeder & its accessories, cable alley with hinged doors, bus chamber with bolted door etc. The panel being of dust & vermin proof construction with rubber gasket attractively powder coating etc. The panel shall be free standing type / wall mounted type as per relavant drawing and comprising with the following:
Notes :
1. All MCCBs shall be with operating handle.
2. CTs burden shall be 15VA & accuracy class 1.0
3. CTs shall be cast resin type .
4. All MCCBs shall be with thermal magnetic
release.
5. All indication lights shall be LED type.
6. All meter shall be digital type.
7. The outgoing starter feeders for pumps,AHUS
& ventilation fans shall be provided
with push buttons & indicating lamps for
status indication.
8. Proper isolation switches to be
provided near air handling units and
ventilation fans in weather proof enclosure.
9. Bimetal overload relay for all the
starters shall have built-in single
phasing prevention feature.
10. Electrical interlocking wiring shall be
provided as per system requirement.
11. Power cabling/wiring with necessary
earthing from source to each panel
and each exhaust fan shall be
provided by other agencies.
12. All HVAC equipment shall be compatible with
BMS and necessary provisions to be made
in each panel.
4.1.1 | KVF PANEL -1 (Location : Kitchen ) - 13.8KW
| For 9700Cfm Air Washers & Pump, 12100Cfm SISW Fan & ESP | No | 1 |  | 0
Incoming :
63 Amps ,TP MCCB with electronic release &
earth fault relay, door interlock and front drive
rotor kit-- 1set
(0-500) V digital Voltmeter with built in Selector
switch -- 1set
Digital Ammeter with built in selector
switch- 1set
Current Transformers - 1set
LED type RYB phase indication lights- 1set
Busbar
100 Amps TPN aluminium busbar having
suitable fault level, with PVC heat shrunk
sleeves on SMC/DMC supports.
Outgoings :
a. | For Air Washers - (1x11.0KW)
40 Amps ,TP MCCB -- 1 set
Digital Ammeter with built in selector
switch- 1 set
Current Transformers -- 1 set
LED type ON & OFF indication lights -- 1 set
START-STOP Push Buttons -- 1 set
15.0HP Star Delta starter with built-in single phasing
preventor & overload relay & adjustable timer-- 1 set
Auto-Manual type selector switch
to facilitate auto start of unit
after restoration of power -- 1 set
Control wiring and safety circuit as required
with start-stop push buttons stay put or
lockable type -1 set
b. | For Air Scrubber - (1x15KW)
40 Amps ,TP MCCB -- 1 set
Digital Ammeter with built in selector
switch- 1 set
Current Transformers -- 1 set
LED type ON & OFF indication lights -- 1 set
START-STOP Push Buttons -- 1 set
20HP Star Delta starter with built-in single phasing
preventor & overload relay & adjustable timer-- 1 set
Auto-Manual type selector switch
to facilitate auto start of unit
after restoration of power -- 1 set
Contactors, Potential Free Contacts, Control wiring and
safety circuit as requiredwith start-stop push buttons stay
put or lockable type - 1 set
c. | For Pump of Air washer (1x1.0HP) -single phase
20 Amps ,TP MCB -- 1 set
LED type ON & OFF indication lights -- 1 set
START-STOP Push Buttons -- 1 set
Auto-Manual type selector switch-- 1 set
Contactors, Potential Free Contacts, Control wiring and
safety circuit as requiredwith start-stop push buttons stay
put or lockable type - 1 set
d. | For Pump of Air Scrubber (1x1.0HP) -single phase
20 Amps ,TP MCB -- 1 set
LED type ON & OFF indication lights -- 1 set
START-STOP Push Buttons -- 1 set
Auto-Manual type selector switch-- 1 set
Contactors, Potential Free Contacts, Control wiring and
safety circuit as requiredwith start-stop push buttons stay
put or lockable type - 1 set
4.2 | CABLING
4.2.1 | Supply, laying, affecting connections and
Testing of the following sizes of 1.1 KV
armoured PVC insulated aluminium/ copper
conductor cables. Cables shall be inclusive of
all clamps, saddles, screws, cable identification
tags, cable terminal joints including terminal
lugs, insulating tapes, affecting terminal
connections to the equipment as per the
specifications and as required. Quoted price
shall be inclusive of perforated duly painted
2mm thick MS trays to be installed inside and
GI trays to be installed outside exposed and
8SWG copper earth wire for all equipment.
All power cables shall be FRLS type.
a. | 3 C x 16 Sqmm cable (Copper) | RM | -- |  |  | Rate Only
b. | 3 C x 10 Sqmm cable (Copper) | RM | 10 |  | 0
c. | 3 C x 6 Sqmm cable (Copper) | RM | 20 |  | 0
d. | 3 C x 4 Sqmm cable (Copper) | RM | -- |  |  | Rate Only
e. | 3 C x 2.5 Sqmm cable (Copper) | RM | 5 |  | 0
f. | 3 C x 2.5 Sqmm cable( Copper Control cabling) | RM | 5 |  | 0
g. | 3 C x 1.5 Sqmm cable(Copper Control cabling) | RM | 10 |  | 0
h. | 4 C x 1.5 Sqmm cable( Copper Control cabling) | RM | - |  |  | Rate Only
4.3 | Supply and fixing of 1.1 KV grade rubber
mat 914.4 mm wide 6mm thick to withstand
1.1 KV dielectric strength in front of
| each panel. | RM | 2 |  | 0
4.4 | Supply, Installation & Testing of TPN
isolator in weather proof enclosure near
| Fans. | No | 2 |  | 0
| TOTAL ITEM NO. 4 (ELECTRICAL) |  |  | Rs. | 0
|  |  |  | TOTAL | 0

## MAKES
PLUMBING
S No. | Item | Make
1 | Vitreous China Sanitaryware | As Approved
2 | C.P. Brass fittings | Jaquar/Hindware/ as approved
3 | Cast iron pipes & fittings, Manhole covers and frames. | NECO/RIF
4 | G.I. pipes. | Tata/Jindal Hissar/Prakash Surya
5 | G.I. pipes fittings. | K.S. / Unik / `R’ Brand
6 | R.C.C pipe | K.K. / App. Equivalent ISI marked
7 | Stoneware pipes, Gully traps | Perfect potteries, Jabalpur / Approved equivalent ISI marked
8 | Valves | Zoloto / Leader/ C & R / Advance
9 | Paints | Asian Paints / Shalimar Paints /Berger
10 | Pressure Gauge | H Guru/Fiebig
11 | Pumps | Grundfoss/ITT/Kirloskar/KSB
12 | Level Controller & Indicator (Water) | Advance Auto/Technika / Minilec
13 | PVC Pipes | Supreme / Prince/Astral
14 | Urinal Sensor | UTEC System/Jaquar/Hindware
15 | Geyser | Venus/Racold/AO Smith
16 | Sink | Neelkanth/Kobra/Hindware
17 | Water purifier | Eureka Forbes/Kent
18 | HDPE Water tanks | Sintex/Frontier
19 | CPVC Pipes | Aashirwad/Finolex/Astral
20 | Gratings,Cleanouts,Funnels | GMGR/Neer/Jayna
ELECTRICAL
S No. | Item | Make
1 | Conduits | Precision/ AKG/ BEC
2 | FRLS Wires | Finolex / Havells/ KEI/ Polycab
3 | Cables | Polycab/ Havells/ Finolex
4 | Switches | Legrand /Roma / Clipsal/ Opale/ Crabtree/ Northwest
5 | Distribution Boards | Siemens/ MDS/ legrand / L&T
6 | MCB’s /ELCB’s | Siemens/ MDS/ legrand / L&T
7 | Telephone/Speaker Wires | Finolex/ Polycab/ Falcon
8 | T.V.Wires | Comscop/ Finolex
11 | Switch Fuse Units/ Starters | L&T/ Siemens
12 | Fire Alarm System | Apollo/ System Sensor/ Agni/ Honeywell/ Ravel
13 | Data Cable / IO | Amp (TE)/ D Link
14 | Light Fittings | Havells/Wipro/Philips
Notes:-
[1] The Contractor should quote the tender rates considering First make of materials given in above list.
[2] Wherever contractor proposes to use `equivalent' makes (i.e. other than specified) he shall obtain Client's prior approval. Client may consult Consultants before giving approval to the same. Any additional cost and time lost due to this will be on Contractor's account and no claims will be entertained.
[3] The contractor should take approval for make & manufacturer from the TFS before using any material, which does not appear in the list of approved manufacturers.
FIRE FIGHTING
S No. | Item | Make
1 | G.I./M.S pipes. | Tata/Jindal Hissar/Prakash Surya
2 | MS Forged fittings. | VS/KS
3 | Valves | Zoloto / Leader/ C & R / Advance
4 | `Y' strainer | Emerald Enterprises / Zoloto/Kartar
5 | Level Controller & Indicator (Water) | Advance Auto/Technika / Minilec
6 | Paints | Asian Paints / Shalimar Paints /Berger
7 | Pressure Gauge | H Guru/Fiebig
8 | Flexible Rubber Expansion Joint | Kanwal Easyflex/Resistoflex
9 | Pumps | Kirloskar/Mather & Platt /KSB
10 | Fire Fighting Equipments | Minimax/Safeguard/Getech
11 | Sprinklers | Tyco/Grinnel/Best/HD
12 | Welding Rods | Advani/Victor
13 | GI Hangers | Chilly/GMGR