## TechItemDoc
ItemCode | Item Name | UOM | Qty | Unit Price | Remarks
The main fire fighting sprinkler riser pipe including floor isolation valve, flow indicating switch, inspectors-test-cum-drain assembly and drain pipe in vertical shafts have already been installed by the main builder. The interior contractor needs to make connections, alteration to existing main network only. All works to be done after seeking permission from building manitenance agency.
4.1 | Providing, fixing, jointing and testing of (Class-C/Heavy duty) MS Pipe IS:1239 / 3589 marked, with accessories like tees, elbows, flanged joints, reducers, compressed asbestos gaskets, nuts and bolts including using modular pipe support. complete as required for delivery/suction manifold relating to the pumps including painting of two coats of Red Oxide including all civil breakages and making good the same. The rate includes the cost of installing DI threaded fittings UL listed & FM approved for pipe sizes upto 50mm dia and welded joint abov jointing pipe sizes above 50mm dia. All work is to be carried out as per the specifications (Make : HSL, Mukut, Lalit steel )
The support channel should be made up of cold rolled steel of quality DX51 or greater. The Support channel should be pre-galvanised with minimum GSM of 275 and should have universal mounting slot on the front of the rail for accurate positioning of fasteners and system compatible round and long holes on back of the rail the pipe.
The pipe clamps should be split type with EPDM inner rubber lining, FM/UL approved.
Threaded rod should be of 4.8 stregth class and necessary accessories should be of 8.8 strength class.
a. DI Threaded Fittings for pipe size upto 50mm dia:
b. Welded joint above 50mm diameter pipe.
4.1.1 | 25 mm nominal bore | Metre | 55
4.1.2 | 32 mm nominal bore | Metre | 5
4.1.3 | 40 mm nominal bore | Metre | 10
4.1.4 | 50 mm nominal bore | Metre | 15
4.1.5 | 65 mm nominal bore | Metre | 15
4.2 | Providing and fixing 15 mm dia gunmetal quick response sprinkler head with quartz bulb and set to operate at specified temperature. Sprinkler head shall carry UL-FM approval (Make Ansul, Buckeye, Smog Hog, Gem-Tyco, )
Temperature of operation 68 deg.C.
4.2.1 | Chrome plated pendent type with powder coated twin rosette plate. | Each | 10
4.2.2 | Upright type sprinkler head | Each | 10
4.3 | Providing and fixing 25 mm dia, UL-FM approval flexible stainless steel (SS 304) pipe for making final connection of sprinkler head with sprinkler system piping network including 2 nos. 25mm diameter G.I. connector, G.I. Nipple, Reducer, elbow and threaded jointing complete as per detail. (Make Ansul, Buckeye, Smog Hog, Gem-Tyco, )
4.3.1 | 1000mm long | Each | 5
4.3.1 | 1500mm long | Each | 5
4.4 | Dismantling and refixing of existing MS pipes including all works like welding, support fixing, painting, testing complete in all respects.
4.4.1 | 25 mm nominal bore | Metre | 5
4.4.2 | 32 mm nominal bore | Metre | 5
4.4.3 | 40 mm nominal bore | Metre | 5
4.4.4 | 50 mm nominal bore | Metre | 5
4.5 | Making connection with existing main header including butterfly valve, flanges and accessories required.[Make: ZOLOTO / SANT / DRP]
4.5.1 | 65 mm nominal bore | Each | 1
4.6 | Providing and fixing brass ball valve with SS 304 Stem and ball, teflon seat complete (PN-16).[Make: ZOLOTO / SANT / DRP]
4.6.1 | 25 mm dia nominal bore | Each | 1
TOTAL FOR S. IV CARRIED OVER TO SUMMARY