## F-F-026_HVAC BOQ
BILL OF QUANTITIES AND ESTIMATE
PROJECT: | F-F-026_CHAI POINT_HYDERABAD AIRPORT |  |  | DATE: | 22.03.2024
|  |  |  | REV: | R0
HVAC SERVICES - WORKS BILL OF QUANTITIES AND ESTIMATE |  |  |  | STATUS: | TENDER
GENERAL NOTES :
All measurements and figures provided below are indicative and must be confirmed by the contractor. The contractor shall have full responsibility for measurements or surveys, and no additional costs or charges will be accepted. The scope of work and quantities mentioned in the MEP BOQ pertain to the MEP services only inside the site location (e.g., within the unit demise). If any termination or connection of services is required outside the site location (i.e., connection of the unit M&E to the airport M&E or service termination to the airport external façade or roof, etc.), then the contractor has to plan, design, and detail these connections in consultation with the airport. The contractor is to do all necessary site surveys to verify the optimal routing for the services in such cases. Any service penetration inside the unit has to be made good after installation, and any fire penetrations on site have to be detailed as per Airport requirements. The contractor is to verify at site and also with Airport authorities whether there are provisions at site to suit the design. Example: The contractor should check for provisions and the extent of power, plumbing, chilled water, ducting, fire and gas provisions etc. available at the site and satisfy himself that there are no risks to the design intent.
ITEM CODE | ITEM NAME | UOM | QTY | UNIT COST | REMARKS
A | HVAC SYSTEM EQUIPMENTS
KITCHEN EQUIPMENTS
A.1 | Supply, installation, testing, commissioning and field performance of ceiling suspended Kitchen Exhaust Fan with all necessary supports and fittings.
A.1.1 | 1200 CFM | Nos | 1
A.2 | Supply, installation, testing, commissioning and field performance of ceiling suspended Electrostatic Precipitator (for removal of Kitchen Grease and Smoke particles) with all necessary supports and fittings.
A.2.1 | 1200 CFM | Nos | 1
A.3 | Supply, installation, testing, commissioning and field performance of ceiling suspended Air Washer Unit with all necessary supports and fittings.
A.3.1 | 1200 CFM | Nos | 1
B | AC PIPING
HVAC CONDENSATE DRAIN PIPE
B.1 | Supply and fixing in position of Rigid PVC condensate drain water piping with necessary supports and fittings like, U-traps, elbows, tees and reducers insulated with 9mm nitrile rubber and BOPP tape.
B.1.1 | 25 mm Ø | Mtr | 6
C | AIR DISTRIBUTION DUCTS
RECTANGULAR DUCTS
C.1 | Supply, installation and testing of Galvanized Steel / Galvanized Iron, factory fabricated square / rectangular ducts, complete with TDF flanges and bracing necessary supports using thread roads and anchor bolts, supply air collars, vanes, splitters dampers. The ducts shall be fabricated and installed in line with SMACNA standards. (for Supply Air Duct)
C.1.1 | 24 Gauge (for low pressure duct with duct size larger side 0 - 1000 mm) | Sq.mtr | 18
C.2 | Supply, installation and testing of Galvanized Steel / Galvanized Iron, factory fabricated square / rectangular ducts, complete with TDF flanges and bracing necessary supports using thread roads and anchor bolts, supply air collars, vanes, splitters dampers. The ducts shall be fabricated and installed in line with SMACNA standards. (for Make-up Air Duct)
C.2.1 | 24 Gauge (for low pressure duct with duct size larger side 1001 - 1200 mm) | Sq.mtr | 12
C.3 | Supply, installation and testing of Mild Steel / Black Steel, factory fabricated square/rectangular ducts, complete with MS flanges and bracing necessary supports using thread roads and anchor bolts, collar risers fully welded construction, duct and all other accessories shall be fire resistant. The ducts shall be fabricated and installed in line with SMACNA standards. (for Kitchen Exhaust Air Duct)
C.3.1 | 20 Gauge | Sq.mtr
D | AIR DISTRIBUTION DUCT INSULATION & LINNING
D.1 | Supply, installation & testing of Thermal Insulation of ducting using closed-cell elastomeric nitrile rubber, Black Colour with silver foil covering, Thermal Conductivity λ - 0.036 W/(m-K) at 0° C and Fire performance according to building regulations - Class "O" as per BS 476 with necessary adhesives.
D.1.1 | 19 mm thicknesses | Sq.mtr | 30
D.2 | Supply, installation & testing of Thermal Insulation of ducting using glass wool with silver foil covering, density 40 Kg/m3, Thermal Conductivity λ - 0.030 W/(m-K) at 0° C and Fire performance according to building regulations - Class "O" as per BS 476.
D.2.1 | 80 mm thicknesses | Sq.mtr
E | AIR DISTRIBUTION DUCT ACCESSORIES
E.1 | Supply, installation, testing and commissioning of Extruded Aluminium Low Leakage square / rectangular Volume Control Damper with aero-foil opposed blades and nylon gears system outside air stream with adjustable handle with position arresting bolt.
E.1.1 | Size - 150 x 150 mm | Nos | 2
E.2 | Supply, installation, testing and commissioning of Extruded Aluminium Opposed Blade Damper / Collar Damper with Nylon gears and lever on face side for smooth operation.
E.2.1 | Size - 150 x 150 mm | Nos | 2
E.2.2 | Size - 350 x 350 mm | Nos
F | AIR TERMINALS - (GRILLES, REGISTERS, DIFFUSERS & LOUVERS)
F.1 | Supply, installation, testing and commissioning of Extruded Aluminium Rectangle Grille with fixed Aero foil Blades, with 30° deflection - 2 Way with rigid frame of 16mm flange as standard.
F.1.1 | Neck Size - 600 x 150 mm | Nos | 4
F.2 | Supply, installation, testing and commissioning of Extruded Aluminium Linear Slot Diffuser with vertical deflections blades to adjust direction of air flow with 25 mm slot opening.
F.2.1 | 3 Slot with OBD x Length - 1000 mm (For Supply Air) | Nos | 0
G | TESTING & COMMISIONING
G.1 | Air Balancing & Chilled Water Testing & Commissioning | Lot | 1
GRANT TOTAL NET
NOTE: The quantities mentioned in the above BOQ includes services only inside the site location (building). If any termination of services required outside the site location contractor to verify at site and provide the quantity and cost over and above this BOQ. Any service penetration to be made good after installation. Fire sealing to be done for penetrations as per Airport requirement.

## F-F-026_FIRE BOQ
BILL OF QUANTITIES AND ESTIMATE
PROJECT: | F-F-026_CHAI POINT_HYDERABAD AIRPORT |  |  | DATE: | 22.03.2024
|  |  |  | REV: | R0
FIRE SERVICES - WORKS BILL OF QUANTITIES AND ESTIMATE |  |  |  | STATUS: | TENDER
GENERAL NOTES :
All measurements and figures provided below are indicative and must be confirmed by the contractor. The contractor shall have full responsibility for measurements or surveys, and no additional costs or charges will be accepted. The scope of work and quantities mentioned in the MEP BOQ pertain to the MEP services only inside the site location (e.g., within the unit demise). If any termination or connection of services is required outside the site location (i.e., connection of the unit M&E to the airport M&E or service termination to the airport external façade or roof, etc.), then the contractor has to plan, design, and detail these connections in consultation with the airport. The contractor is to do all necessary site surveys to verify the optimal routing for the services in such cases. Any service penetration inside the unit has to be made good after installation, and any fire penetrations on site have to be detailed as per Airport requirements. The contractor is to verify at site and also with Airport authorities whether there are provisions at site to suit the design. Example: The contractor should check for provisions and the extent of power, plumbing, chilled water, ducting, fire and gas provisions etc. available at the site and satisfy himself that there are no risks to the design intent.
ITEM CODE | ITEM NAME | UOM | QTY | UNIT COST | REMARKS
A | FIRE SPRINKLER SYSTEM
AUTOMATIC FIRE SPRINKLER HEADS & ACCESSORIES
A.1 | Supply, Installation, Testing & Commissioning of Automatic Concealed Fire Sprinkler Heads (Bulb type Sprinklers) with adjustable Escutcheon plates (Rosette plates). Standard Temperature Response with 5mm glass bulb, Temperature rating of 68° C, K-factor of 80, Nominal Thread size of 1/2" NPT (15mm) and a Orifice size of 13mm with a Max. Working Pressure of 12 Bar (Factory hydrostatic test pressure of 35 Bar) and to be Manufactured & Certified to UL 199. Shall also include suspending arrangement with ceiling / wall etc.
A.1.1 | Pendant type of 68° C (Finishing - Chrome Plated) | Nos | 3
A.1.2 | Pendant type of 79° C (Finishing - Chrome Plated) | Nos | 3
FIRE SPRINKLER PIPE VALVES & ACCESSORIES
A.3 | Supply, Installation, Testing & Commissioning of Cast Iron Butterfly Valve slim seal PN16 (working pressure of 16 Bar), standard flow control lever operated with stainless steel shaft & disc, seat material with Black Nitrile / EPDM, flanges nuts and bots etc.
A.3.1 | 65 mm Dia | Nos | 1
A.4 | Supply, Installation, Testing & Commissioning of Brass body Test And Drain Valve with Sight Glass, working pressure of 20 Bar (300 PSI), standard lever operated with stainless steel stem & lever, with necessary weldable fittings in position as per drawings / site conditions.
A.4.1 | 25 mm Dia | Nos | 1
A.5 | Supply, Installation, Testing & Commissioning of Flow Switch on Sprinkler distribution header pipe with a working pressure of 31 Bar (450 PSI) and a flow sensitivity range of 4-10 GPM (15 - 38 LPM) on each floor / zone / inside proposed demise area tap of point, shall be connected to fire alarm panel through cable.
A.5.1 | 65 mm Dia | Nos | 1
FIRE SPRINKLER PIPING
A.6 | Supply, Installation, Testing & Commissioning of GI "C" Class Fire Sprinkler Pipe confirming to IS: 1239 with all fittings like bends, tees, flanges, nut, bolt and washers etc., and proper pipe supports to not more than 3 meter apart of the pipe length. The pipe work shall be hydrostatically tested for not less than 2 hours at 15 Bar (or 1.5 times the working) pressure without leak. The pipes are to be applied with 2 coats of primer (indicated film thickness, dry 50 microns) and 2 coats of enamel finish paint of approved Colour (indicated film thickness, dry 30 microns)
A.6.1 | 25 mm Dia | Mtr | 3
A.6.2 | 40 mm Dia | Mtr | 3
A.6.3 | 50 mm Dia | Mtr | 2
B | FIRE ALARM SYSTEM ( ADDRESSABLE TYPE )
FIRE ALARM SYSTEM - DETECTION DEVICES
B.1 | Supply, Installation, Testing, and Commissioning of Addressable Type (Optical Smoke & Heat) Smoke Detector Conforming to EN54, with standard detector mounting base, IP30 Ingress Protection, Area Coverage of 50 sq. mm (subject to local standard), 360° Angle Visibility, Operating Temperature (-10°C to +50°C), approved by LPCB, of approved make with all necessary mounting and fixing arrangements.(Above & Below Ceiling)
B.1.1 | Below ceiling level | Nos | 3
B.2 | Supply, Installation, Testing, and Commissioning of Addressable Type Fixed Temperature Heat Detector Conforming to EN54, with standard detector mounting base, IP30 Ingress Protection, Area Coverage of 50 sq. mm (subject to local standard), 360° Angle Visibility, Operating Temperature (-10°C to +50°C), approved by LPCB, of approved make with all necessary mounting and fixing arrangements.
B.2.1 | Heat Detector - 58°C fixed temperature | Nos | 3
B.3 | Supply, Installation, Testing, and Commissioning of Addressable Type Manual Call Point Conforming to EN54 with Break glass, ABS material enclosure, IP30 Ingress Protection, Operating Temperature (-10°C to +50°C) of approved make suitable for flush and surface mounting with all necessary mounting, termination and fixing arrangements.
B.3.1 | Manual Call Point - (Wall / Partition Mounted) | Nos | 1
B.4 | Supply, Installation, Testing and commissioning of Addressable type Sounder Strobe with inbuilt Isolator & operating temp (- 10 degree to + 55 degree ) complete as required and duly approved by LPCB / EN54.
B.4.1 | Sounder Strobe - (Wall / Partition Mounted) | Nos | 1
FIRE ALARM SYSTEM - MODULE DEVICES
B.5 | Supply, Installation, Testing, and Commissioning of Addressable Type Monitor Module
B.5.1 | Monitor Module | Nos | 3
B.6 | Supply, Installation, Testing, and Commissioning of Addressable Type Control Module for shutting down FCU’s, and magnetic fire door holders. Elevator recall, fire damper, pressurization fan, strobes etc.
B.6.1 | Control Module | Nos | 1
B.7 | Supply, Installation, Testing, and Commissioning of Addressable Type Isolation Module
B.7.1 | Isolation Module | Nos | 1
FIRE ALARM SYSTEM - CABLING
B.8 | Supply and surface laying of Armoured FRLS twisted pair, shielded cable.
B.8.1 | 2 core 1.5 Sqmm | Mtr | 75
B.9 | Supplying, installing, testing and commissioning approved make PVC conduits on ceiling / wall / floor etc. complete with accessories like, Junction boxes, Collars, Bends etc.
B.9.1 | 20 mm Dia | Mtr | 75
FIRE EXTINGUISHERS
C.1 | DRY POWDER STORED FIRE EXTINGUISHER
C.1.1 | Supply and fixing of 4.0 Kg ABC Dry Powder (Stored Pressure) Type Fire Extinguisher. pressurized with dry nitrogen gas at 15 bar. Design, construction and testing as per IS 15683 with BIS Fire rating 2A : 21B, Body Hydrotested at 35 bar, Operating temperature -30°C to +55°C, external epoxy powder coating with PO Red Shade No. 538 of IS 5, Supplied with standard accessories. | Nos | 2
C.2 | CO2 PORTABLE FIRE EXTINGUISHER
C.2.1 | Supply and fixing of 3.0 Kg CO2 (Carbon-dioxide) Type Fire Extinguisher. Design, construction and testing as per IS 15683 with BIS Fire rating 21B, Body Hydrotested at 250 bar, Operating temperature -30°C to +55°C, external epoxy powder coating with PO Red Shade No. 538 of IS 5, Supplied with standard accessories. | Nos | 2
C.6 | FIRE EXTINGUISHER MOUNTING BRACKET / MOUNTING STAND
C.6.1 | Supply and fixing of Mounting Bracket / Stand for Fire Extinguishers fabricated out of good quality M.S, Pipe / Plate & Fittings duly painted with primer and final enamel paint coat as per the regulatory authority or to match with the ID design to suit the above Fire Extinguishers. | Nos | 4
GRANT TOTAL
NOTE: The quantities mentioned in the above BOQ includes services only inside the site location (building). If any termination of services required outside the site location contractor to verify at site and provide the quantity and cost over and above this BOQ. Any service penetration to be made good after installation. Fire sealing to be done for penetrations as per Airport requirement.