## BOQ Price Bid
Sr No. | Item Code | Item Name | Item Description | UOM | Qty | Unit Price | Amount
1 |  | HVAC-High Side | HVAC-High Side
1 |  | Note | Note
2 |  | Prices shall be based on supply, installation, testing commissioning (SITC) at site including all taxes, duties, transportation insurance etc. | Prices shall be based on supply, installation, testing commissioning (SITC) at site including all taxes, duties, transportation insurance etc.
3 | 1 | CHILLED WATER TYPE CEILING SUSPENDED AHU (AIR HANDLING UNIT) | CHILLED WATER TYPE CEILING SUSPENDED AHU (AIR HANDLING UNIT)
4 | 1.1 | CEILING SUSPENDED AHU | CEILING SUSPENDED AHU
5 |  | Supply and assembly of Ceiling Suspended Double skin cabinet type AHU Integrated (Air handling units) of following specifications | Supply and assembly of Ceiling Suspended Double skin cabinet type AHU Integrated (Air handling units) of following specifications
6 |  | Frame Structure It shall consist of 48mm Extruded Aluminium with thermal break profile. | Frame Structure It shall consist of 48mm Extruded Aluminium with thermal break profile.
7 |  | Panel 45mm + - 2mm thick double skin sandwich panels with rockwool insulation of density 64 kg m3 or PUF insulation of 48 kg m3 , The sheet thickness shall be minimum 0.6 mm for the outer skin precoated and 0.8 mm thickness for the inner skin of plain GI. | Panel 45mm + - 2mm thick double skin sandwich panels with rockwool insulation of density 64 kg m3 or PUF insulation of 48 kg m3 , The sheet thickness shall be minimum 0.6 mm for the outer skin precoated and 0.8 mm thickness for the inner skin of plain GI.
8 |  | Mixing Box shall be provided wherever specified in the drawing. | Mixing Box shall be provided wherever specified in the drawing.
9 |  | Filtration Section It shall be provided with single stage washable type of prefilter MERV 8 first stage which shall be placed before coil section. | Filtration Section It shall be provided with single stage washable type of prefilter MERV 8 first stage which shall be placed before coil section.
10 |  | Coil Section Chilled water coil Multi row deep constructed with Aluminium fins of min 0.11mm thick 12 Fins per inch, and copper tubes of min 27 Guage thickness HYRDOPHYLLIC coated fins. Copper tube shall be min 12.5mm diameter. AHRI certified coil.The coil face area velocity shall not exceed 2.5m sec (500 fpm). | Coil Section Chilled water coil Multi row deep constructed with Aluminium fins of min 0.11mm thick 12 Fins per inch, and copper tubes of min 27 Guage thickness HYRDOPHYLLIC coated fins. Copper tube shall be min 12.5mm diameter. AHRI certified coil.The coil face area velocity shall not exceed 2.5m sec (500 fpm).
11 |  | Drain Pan Condensate drain pan shall be fabricated from 18G SS 304 powder coated, insulated with 13 mm thick closed cell elastomeric(nitrile rubber) insulation. | Drain Pan Condensate drain pan shall be fabricated from 18G SS 304 powder coated, insulated with 13 mm thick closed cell elastomeric(nitrile rubber) insulation.
12 |  | Fan Section SISW DIDW Direct drive backward curved fan. The fan section shall be provided with limt switch for safety to shut off fan during Opening of access door. Fan outlet velocity not to exceed 1600 FPM. The sound level shall not be exceed more than 60dB @ 1m from the source. Vibration isolators, Door Limit switch, UV Lamp as per Technical Specifications, AHU Summary Sheet and drawings. Total static pressue has to calculated by Contractor as per the configuration. | Fan Section SISW DIDW Direct drive backward curved fan. The fan section shall be provided with limt switch for safety to shut off fan during Opening of access door. Fan outlet velocity not to exceed 1600 FPM. The sound level shall not be exceed more than 60dB @ 1m from the source. Vibration isolators, Door Limit switch, UV Lamp as per Technical Specifications, AHU Summary Sheet and drawings. Total static pressue has to calculated by Contractor as per the configuration.
13 |  | Other Details AHU to house control box terminal box with Auto-Manual switch and incomer power terminal, with SPP, Over Undervoltage protection, shortcircuit protection and with no-nc contacts (potential free contact) to be provided for tripping on signal from Fire Dampers Fire Alarm Panel. Power cable from Terminal box to motor control cabling of required size upto the thermostat sensor etc. to be provided. Internal electrical and control wiring of AHU to be provided as factory fitted from AHU supplier. The cost shall include all necessary supports accessories required for installation. | Other Details AHU to house control box terminal box with Auto-Manual switch and incomer power terminal, with SPP, Over Undervoltage protection, shortcircuit protection and with no-nc contacts (potential free contact) to be provided for tripping on signal from Fire Dampers Fire Alarm Panel. Power cable from Terminal box to motor control cabling of required size upto the thermostat sensor etc. to be provided. Internal electrical and control wiring of AHU to be provided as factory fitted from AHU supplier. The cost shall include all necessary supports accessories required for installation.
14 |  | Contractor shall design the chilled water coil according to the following conditions | Contractor shall design the chilled water coil according to the following conditions
15 |  | a. Coil air entering temperature - 75.4°F DB | a. Coil air entering temperature - 75.4°F DB
16 |  | b. Coil air leaving temperature - 54 deg. F DB 52.99 deg. F WB | b. Coil air leaving temperature - 54 deg. F DB 52.99 deg. F WB
17 |  | c. Chilled water temperature entering - 7.0 deg. C 44.6 deg. F | c. Chilled water temperature entering - 7.0 deg. C 44.6 deg. F
18 |  | d. Chilled water temperature leaving - 12 deg. C 53.6 deg. F | d. Chilled water temperature leaving - 12 deg. C 53.6 deg. F
19 |  | Make VTS Zeco Citizen | Make VTS Zeco Citizen
20 |  | Type Capacity Tonnage ESP No. of | Type Capacity Tonnage ESP No. of
21 |  | (Cfm) TR (mm WG) Rows | (Cfm) TR (mm WG) Rows
22 |  | CS AHU 2000 4.2 25 4 6 | CS AHU 2000 4.2 25 4 6 | nos | 1 | 180000 | 180000
23 |  | GENERAL NOTES | GENERAL NOTES
24 |  | LHS RHS VALVE station location to be confirmed. | LHS RHS VALVE station location to be confirmed.
25 |  | Fan outlet velocity - 1600 FPM | Fan outlet velocity - 1600 FPM
26 |  | Contractor shall submit static pressure calculation for all above units to Client Consultant. | Contractor shall submit static pressure calculation for all above units to Client Consultant.
27 |  | Any change in motor HP shall be made at no extra cost to client. | Any change in motor HP shall be made at no extra cost to client.
28 |  | Fan efficiency shall be minimum 75% | Fan efficiency shall be minimum 75%
29 |  | The cost shall be included liftting shifting of each equipment material with all necesaary arrnagement. Also, it shall be included the cost of scaffloding required for Installation of such material equipment. | The cost shall be included liftting shifting of each equipment material with all necesaary arrnagement. Also, it shall be included the cost of scaffloding required for Installation of such material equipment.
30 |  | SUB-TOTAL | SUB-TOTAL
31 | 3 | VENTILATION SYSTEM | VENTILATION SYSTEM
32 | 3.1 | KITCHEN EXHAUST AIR FAN WITH WET SCRUBBER | KITCHEN EXHAUST AIR FAN WITH WET SCRUBBER
33 |  | SITC of Cabinet type Ventilation fan with Centrifugal Blower, Belt Direct Drive, Statically Dynamically Balanced, Backward Curved Impeller, Speed regulator, Dunlop Anti- Vibration Pads, etc. Motor should be TEFC squirrel cage, IP 55 rating with Class F Insulation, suitable for 3phase, 415volts, 50hz power supply. Sound level should be 65dB @ 3mtr distance. MERV 8 G4 pleated pre-filters should be made of 100% synthetic media to capture common airborne contaminants as per ASHRAE Standard 52.2. Fan shall be BMS compatible. Power will be provided 5 ft away from fan and necessary control wiring with plug will be provided by AC contractor.(Vendor to crosscheck static pressure calculation) | SITC of Cabinet type Ventilation fan with Centrifugal Blower, Belt Direct Drive, Statically Dynamically Balanced, Backward Curved Impeller, Speed regulator, Dunlop Anti- Vibration Pads, etc. Motor should be TEFC squirrel cage, IP 55 rating with Class F Insulation, suitable for 3phase, 415volts, 50hz power supply. Sound level should be 65dB @ 3mtr distance. MERV 8 G4 pleated pre-filters should be made of 100% synthetic media to capture common airborne contaminants as per ASHRAE Standard 52.2. Fan shall be BMS compatible. Power will be provided 5 ft away from fan and necessary control wiring with plug will be provided by AC contractor.(Vendor to crosscheck static pressure calculation)
34 |  | Make Kruger Nicotra Systems Air | Make Kruger Nicotra Systems Air
2 |  | HVAC-Low Side | HVAC-Low Side
47 | 2 | CHILLED WATER PIPING WITH INSULATION | CHILLED WATER PIPING WITH INSULATION
48 | 2.1 | CHW PIPE | CHW PIPE
49 |  | SITC of MS Heavy duty class C ERW Chilled Water pipe conforming to IS 1239 - 2004 primer painted including bends, tees, MS supports, PUFF saddles, anchor fasteners, steel angles and any other material required to complete the work. The piping flange connection bolts, washers and nuts should be hot dipped galvanised. Flourscent Plastic Sticker paint shall be applied to indicate Water flow directions. Only End flanges to be used for capping of pipes. Table E of BS code for flange thickness to be adhered. | SITC of MS Heavy duty class C ERW Chilled Water pipe conforming to IS 1239 - 2004 primer painted including bends, tees, MS supports, PUFF saddles, anchor fasteners, steel angles and any other material required to complete the work. The piping flange connection bolts, washers and nuts should be hot dipped galvanised. Flourscent Plastic Sticker paint shall be applied to indicate Water flow directions. Only End flanges to be used for capping of pipes. Table E of BS code for flange thickness to be adhered.
50 |  | Make Jindal Hissar TATA | Make Jindal Hissar TATA
154 |  | Suply and instalaltion of starter panel for AHU and Fan as per machine specification | Suply and instalaltion of starter panel for AHU and Fan as per machine specification | nos | 3 | 19000 | 57000
|  | Suply and installtion of 32mm dia Balance valve as per airport specification | Suply and installtion of 32mm dia Balance valve as per airport specification | nos | 1 | 9500 | 9500