## HVAC
Sr No. | Item Code | Item Description | UOM | Extra Qty | rates | amount
1 |  | High Side - HVAC
1 | Note: | Prices shall be based on supply, installation, testing commissioning (SITC) at site including all taxes, duties, transportation insurance etc.
2 | 1 | CHILLED WATER TYPE CEILING SUSPENDED AHU (AIR HANDLING UNIT)
3 | 1.1 | CEILING SUSPENDED AHU
4 |  | Supply and assembly of Ceiling Suspended Double skin cabinet type AHU Integrated (Air handling units) of following specifications
5 |  | Frame Structure It shall consist of 48mm Extruded Aluminium with thermal break profile.
6 |  | Panel 45mm + - 2mm thick double skin sandwich panels with rockwool insulation of density 64 kg m3 or PUF insulation of 48 kg m3 , The sheet thickness shall be minimum 0.6 mm for the outer skin precoated and 0.8 mm thickness for the inner skin of plain GI.
7 |  | Filtration Section It shall be provided with single stage washable type of prefilter MERV 8 first stage which shall be placed before coil section.
8 |  | Coil Section Chilled water coil Multi row deep constructed with Aluminium fins of min 0.11mm thick 12 Fins per inch, and copper tubes of min 27 Guage thickness HYRDOPHYLLIC coated fins. Copper tube shall be min 12.5mm diameter. AHRI certified coil.The coil face area velocity shall not exceed 2.5m sec (500 fpm).
9 |  | Drain Pan Condensate drain pan shall be fabricated from 18G SS 304 powder coated, insulated with 13 mm thick closed cell elastomeric(nitrile rubber) insulation.
10 |  | Fan Section SISW DIDW Direct drive backward curved fan. The fan section shall be provided with limt switch for safety to shut off fan during Opening of access door. Fan outlet velocity not to exceed 1600 FPM. The sound level shall not be exceed more than 60dB @ 1m from the source. Vibration isolators, Door Limit switch, as per Technical Specifications, AHU Summary Sheet and drawings. Total static pressue has to calculated by Contractor as per the configuration.
11 |  | Other Details AHU to house control box terminal box with Auto-Manual switch and incomer power terminal, with SPP, Over Undervoltage protection, shortcircuit protection and with no-nc contacts (potential free contact) to be provided for tripping on signal from Fire Dampers Fire Alarm Panel. Power cable from Terminal box to motor control cabling of required size upto the thermostat sensor etc. to be provided. Internal electrical and control wiring of AHU to be provided as factory fitted from AHU supplier. The cost shall include all necessary supports accessories required for installation.
12 |  | Contractor shall design the chilled water coil according to the following conditions
13 |  | a. Coil air entering temperature - 69.8°F DB
14 |  | b. Coil air leaving temperature - 54°F DB 52.99°F WB
15 |  | c. Chilled water temperature entering - 7.0°C 44.6°F
16 |  | d. Chilled water temperature leaving - 12.0°C 53.6°F
17 |  | e. Ambient temperature - DB - 110°F 43.3°C WB - 82°F 27.7°C
18 |  | Make VTS Zeco Citizen
19 |  | Type Capacity TR ESP No. of FA
20 |  | (Cfm) (mm WG) Rows CFM
|  | CS AHU 1800 4.0 25 4/6 | nos | 1 | 155000 | 155000
22 |  | GENERAL NOTES
23 | a. | LHS RHS VALVE station location to be confirmed.
24 | b. | Fan outlet velocity - 1600 FPM
25 | c. | Contractor shall submit static pressure calculation for all above units to Client Consultant.
26 | d. | Any change in motor HP shall be made at no extra cost to client.
27 | e. | Fan efficiency shall be minimum 75%
28 | f. | The cost shall be included liftting shifting of each equipment material with all necesaary arrnagement. Also, it shall be included the cost of scaffloding required for Installation of such material equipment.
2 |  | LOW Side
53 | 2 | CHILLED WATER PIPING
54 | 2.1 | CHW PIPE
55 |  | SITC of MS Heavy duty class C ERW Chilled Water pipe conforming to IS 1239 Part I class ‘C’ heavy and fitting shall be conforming to ASTM A-105,3000lbs socket weld end (up to 50mm) 1S 1239 Part-II HEAVY ASTM A-234 WPB, Gr.B butt weld fitting ( above 50NB pipe size). The cost also shall cover primer painted including bends, tees, MS supports, PUFF saddles, anchor fasteners, steel angles and any other material required to complete the work. The piping flange connection bolts, washers and nuts should be hot dipped galvanised. Flourscent Plastic Sticker paint shall be applied to indicate Water flow directions. Only End flanges to be used for capping of pipes. Table E of BS code for flange thickness to be adhered.
56 |  | Make Jindal Hissar TATA
58 | c | F 32 mm | Rmt | 40 | 950 | 38000
|  | F 50 mm | RMT | 40 | 1250 | 50000
60 | 2.2 | CHILLED WATER PIPING INSULATION - INTERNAL USE
61 |  | SITC of insulation for chilled water. piping. For internal pipe - Stick 25mm thick Nitrile rubber class O Closed cell nitrile rubber with anti-microbial coating on it. Insulation shall have Thermal conductivity of 0.033 W (m.K) and water vapor permeance of 0.10. Joints should be sealed with 50 mm wide 3 mm thick self adhesive tape and putting PVC bands at all supports. Further, insulation shall be wrapped with 7 mil cloth with required adhesive on it.
62 |  | Make Armaflex K-flex
64 | b | F 32 mm | Rmt | 40 | 415 | 16600
|  | F 50 mm | RMT | 40 | 650 | 26000
66 | 2.3 | BALL VALVE
67 |  | SITC of following sizes of Ball Valve consist of Cap, Brass Body, Rated for 150 psi SWP, 600 psi WOG Pressure Two-piece construction; with brass body, regular port, B-16 chrome-plated ball and stem, replaceable “Teflon” or “TFE” seats and seals, blowout-proof stem, vinyl covered steel handle, threaded or soldered ends and extended stem for insulated piping. Same valve shall be used as a Drain valve.
68 |  | Make Zoloto Audco Kitz
70 | b | F 32 mm | Nos. | 5 | 3050 | 15250
72 | 2.4 | BALL VALVE WITH Y-STRAINER
73 |  | SITC of following sizes of Brass Ball Valve with Y-Strainer consist of Cap, Brass Body, Rated for 150 psi SWP, 600 psi WOG Pressure Two-piece construction; with brass body, regular port, B-16 chrome-plated ball and stem, replaceable “Teflon” or “TFE” seats and seals, blowout-proof stem, vinyl covered steel handle, threaded or soldered ends and extended stem for insulated piping. Filter element shall be of non magnetic SS sheet with perforation.
74 |  | Make Zoloto Audco Kitz
76 | b | F 32 mm | Nos. | 1 | 3500 | 3500
78 | 2.5 | PIBCV VALVES
79 |  | SITC of Pressure Independent Balancing cum Control Valves (PIBCV) including integrated motorised control valve and balancing device for combined flow and water balancing requirement. Valve body to be rated for PN 16. The valve design flow rate should be factory calibrated with + - 5% flow accuracy. Valve shall have necessary measuring ports, drain port, flanges etc., Valve shall also provide temperature sensor with necessary cabling (min 2mtr length to be considered with each valve). The balancing to be done through microprocessor based hand held terminal POT and the same results shall be furnished in the water balancing report as part of commissioning report and handing over manual.
80 |  | Make Oventrop Siemens Danfoss
82 | b | F 32 mm | Nos. | 1 | 32500 | 32500
84 | 2.6 | Auto Air Vent Valves
85 |  | Make Anergy Flamco
86 |  | Providing and fitting Auto Vent Valves.
87 | a | SITC of Auto air vent in each risers common headers AHU. 3 4 auto vent valves at each coil riser header. | Nos. | 2 | 1250 | 2500
88 | 2.7 | SITC of Pressure gauges Thermometers
89 |  | Make H Guru Waree
90 |  | Necessary pressure gauges and thermometers 4 Dial type.
91 | a | Water Pressure gauges 150mm dial complete with gauge valves, mounting, fittings and copper tubing extension wherever required. Pressure gauges Range 0-10 Kg CM2 | Nos. | 2 | 1450 | 2900
92 | b | Thermometers of the mercury in glass stem type and copper separable well complete with guard etc., of industrial grade mounting on water lines. Length 9 12 inches, Thermometer, Range 0-50 deg C | Nos. | 2 | 1350 | 2700
93 | c | Thermowells | Nos. | 2 | 300 | 600