## TechItemDoc
ItemCode | Item Name | UOM | Qty | Unit Price | Remarks
A | INCOMER ISOLATOR / MCCB PANEL
A.1 | Supply, Installation, Testing & Commissioning of Incomer Isolator / MCCC Panel complete with Enclosure (If required as per site condition / Airport TDM). Make : Electrical Panel / DB's & Creakers (MCC, RCBO, ELCB & MCBC) : Legrand, ACC, Schneider, Siemens or equivalent.
A1.1 | 250A ISOLATOR / MCCB PANEL | Nos. | 1
B | METER / METER PANEL
B.1 | Supply, Installation, Testing & Commissioning of kWH / MFM Energy Meter Panel complete with Enclosure (If required as per site condition / Airport TDM). Make : Schneider, Secure, L & T or equivalent with Airport approval.
B.1.1 | 250A/5A ENERGY METER (CT TYPE) | Nos. | 1
C | LV CABLING
C.1 | Supply, Installation, Testing & Commissioning of Fire Rated LS/LSZH PVC insulated PVC sheathed, Copper conductor, Steel Tape / Wire Armoured, 1100V grade cable, Number of Cable Core as per SLD / Load Calculation Sheet (Main Cable) & Unarmoured Single Core Wire (ECC), complete with Termination of the same with Single Compression Crass Glands, Solderless Tinned Copper Lugs, Gland earthing, etc. The cable shall be laid Underground / on Cable Tray / through Cable Trunking / in Pipe / on Wall / Trench as required. Make : Electrical Wires & Cables: Polycab, KEI, RR, Havells, Gemco or equivalent. For cables laid on Cable Tray / in Pipe / on Wall / Trench - the rate shall include necessary supporting / clamping arrangements.
C.1.1 | 4C x 95 MM2 CABLE | Mtr. | 18
C.1.2 | 4C x 35 MM2 CABLE | Mtr. | 21
C.1.3 | 4C x 16 MM2 CABLE | Mtr. | 15
C.1.4 | 4C x 6 MM2 CABLE | Mtr. | 15
C.1.5 | 4C x 4 MM2 CABLE | Mtr. | 15
C.1.6 | 1C x 50 MM2 CABLE | Mtr. | 18
C.1.7 | 1C x 16 MM2 CABLE | Mtr. | 31
C.1.8 | 1C x 6 MM2 CABLE | Mtr. | 15
C.1.9 | 1C x 4 MM2 CABLE | Mtr. | 15
D | DISTRICUTION BOARDS
D.1 | Supply, Installation, Testing & Commissioning of Surface / Flush mounting 10kA / 25kA (As per Panel requirement) Distribution boards. The DB shall be made out of 1.2 mm CRCA sheet steel enclosure and powder coated complete with cable gland plate & knock out at the top and bottom. The DB shall have hinged lockable door. The busbar shall be tinned copper, for phases mounted on suitable type Insulator, Independent neutral busbar including interconnecting wiring & earth bus on insulation mount. Make : Electrical Panel / DB's & Creakers (MCC, RCBO, ELCB& MCCB) : Legrand, ACC, Schneider, Siemens or equivalent. All DB's must named as per the SLD / Load Calculation Sheet. Laminated SLD & Load Calculation Sheet shall be placed near to DB Panel Locations. The RCCB / RCBO shall Ce Hpi / Si series & MCB's shall Ce 'C" / 'B' Curve (As per requirement).
SMDB
D.1.1 | 10 Way TPN Panel Board with 250A TP MCCB incomer,and outgoings as per SLD & Load Calculation Sheet. | Nos. | 1
LPDB
D.1.2 | 16 Way TPN Panel Board with 125A 30mA 4P RCBO incomer,and outgoings as per SLD & Load Calculation Sheet. | Nos. | 1
UPS DB
D.1.3 | 4 Way SPN Panel Board with 20A 30 mA 2P RCBO incomer and outgoings as per SLD & Load Calculation Sheet. | Nos. | 1
E | LIGHT FIXTURES POINT WIRING
E.1 | Supply, Installation, Testing & Commissioning of Light Fixture Point wiring (Light Fixtures to be as approved by Architect Design & BOQ) with Lamps, Callasts / Drivers / Starters, Switches / Lighting Control Switch Board with Fire Rated LS/LSZH PVC insulated FlexiBle Copper Wires 660/1100V grade through suitable size GI Conduit / Heavy Duty PVC Conduit / GI Trunking (Containment size & Type selection as per site requirement), complete with suitable GI Cack boxes, Earthing, accessories, flexible conduits, glands, saddles, supports, ropes for future wire pulling, Labeling of wires etc. with Termination of the same with Solderless Tinned Copper Lugs, etc. carrying out Surface / Concealed wiring as per site condition & maintain aesthetic of the unit. Wiring shall be as per IS 732. Make : Light Fixtures : Philips, Wipro, Havells or equivalent. Make : AKG, CEC (ISI marker) or equivalent. Make : GI Conduits : Techno Flex India, K. M. Cables & Conduits or equivalent with Airport approval. The rate shall include wall chasing, chipping of floors, rough plastering, providing suitable supports / brackets for conduit and Trunking suspension.
E.1.1 | PENDANT LIGHT (Point Wiring only) | Nos. | 57
E.1.2 | CEILING SPOT LIGHT (Point Wiring only) | Nos. | 53
E.1.3 | 600x600mm LED PANEL LIGHT (Point Wiring only) | Nos. | 11
E.1.4 | WALL LIGHT (Point Wiring only) | Nos. | 18
E.1.5 | LED STRIP LIGHT (Point Wiring only) | RO | -
E.1.6 | SIGNAGE (Point Wiring only) | Nos. | 3
E.1.7 | EXIT LIGHT (Wall / Ceiling Mounted) | Nos. | 4
8 | LIGHTING CONTROL SWITCH COARD WITH SWITCHES AS REQUIRED (Point Wiring only) | Nos. | 2
F | WIRING DEVICES (SWITCHES & SOCKETS)
F.1 | Supply, Installation, Testing & Commissioning of Wiring Devices (Switches & Sockets - Face Plate Finish as approved By Architect / Matching to Architecture Finishes) with Fire Rated LS/LSZH PVC insulated Flexible Copper Wires 660/1100V grade through suitable size GI Conduit / Heavy Duty PVC Conduit / GI Trunking (Containment size & Type selection as per site requirement), complete with suitable GI back Boxes, Earthing, accessories, flexible conduits, glands, saddles, supports, ropes for future wire pulling, Labeling of wires etc. with Termination of the same with Solderless Tinned Copper Lugs, etc. carrying out Surface / Concealed wiring as per site condition & maintain aesthetic of the unit. Wiring shall be as per IS 732. Make : Switch & Sockets : Anchor Roma / Penta, Legrand, Havells CraCtree, Finolex, L & T Switchgear or equivalent with Airport approval. Make : PVC Conduits : AKG, CEC (ISI marker) or equivalent. Make : GI Conduits : Techno Flex India, K. M. Cables & Conduits or equivalent with Airport approval. The rate shall include wall chasing, chipping of floors, rough plastering, providing suitable supports / Crackets for conduit and Trunking suspension.
F.1.1 | 6/16A SINGLE SWITCHED SOCKET OUTLET | Nos. | 17
F.1.2 | 6/16A DUAL SWITCHED SOCKET OUTLET | Nos. | 7
F.1.3 | 6/16A DUAL SWITCHED UNIVERSAL SOCKET OUTLET + DUAL USB PORT | Nos. | 26
F.1.4 | 16A SINGLE PHASE INDUSTRIAL SWITCHED SOCKET (3 PIN) (WALL MOUNTED) | Nos. | 16
F.1.5 | 20A SINGLE PHASE INDUSTRIAL SWITCHED SOCKET (3 PIN) (WALL MOUNTED) | Nos. | 4
F.1.6 | 32A SINGLE PHASE INDUSTRIAL SWITCHED SOCKET (3 PIN) (WALL MOUNTED) | Nos. | 2
F.1.7 | 63A SINGLE PHASE INDUSTRIAL SWITCHED SOCKET (3 PIN) (WALL MOUNTED) | Nos. | 1
F.1.8 | 32A THREE PHASE INDUSTRIAL SWITCHED SOCKET (5 PIN) (WALL MOUNTED) | Nos. | 2
F.1.9 | 63A THREE PHASE INDUSTRIAL SWITCHED SOCKET (5 PIN) (WALL MOUNTED) | Nos. | 1
F.1.7 | 20A UNSWITCHED FUSED CONNECTION OUTLET WITH-OUT NEON INDICATOR | Nos. | 1
F.1.8 | 20A DOUCLE POLE SWITCH WITH NEON INDICATOR | Nos. | 1
F.1.9 | 16A SINGLE PHASE ISOLATOR | Nos. | 1
F.1.10 | 16A THREE PHASE ISOLATOR | Nos. | 1
F.1.11 | 20A THREE PHASE ISOLATOR | Nos. | 2
F.1.12 | 63A THREE PHASE ISOLATOR | Nos. | 1
G | CONTAINMENT (CABLE TRAY & TRUNKING)
G.1 | Supply & Installation of GI Cable Tray & GI Cable Trunking, through Wall / Ceiling / Floor as per drawings, complete with standard accessories / factory made fittings, earthing throughout the run with copper braids, wall / ceiling suspended supports, etc. Make : Cable Management System : MEM, Profab (ISI marked) or equivalent.
G.1.1 | 100 x 25 CABLE TRAY | Mtr. | 30
G.1.2 | 50 x 50 MM CABLE TRUNKING | Mtr. | 66
G.1.3 | 50 x 50 MM CABLE TRUNKING | Mtr. | 78
H | UPS SYSTEM
H.1 | Supply, Installation, Testing & Commissioning of UPS along with required Cattery for specified back-up time, complete with battery Stand (If required) & standard accessories / equipments required for complete functioning of the system, earthing, support system (if required), etc. Make : UPS System : Luminous, APC, Microtek or equivalent with Airport approval.
H.1.1 | 2 KVA Single phase UPS with 30 Minute Cack-up | Nos. | 1