## HVAC
BILL OF QUANTITIES
PROJECT: | IRISH HOUSE_DELHI AIRPORT |  |  | DATE: | 2024-03-07
|  |  |  | REV: | R0
HVAC SERVICES - WORKS BILL OF QUANTITIES AND ESTIMATE |  |  |  | STATUS: | TENDER
GENERAL NOTES :
All measurements and figures provided below are indicative and must be confirmed by the contractor. The contractor shall have full responsibility for measurements or surveys, and no additional costs or charges will be accepted. The scope of work and quantities mentioned in the MEP BOQ pertain to the MEP services only inside the site location (e.g., within the unit demise). If any termination or connection of services is required outside the site location (i.e., connection of the unit M&E to the airport M&E or service termination to the airport external façade or roof, etc.), then the contractor has to plan, design, and detail these connections in consultation with the airport. The contractor is to do all necessary site surveys to verify the optimal routing for the services in such cases. Any service penetration inside the unit has to be made good after installation, and any fire penetrations on site have to be detailed as per Airport requirements. The contractor is to verify at site and also with Airport authorities whether there are provisions at site to suit the design. Example: The contractor should check for provisions and the extent of power, plumbing, chilled water, ducting, fire and gas provisions etc. available at the site and satisfy himself that there are no risks to the design intent.
ITEM CODE | ITEM NAME | UOM | QTY | UNIT COST | REMARKS
A | HVAC SYSTEM EQUIPMENTS
HVAC EQUIPMENTS
A.1 | Supply, Installation, Testing commisioning of pedestal mounted compact Top discharge Air Cooled type VRF/VRV outdoor units having inverter driven scroll type compressors insulated refrigeration piping, power / control wiring, multi-connection kit, earthing, external wiring between Indoor & outdoor units, system controls-safety. The system should have flexibility to handle total 1000 Rmt of ref. piping. Outdoor units with high/low pressure switch, fan driver overload protector, phase preventer over current relay, Inverter overload protector & fusible plug (or equivalent). The unit shall be suitable for 415 ± 10 % volts, 50 Hz, 3 phase AC supply, and IP 55 protection. The refrigerant shall be R-410 A only. (Make: Daikin,mitsubishi electric or equivalent with airport approval)
A.1.1 | 18 HP | Nos | 1
A.2 | Supply, Installation, Testing, and Commissioning of VRF type Single Skin Ceiling Suspended Air Handling Unit (AHU) of approved make with all necessary mounting and fixing arrangements for the equipment, including hanging arrangements with vibration isolation as required based on the hanging structure above with a suitably sized stainless steel insulated drip tray below the AC equipment. Quote shall be inclusive of AHU kit for connecting VRF Outdoor.(Make: Waves, System Air, Daikin, Voltas, Caryaire,Blue Star or equivalent with airport approval)
A.2.1 | 5.0 TR - (1750 CFM) | Nos | 1
A.2.2 | 9.0 TR - (3150 CFM) | Nos | 1
A.3 | Supply, Installation, Testing, and Commissioning of Chilled water type Double Skin Ceiling Suspended Air Handling Unit (AHU) of approved make with all necessary mounting and fixing arrangements for the equipment, including hanging arrangements with vibration isolation as required based on the hanging structure above with a suitably sized stainless steel insulated drip tray below the AC equipment.Quote shall be inclusive of flexible connector ,Dielectric union & drain valve. (Make: Waves, System Air, Daikin, Voltas, Caryaire,Blue Star or equivalent with airport approval)
A.3.1 | 4.5 TR - (1350 CFM) for Kitchen | Nos | 1
KITCHEN EQUIPMENTS
A.4 | Supply, installation, testing, commissioning and field performance of ceiling suspended Kitchen Exhaust Fan with all necessary supports and fittings.
A.4.1 | 4550 CFM | Nos | 1
A.5 | Supply, installation, testing, commissioning and field performance of ceiling suspended Electrostatic Precipitator (for removal of Kitchen Grease and Smoke particles) with all necessary supports and fittings. (Make: Rydair, Trion or equivalent with airport approval).
A.5.1 | 4550 CFM | Nos | 1
A.6 | Supply, installation, testing, commissioning and field performance of ceiling suspended Air Washer Unit inluding fan for Make up air with all necessary supports and fittings.
A.4.1 | 4550 CFM | Nos | 1
B | AC PIPING
VRF REFRIGERANT PIPING
B.1 | Supply, installation, testing and commissioning of seamless heavy gauge/hard drawn Copper piping for VRF system duly insulated with 19mm thick and 13mm thick nitrile rubber insulation for gas line and liquid line respectively.Polyshield coating for outdoor piping shall be considered. Quote shall be inclusive of communication cabling, refnet joints,required refrigerant gas and all necessary items.
B.1.1 | VRF refrigerant piping system | Lot | 1
HVAC CONDENSATE DRAIN PIPE
B.1 | Supply and fixing in position of Rigid PVC condensate drain water piping with necessary supports and fittings like, U-traps, elbows, tees and reducers insulated with 9mm nitrile rubber and BOPP tape. (Make: Astral, Supreme or equivalent with airport approval).
B.1.1 | 25 mm Ø | Mtr | 20
B.1.1 | 32 mm Ø | Mtr | 20
HVAC CHILLED WATER PIPING
B.2 | Supply, installation and testing of MS class (C) Pre-Insulated Chilled Water Pipe with Poly urethane foam (PUF) insulation of minimum 36 kg/cu.m density and AL jacket or cladding with all necessary fittings, connections, flanges and all necessary pipe supports, clamps as applicable and as per site conditions. (Make: Jindal (Hissar), Tata Steel, SAIL or equivalent with airport approval).
B.2.2 | 32 mm Ø (Insulation thickness - 32 mm) | Mtr | 36
B.2 | Supply, Installation, Testing, and Commissioning of Pressure Independent Control Valve (PICV) with Electric actuators with selectable control modes, with a pressure rating of PN 16 of approved make with threaded or flange connection ends with all necessary fixing arrangements. (Make: Danfoss,Siemen,Flowcon,Honeywell,Anergy,Belimo,Johnsons Control )
B.2.2 | 32 mm Ø (10.8 gpm) | Nos | 1
B.2 | Supply, Installation, Testing, and Commissioning of Forged Brass Y - Strainer with removable perforated SS mesh screen with a pressure rating of PN 16 of approved make, insulation shall be same thickness for corresponding size as chilled water pipe insulation with threaded connection ends with all necessary fixing arrangements. (Make: Emerald, Rapidcool or equivalent with airport approval).
B.2.2 | 32 mm Ø | Nos | 1
B.2 | Supply, Installation, Testing, and Commissioning of Forged Brass Ball Valve with full bore lever operated with a pressure rating of PN 16 of approved make, Valve insulation shall be same thickness for corresponding size as chilled water pipe insulation with threaded connection ends with all necessary fixing arrangements. (Make: Rapidcool, RB, Emerald, Sant, Zoloto.)
B.2.2 | 32 mm Ø | Nos | 2
B.2 | Supply, Installation, Testing, and Commissioning of Analog type Pressure Gauge of approved make with all necessary fixing arrangements. (Make: H.Guru, Fiebig, Emerald.)
B.2.2 | 100 mm Ø Dial | Nos | 2
B.2 | Supply, Installation, Testing, and Commissioning of Analog type Thermometer of approved make with all necessary fixing arrangements. (Make: H.Guru, Fiebig, Emerald.)
B.2.2 | 100 mm Ø Dial | Nos | 2
C | AIR DISTRIBUTION DUCTS
RECTANGULAR DUCTS
C.1 | Supply, installation, and testing of Galvanized Iron (GI) factory fabricated Square / Rectagular Ducts with all necessary fittings, connections, vanes, flanges, bracings,gaskets,duct collars, splitter dampers, and all necessary duct supports like MS Angle bars, slotted rails, threaded rods, anchor bols, nuts, bots, structural beam clamps as applicable. The ducts shall be fabricated and installed in line with SMACNA or DW-144 as required by Airport / local regulatory or approval body having jurisdiction. (Make: Zeco, Ductofab, Waves, Rolastar or equivalent with airport approval).
C.1.1 | 22 Gauge - (0.85 mm Thick) - Supply Air Duct | Sq.Mtr | 10
C.1.2 | 24 Gauge - (0.70 mm Thick) - Supply Air Duct | Sq.Mtr | 60
C.1.3 | 22 Gauge - (0.85 mm Thick) - Make-Up Air Duct | Sq.Mtr | 20
C.1.4 | 24 Gauge - (0.70 mm Thick) - Make-Up Air Duct | Sq.Mtr | 80
C.2 | Supply, installation, and testing of Mild Steel (MS) Ducts fabricated with hot rolled or cold rolled black steel sheets Square / Rectagular Ducts with fully welded leak proof construction with Fire rated spay coat or painted with multiple coats of Red Oxide along with Rock wool insulation conforming to NFPA 96 Standards. with all necessary fittings, connections, vanes, flanges, bracings,gaskets,duct collars, splitter dampers, and all necessary duct supports like MS Angle bars, threaded rods, anchor bols, nuts, bolts, structural beam clamps as applicable. Duct and all other acessaries shall be fire resistant, The ducts shall be fabricated and installed in line with SMACNA or DW-144 as required by Airport / local regulatory or approval body having jurisdiction. (Make: Zeco, Ductofab, Waves, Rolastar or equivalent with airport approval).
C.2.1 | 18 Gauge - (1.31 mm Thick) - Kitchen Exhaust Air Duct | Sq.Mtr | 80
FLEXIBLE DUCTS
C.4 | Supply, installation, and testing of aluminium-polyester casig Round Flexible Duct reinforced with spiral wound steel wire, Temperature range -20° C to +140° C, with a standard insulation thickness of 25 mm and with all necessary connections, fixing and support arrangements of approved make.
C.4.1 | 250 mm Ø | Mtr | 15
C.5 | Supply, installation, and testing of Insulated Flexible Duct Connectors to isolate vibrations caused by air handling units , fans or any other equipments connected to the duct with air tight fittings with all necessary accessories.
C.5.1 | For AHU | Nos | 3
C.5.1 | For FAN | Nos | 1
D | AIR DISTRIBUTION DUCT INSULATION & LINNING
AIR DISTRIBUTION DUCT - THERMAL INSULATIONS
D.1 | Supply, installation, and testing of Thermal Insulation of ducting using closed cell antimicrobial Class “O” BS 476 and part 6 & 7 FM approved nitrile rubber elastomeric insulation thermal conductivity 0.033 watts per meter-kelvin (W/ (M⋅K)) at 0°C. (Make: Armacell, K-Flex, A-Flex or equivalent with airport approval).
D.1.1 | 19 mm thicknesses - (SAD) | Sq.Mtr | 70
D.1.2 | 19 mm thicknesses - (MUAD) | Sq.Mtr | 100
D.2 | Supply, installation & testing of Thermal Insulation of ducting using Aluminium foil faced resin bonded fibre Glass wool of density not less than 48 kg/m3. (Make: Armacell, K-Flex, A-Flex or equivalent with airport approval).
D.2.1 | 80 mm thicknesses - (KED) - External Duct Insulation | Sq.Mtr | 80
AIR DISTRIBUTION DUCT - ACCOUSTIC LININGS
D.3 | Supply, installation & testing of Acoustic Insulation of ducts using opencell processed elastomeric nitrile rubber, Black Colour with Thermal Conductivity λ - 0.045 W/(m-K) at 0° C and Fire performance according to building regulations - Class 1 as per BS 476, with very good sound absorption, damping and barrier properties. (Make: Armacell, K-Flex, A-Flex or equivalent with airport approval).
D.3.1 | 15 mm thicknesses - (SAD) | Sq.Mtr | 20
E | AIR DISTRIBUTION DUCT ACCESSORIES
DUCT AIR CONTROL DAMPERS
E.1 | Supply, installation, tetsing and commissioning of Extruded Aluminium Low Leakage Square / Rectangular Volume Control Damper with aero-foil opposed blades and nylon gears system outside air stream with adjustable handle with position arresting bolt. (Make: Greenheck, System Air, JCI, Caryaire or equivalent with airport approval)
E.1.1 | Size - 600 x 400 mm | Nos | 1
E.1.2 | Size - 600 x 300 mm | Nos | 1
E.1.3 | Size - 450 x 350 mm | Nos | 1
E.1.4 | Size - 450 x 300 mm | Nos | 1
E.1.5 | Size - 300 x 300 mm | Nos | 2
E.1.6 | Size - 200 x 300 mm | Nos | 1
E.1.6 | Size - 200 x 200 mm | Nos | 1
E.1.6 | Size - 150 x 150 mm | Nos | 1
E.1 | Supply, installation, tetsing and commissioning of Circular Volume Control Damper with high quality Galvanized steel and Flap Blade fixed with nylon bushes, with hand locking quadrant. (Make: Greenheck, System Air, JCI, Caryaire or equivalent with airport approval)
E.1.1 | Size - 350 mm | Nos | 10
F | AIR TERMINALS - (GRILLES, REGISTERS, DIFFUSERS & DAMPERS)
GRILLES
F.1 | Supply, installation, tetsing and commissioning of Extruded Aluminium Square Grille with opposed blade collar damper & fixed Aerofoil Blades, fixed Aerofoil Blades, with 15° deflection - 2 Way with rigid frame of 20mm flange as standard. (Make: System Air, Caryaire, Dynacraft, Airmaster or equivalent with airport approval).
F.1.1 | Neck Size - 400 x 400 mm | Nos | 6
F.2 | Supply, installation, tetsing and commissioning of Extruded Aluminium Rectangular Grille with opposed blade collar damper & fixed Aerofoil Blades, fixed Aerofoil Blades, with 15° deflection - 1 Way with rigid frame of 20mm flange as standard. (Make: System Air, Caryaire, Dynacraft, Airmaster or equivalent with airport approval).
F.2.1 | Neck Size - 450 x 200 mm | Nos | 4
F.2.2 | Neck Size - 350 x 300 mm | Nos | 1
F.2.2 | Neck Size - 200 x 100 mm | Nos | 1
F.1 | Supply, installation, tetsing and commissioning of Extruded Aluminium Curved linear Grille with opposed blade collar damper & fixed Aerofoil Blades, with 15° deflection - 1 Way with rigid frame of 20mm flange as standard. Curve of the grille shall be taken from the tender drawings .Quote shall be inclusive of plenum box and fittings. (Make: System Air, Caryaire, Dynacraft, Airmaster or equivalent with airport approval).
F.2.1 | Neck Size - 1050 x 150 mm | Nos | 5
F.2.1 | Neck Size - 1050 x 150 mm without damper. | Nos | 2
CEILING DIFFUSERS
F.2 | Supply, installation, tetsing and commissioning of Aluminium Round Diffuser with circular cones for throw in circular patern and with volume control damper, Powder coated finish with RAL Colour as required by ID Designer / Architect of approved make and with all necessary fixing arrangements. Quote shall be inclusive of Plenum box and fittings. (Make: System Air, Caryaire, Dynacraft, Airmaster or equivalent with airport approval).
F.2.1 | Neck Size - 350 mm Ø | Nos | 10
F.2 | Supply, installation, tetsing and commissioning of Aluminium Round Diffuser with circular cones for throw in circular patern and without volume control damper, Powder coated finish with RAL Colour as required by ID Designer / Architect of approved make and with all necessary fixing arrangements. (Make: System Air, Caryaire, Dynacraft, Airmaster or equivalent with airport approval).
F.2.1 | Neck Size - 350 mm Ø | Nos | 8
G | TESTING & COMMISIONING
G.1 | Air Balancing & Chilled Water Testing & Commisioning | Lot | 1
GRANT TOTAL NET
NOTE: The quantities mentioned in the above BOQ includes services only inside the site location (building). If any termination of services required outside the site location contractor to verify at site and provide the quantity and cost over and above this BOQ. Any service penetration to be made good after installation. Fire sealing to be done for penetrations as per Airport requirement.