## BOQ
ANJLE MEP PROJECTS PVT LTD
41/1407 , 2ND FLOOR DDA FLAT MADANGIR NEW DELHI 110062 - 01141401600 , 9871770191
|  |  |  | Po QTY |  | AS Per Signed MB Sheet |  | Invoice QTY |  | New PR Qty
ItemCode | Item Name | UOM | Qty | Unit Price | AMT | qty | AMT | Final qty | Final Amount | Final qty | Final Amount
FIRE ALARM SYSTEM - DETECTION DEVICES
B.1 | Supply, Installation, Testing, and Commissioning of Addressable Type (Optical Smoke & Heat) Smoke Detector Conforming to EN54, with standard detector mounting base, IP30 Ingress Protection, Area Coverage of 50 sq. mm (subject to local standard), 360° Angle Visibility, Operating Temperature (-10°C to +50°C), approved by LPCB, of approved make along with suitable size 2 core cable clipped to structure/wall/ceiling / through GI or Heavy Duty PVC Conduits with suitable cable clips/saddles with all necessary mounting and fixing arrangements. (Above & Below Ceiling) Make Fire Alarm Devices: Johnson or as directed by the Airport. Make: PVC Conduits: Sudhakar, Shakti or equivalent
B.1.1 | Below ceiling level and above | Nos | 8 | 5500 | 44000 | 9 | 49500 | 8 | 44000 | 1 | 5500
B.2 | Supply, Installation, Testing, and Commissioning of Addressable Type Fixed Temperature Heat Detector Conforming to EN54, with standard detector mounting base, IP30 Ingress Protection, Area Coverage of 50 sq. mm (subject to local standard), 360° Angle Visibility, Operating Temperature (-10°C to +50°C), approved by LPCB, of approved make along with suitable size 2 core cable clipped to structure/wall/ceiling / through GI or Heavy Duty PVC Conduits with suitable cable clips/saddles with all necessary mounting and fixing arrangements. Make Fire Alarm Devices: Johnson or as directed by the Airport. Make: PVC Conduits: Sudhakar, Shakti or equivalent
B.2.1 | Heat Detector - 58°C fixed temperature | Nos | 1 | 5450 | 5450 | 2 | 10900 | 1 | 5450 | 1 | 5450
B.3 | Supply, Installation, Testing, and Commissioning of Addressable Type Manual Call Point Conforming to EN54 with Break glass, ABS material enclosure, IP30 Ingress Protection, Operating Temperature (-10°C to +50°C) of approved make along with suitable size 2 core cable clipped to structure/wall/ceiling / through GI or Heavy Duty PVC Conduits with suitable cable clips/saddles suitable for flush and surface mounting with all necessary mounting, termination and fixing arrangements. Make Fire Alarm Devices: Johnson or as directed by the Airport. Make: PVC Conduits: Sudhakar, Shakti or equivalent
B.3.1 | Manual Call Point - (Wall / Partition Mounted) | Nos | 2 | 6750 | 13500 | 2 | 13500 | 2 | 13500 | 0 | 0
B.4 | Supply, Installation, Testing and commissioning of Addressable type Sounder Strobe with inbuilt Isolator & and operating temp (- 10 degrees to + 55 degrees) complete as required and duly approved by LPCB / EN54 along with suitable size 2 core cable clipped to structure/wall/ceiling / through GI or Heavy Duty PVC Conduits with suitable cable clips/saddles. Make Fire Alarm Devices: Johnson or as directed by the Airport. Make: PVC Conduits: Sudhakar, Shakti or equivalent
B.4.1 | Sounder Strobe - (Wall / Partition Mounted) | Nos | 3 | 6200 | 18600 | 4 | 24800 | 3 | 18600 | 1 | 6200
FIRE ALARM SYSTEM - MODULE DEVICES
B.5 | Supply, Installation, Testing, and Commissioning of Addressable Type Monitor Module along with suitable size 2 core cable clipped to structure/wall/ceiling / through GI or Heavy Duty PVC Conduits with suitable cable clips/saddles. Make Fire Alarm Devices: Johnson or as directed by the Airport. Make: PVC Conduits: Sudhakar, Shakti or equivalent
B.5.1 | Monitor Module | Nos | 2 | 6850 | 13700 | 7 | 47950 | 2 | 13700 | 5 | 34250
B.6 | Supply, Installation, Testing, and Commissioning of Addressable Type Isolation Module along with suitable size 2 core cable clipped to structure/wall/ceiling / through GI or Heavy Duty PVC Conduits with suitable cable clips/saddles. Make Fire Alarm Devices: Johnson or as directed by the Airport. Make: PVC Conduits: Sudhakar, Shakti or equivalent | [6 empty] | 0
B.6.1 | Isolation Module | Nos | 1 | 5650 | 5650 | 1 | 5650 | 1 | 5650 | 0 | 0
B.6.2 | Response Indicatore | nos | 4 | 250 | 1000 | 4 | 1000 | 4 | 1000 | 0 | 0
B.6.2 | Suply and installation of power suply for hooter | nos | 4 | 1500 | 6000 | 4 | 6000 | 4 | 6000 | 0 | 0
| Total for FAS |  |  |  | 100900 |  | 159300 | 0 | 107900 | 0 | 51400
AUTOMATIC FIRE SPRINKLER HEADS & ACCESSORIES
A.1 | Supply, Installation, Testing & Commissioning of Automatic Concealed Fire Sprinkler Heads (Bulb type Sprinklers) with adjustable Escutcheon plates (Rosette plates). Standard Temperature Response with 5mm glass bulb, Temperature rating of 68° C, K-factor of 80, Nominal Thread size of 1/2" NPT (15mm) and a Orifice size of 13mm with a Max. Working Pressure of 12 Bar (Factory hydrostatic test presure of 35 Bar) and to be Manufactured & Certified to UL 199. Shall also include suspending arrangement with ceiling / wall etc. (Make: Ansul, Buckeye, Smog Hog, Gem-Tyco, Spray safe or equivalent with airport approval)
A.1.1 | Pendant type of 68° C (Finishing - Chrome Plated) | Nos | 26 | 950 | 24700 | 30 | 28500 | 26 | 24700 | 4 | 3800
A.1.2 | Pendant type of 79° C (Finishing - Chrome Plated) | Nos | 5 | 1020 | 5100 | 5 | 5100 | 5 | 5100 | 0 | 0
A.1.3 | Upright Pendant type of 68° C (Finishing - Chrome Plated) | Nos | 29 | 1050 | 30450 | 30 | 31500 | 29 | 30450 | 1 | 1050
| FIRE SPRINKLER PIPE VALVES & ACCESSORIES | [5 empty] | 0
A.3 | Supply, Installation, Testing & Commissioning of Cast Iron Butterfly Valve slimseal PN16 (working pressure of 16 Bar), standard flow control lever operated with stainless steel shaft & disc, seat material with Black Nitrile / EPDM, flanges nuts and bots etc. (Make: Tyco/Viking/Victualic/ HD fire/Newage or equivalent with airport approval.) | [5 empty] | 0
A.3.1 | 100mm Dia | Nos | 1 | 8250 | 8250 | 1 | 8250 | 1 | 8250 | 0 | 0
A.4 | Supply, Installation, Testing & Commissioning of Brass body Test And Drain Valve with Sight Glass, working pressure of 20 Bar (300 PSI), standard lever operated with stainless steel stem & lever, with necessary weldable fittings in position as per drawings / site conditions. (Make: Tyco/Viking/Victualic/ HD fire/Newage or equivalent with airport approval.) | [5 empty] | 0
A.4.1 | 25 mm Dia | Nos | 1 | 1250 | 1250 | 1 | 1250 | 1 | 1250 | 0 | 0
A.5 | Supply, Installation, Testing & Commissioning of Flow Switch on Sprinkler distribution header pipe with a working pressure of 31 Bar (450 PSI) and a flow sensitivity range of 4-10 GPM (15 - 38 LPM) on each floor / zone / inside proposed demise area tap of point, shall be connected to fire alarm panel through cable. (Make: Potter/ System Sensor or equivalent with airport approval) | [5 empty] | 0
A.5.1 | 100 mm Dia | Nos | 1 | 10500 | 10500 | 1 | 10500 | 1 | 10500 | 0 | 0
A.5.2 | Supply and installation with pressure gouge with Ball valve | nso | 0 | 2500 | 0 | 1 | 2500 |  | 0 | 1 | 2500
| FIRE SPRINKLER PIPING | [5 empty] | 0
A.6 | Supply, Installation, Testing & Commissioning of MS "C" Class Fire Sprinkler Pipe confirming to IS: 1239 with all fittings like bends, tees, flanges, nut, bolt and washers etc, and proper pipe supports to not more than 3 meter apart of the pipe length. The pipe work shall be hydrostatically tested for not less than 2 hours at 15 Bar (or 1.5 times the working) pressure without leak. The pipes are to be applied with 2 coats of primer (indicated film thickness, dry 50 microns) and 2 coats of enamel finish paint of approved colour (indicated film thickness, dry 30 microns) (Make: HSL, Mukut, Lalit steel or equivalent) | [5 empty] | 0
A.6.1 | 25 mm Dia | Mtr | 60 | 750 | 45000 | 90 | 67500 | 60 | 45000 | 30 | 22500
A.6.2 | 32 mm Dia | Mtr | 12 | 950 | 11400 | 18 | 17100 | 12 | 11400 | 6 | 5700
A.6.3 | 40 mm Dia | Mtr | 26 | 1050 | 27300 | 30 | 31500 | 26 | 27300 | 4 | 4200
A.6.4 | 50 mm Dia | Mtr | 5 | 1250 | 6250 | 9 | 11250 | 5 | 6250 | 4 | 5000
A.6.5 | 65 mm Dia | Mtr | 25 | 1650 | 41250 | 30 | 49500 | 25 | 41250 | 5 | 8250
A.6.6 | 80 mm Dia | Mtr | 5 | 1750 | 8750 | 6 | 10500 | 5 | 8750 | 1 | 1750
A.6.7 | 100 mm Dia | Mtr | 5 | 1850 | 9250 | 34 | 62900 | 5 | 9250 | 29 | 53650
| Total for Fire |  |  |  | 229450 |  | 337850 |  | 229450 | 0 | 108400
A | HVAC SYSTEM EQUIPMENTS
KITCHEN EQUIPMENTS
A.1 | Supply, installation, testing, commissioning and field performance of ceiling suspended Electrostatic Precipitator (for removal of Kitchen Grease and Smoke particles) with all necessary supports and fittings. (Make: Rydair, Trion or equivalent with airport approval).
A.1.1 | 2500 CFM | Nos | 1 | 145000 | 145000 | 1 | 145000 | 1 | 145000 | 0 | 0
| Total for Hi-side |  |  |  | 145000 |  | 145000 | 0 | 145000 | 0 | 0
B | AIR DISTRIBUTION DUCTS RECTANGULAR DUCTS
B.1 | Supply, installation, and testing of Galvanized Iron (GI) factory fabricated Square / Rectagular Ducts with all necessary fittings, connections, vanes, flanges, bracings,gaskets,duct collars, splitter dampers, and all necessary duct supports like MS Angle bars, slotted rails, threaded rods, anchor bols, nuts, bots, structural beam clamps as applicable. The ducts shall be fabricated and installed in line with SMACNA or DW-144 as required by Airport / local regulatory or approval body having jurisdiction. (Make: Zeco, Ductofab, Waves, Rolastar or equivalent with airport approval).
B.1.1 | 24 Gauge - (0.70 mm Thick) - Supply Air Duct | Sq.Mtr | 88 | 1240 | 109120 | 92.5 | 114700 | 88 | 109120 | 4.5 | 5580
B.1.2 | 24 Gauge - (0.70 mm Thick) - Kitchen Supply Air Duct | Sq.Mtr | 58 | 1270 | 73660 | 65 | 82550 | 58 | 73660 | 7 | 8890
B.2 | Supply, installation, and testing of Mild Steel (MS) Ducts fabricated with hot rolled or cold rolled black steel sheets Square / Rectagular Ducts with fully welded leak proof construction with Fire rated spay coat or painted with multiple coats of Red Oxide along with Rock wool insulation conforming to NFPA 96 Standards. with all necessary fittings, connections, vanes, flanges, bracings,gaskets,duct collars, splitter dampers, and all necessary duct supports like MS Angle bars, threaded rods, anchor bols, nuts, bolts, structural beam clamps as applicable. Duct and all other acessaries shall be fire resistant, The ducts shall be fabricated and installed in line with SMACNA or DW-144 as required by Airport / local regulatory or approval body having jurisdiction. (Make: Zeco, Ductofab, Waves, Rolastar or equivalent with airport approval). | [5 empty] | 0 | 0 | 0 | 0 | 0
B.2.1 | 18 Gauge - (1.31 mm Thick) - Kitchen Exhaust Air Duct - GI Sheet | Sq.Mtr | 70 | 2020 | 141400 | 65 | 131300 | 65 | 131300 | 0 | 0
B.3 | Demolition of necessary Galvanized Iron (GI)/ Galvanized Steel (GS) ducts, as well as their closing and dummying to best align with the suggested HVAC system, are required. Contractor to conduct field verification and analysis based on site conditions. | [5 empty] | 0 | 0 | 0 | 0 | 0
B.3.1 | Supply Air Duct | LOT | 1 | 22000 | 22000 | 1 | 22000 | 1 | 22000 | 0 | 0
C | AIR DISTRIBUTION DUCT INSULATION & LINNING AIR DISTRIBUTION DUCT - THERMAL INSULATIONS | [5 empty] | 0 | 0 | 0 | 0 | 0
C.1 | Supply, installation, and testing of Thermal Insulation of ducting using closed-cell elastomeric nitrile rubber, Black Colour with Thermal Conductivity λ - 0.036 W/(m-K) at 0° C and Fire performance according to building regulations - Class "O" as per BS 476. (Make: Armacell, K-Flex, A-Flex or equivalent with airport approval). | [5 empty] | 0 | 0 | 0 | 0 | 0
C.1.1 | 19 mm thicknesses - (SAD) - External Duct Insulation | Sq.Mtr | 88 | 740 | 65120 | 92.5 | 68450 | 88 | 65120 | 4.5 | 3330
C.1.2 | 19 mm thicknesses - (KSAD) - External Duct Insulation | Sq.Mtr | 58 | 740 | 42920 | 65 | 48100 | 58 | 42920 | 7 | 5180
C.2 | Supply, installation & testing of Thermal Insulation of ducting using glass wool with silver foil covering, density 40 Kg/m3, Thermal Conductivity λ - 0.030 W/(m-K) at 0° C and Fire performance according to building regulations - Class "O" as per BS 476. (Make: Armacell, K-Flex, A-Flex or equivalent with airport approval). | [5 empty] | 0
C.2.1 | 80 mm thicknesses - (KEAD) - External Duct Insulation | Sq.Mtr | 70 | 1100 | 77000 | 65 | 71500 | 65 | 71500 | 0 | 0
D | AIR DISTRIBUTION DUCT ACCESSORIES DUCT AIR CONTROL DAMPERS | [5 empty] | 0 | 0 | 0 | 0 | 0
D.1 | Supply, installation, tetsing and commissioning of Extruded Aluminium Low Leakage square / rectangular Volume Control Damper with aero-foil opposed blades and nylon gears system outside air stream with adjustable handle with position arresting bolt. (Make: Greenheck, System Air, JCI, Caryaire or equivalent with airport approval) | [5 empty] | 0 | 0 | 0 | 0 | 0
D.1.1 | Size - 900 x 350 mm | Nos | 1 | 4250 | 4250 | 1 | 4250 | 1 | 4250 | 0 | 0
D.1.2 | Size - 600 x 200 mm | Nos | 1 | 3250 | 3250 | 1 | 3250 | 1 | 3250 | 0 | 0
D.1.3 | Size - 400 x 150 mm | Nos | 1 | 3050 | 3050 | 1 | 3050 | 1 | 3050 | 0 | 0
D.1.4 | Size - 300 x 350 mm | Nos | 1 | 2650 | 2650 | 1 | 2650 | 1 | 2650 | 0 | 0
D.1.5 | Size - 750 x 300 mm | Nos | 1 | 3500 | 3500 | 1 | 3500 | 1 | 3500 | 0 | 0
D.1.6 | Size - 700 x 250 mm | Nos | 1 | 4250 | 4250 | 1 | 4250 | 1 | 4250 | 0 | 0
D.1.7 | Size - 900 x 350 mm MS FLANGE | Nos | 1 | 5250 | 5250 | 1 | 5250 | 1 | 5250 | 0 | 0
D.1.8 | Size - 700 x 250 mm MS FLANGE | Nos | 1 | 4250 | 4250 | 1 | 4250 | 1 | 4250 | 0 | 0
D.1.9 | Size - 350 x 150 mm MS FLANGE | Nos | 1 | 3540 | 3540 | 1 | 3540 | 1 | 3540 | 0 | 0
D.1.10 | Size - 550 x 250 mm MS FLANGE | Nos | 1 | 4650 | 4650 | 1 | 4650 | 1 | 4650 | 0 | 0
E | AIR TERMINALS - (GRILLES, REGISTERS, DIFFUSERS & LOUVERS) GRILLES | [5 empty] | 0 | 0 | 0 | 0 | 0
E.1 | Supply, installation, tetsing and commissioning of Extruded Aluminium Single Deflection Grille with opposed blade collar damper aerofoil adjustable front and rear blades with collar damper frame of 20mm flange, Powder coated finish with RAL Colour as required by ID Designer / Architect of approved make and with all necessary fixing arrangements. (Make: System Air, Caryaire, Dynacraft, Airmaster or equivalent with airport approval). | [5 empty] | 0
E.1.1 | Neck Size - 750 x 150 mm | Nos | 9 | 1650 | 14850 | 9 | 14850 | 9 | 14850 | 0 | 0
E.1.2 | Neck Size - 750 x 150 mm - without damper | Nos | 9 | 1250 | 11250 | 8 | 10000 | 8 | 10000 | 0 | 0
E.2 | Supply, installation, tetsing and commissioning of Extruded Aluminium Double Deflection Grille with opposed blade collar damper aerofoil adjustable blades with of 20mm flange, Powder coated finish with RAL Colour as required by ID Designer / Architect of approved make and with all necessary fixing arrangements (Make: System Air, Caryaire, Dynacraft, Airmaster or equivalent with airport approval). | [5 empty] | 0
E.2.1 | Neck Size - 350 x 350 mm | Nos | 8 | 1550 | 12400 | 8 | 12400 | 8 | 12400 | 0 | 0
E.2.2 | Neck Size - 350 x 350 mm - without damper | Nos | 4 | 1450 | 5800 | 1 | 1450 | 1 | 1450 | 0 | 0
F | TESTING & COMMISIONING | [5 empty] | 0 | 0 | 0 | 0 | 0
F.1 | Duct Air Balancing & Commisioning | Lot | 1 | 8000 | 8000 | 1 | 8000 | 1 | 8000 | 0 | 0
Extra Work
| Supply & Installation Grill 20000MM X 250mm ( As per confirm by Shadab Sir) | Rmt | 20 | 1650 |  |  | 33000 |  | 0 | 20 | 33000
| Gate Pass & Escort Charges | Nos | 1 | 25000 |  |  | 25000 |  | 0 | 1 | 25000
| Total for Low-side |  |  |  | 622160 |  | 681940 |  | 600960 |  | 80980
| Grand Total |  |  |  | 1097510 |  | 1324090 |  | 1083310 |  | 240780
|  |  |  | po value | 1097510
[5 empty] | Diffrence Amount exclud gst |  | 226580
GST EXTRA
Updated Quntities are Highlighted
Diffrence amount (Rs.226580.00) as per the Signed MB sheet
We are Raising Invoice As per Purchase Order Rest Will Be raise After receiving Confirmation with PO.