## PHE BOQ
FLYING BITE-PHE BOQ |  |  |  | Rev: | 0
|  |  |  | Date: | 23.11.2024
Item No. | Description | Unit | Qty. | Rate | Amount | Make
A | WATER SUPPLY PIPING
1 | CPVC Pipes conforming to ASTM D-2846, SDR-11 grade and CPVC solvent weld fittings like elbows, tees, couplars, brass threaded adaptors, insert ring etc. suitable for (domestic and flushing) cold applications rated, concealed piping within wall / floor including jointing with fittings using solvent cement, brass threaded end fittings for making connection to fixtures. The work shall also include chasing the walls with machine wherever required for concealed piping and making good the same after laying of pipes & necessary pressure testing Chasing finishing shall be done with 1:1 cement mixed mortar, restore the same original condition for internal and shaft piping, including necessary hot deep galvanised supports vertical / horizontal, as per direction of Site incharge direction. [The rate shall include supply of S.S.screws and nut bolts etc.chasing in walls done by machine] (For Domestic and Flushing water-Toilet internal) (Pipe shall be tested with 1.5 times working pressure as covered in specifications) |  |  |  |  | Astral / Ashirwad /supreme / Prince or Approved Equivalent
1.1 | 20 mm Dia | R.mt | 30 |  | 0
1.2 | 25 mm Dia | R.mt | 5 |  | 0
1.3 | 32mm Dia | R.mt | 0 |  | 0
1.4 | 40mm Dia | R.mt | 0 |  | 0
2 | Providing & Fixing of gun metal heavy Ball Valves-PN-16 (approved makes as covered in specification) screwed type for water system of the following diameters. Valve shall have with unions. |  |  |  |  | Leader / Neta / Zolotto / or approved Equivalent
2.1 | 20mm Dia | Nos. | 4 |  | 0
2.2 | 25mm Dia | Nos. | 1 |  | 0
2.3 | 32mm Dia | Nos. | 1 |  | 0
2.4 | 40mm Dia | Nos. | 0 |  | 0
3 | Providing ,fixing, testing and commissioning capstan make Water Meter including providing & fixing matching Isolation valves ,strainer, non-return valve,complete with all necessary fittings , pressure gaage etc screwed type(15Kgs/Sq.cm). Valve shall have with union.
3.1 | 25 mm Dia incoming line | Nos. | 1 |  | 0
3.2 | 32 mm Dia incoming line | Nos. | 1
3.3 | 40 mm Dia incoming line | Nos. | 0 |  | 0
4 | Supply, installation,testing & commissioning of Storage Type Electric Hot Water Generator of mentioned capacity, suitable for 3 KG/cm2 pressure, Wall Mounted / Floor standing type, with Auto Shut-off Thermostat, along with isoltion Valves, Air Release valve, SS flexible connections andall other std accessories |  |  |  |  | AO Smith or Approved Equivalent
4.1 | 5 L Capacity- | Nos. | RO
4.2 | 20 L Capacity | Nos. | 1 |  | 0
4.3 | 35 L Capacity- For shower | Nos. | RO
5 | Supply, installation,testing & commissioning of Stiebel Type Electric Hot Water Generator of mentioned capacity, suitable for 3 KG/cm2 pressure, Wall Mounted / Floor standing type, with Auto Shut-off Thermostat, along with isoltion Valves, Air Release valve, SS flexible connections andall other std accessories (Optional in pantry) |  |  |  |  | Stiebel Entron or Approved Equivalent
5.1 | 3.5kw in pantry- optional | Nos. | RO
5.2 | 8kw | Nos. | RO
5.3 | 13kw-3ph- Subject to load permits | Nos. | RO
Note- Geyser order shall be placed as per site feasibility. Electrical geyser or Gas geyser to be checked at site prior to proceed.
6 | SITC of 12 LIT RO-ULTRA +UV with required accessories | Nos | 1 |  | 0 | Kent /LG or Approved Equivalent
7 | SITC of Eco smart RO-50 with all required accessories | Nos | 0 |  | 0 | Iron Exchange or Approved Equivalent
8 | SITC of ACO grease trap -model Lipumobil-S -Capacity -32 lit ( 0.5 LPS) with all required accessories or Equivalent Model | Nos | 1 |  | 0 | Aco or Approved Equivalent
9 | Only installtaion of tailer made Grease trap with required accessories | Nos | 0 |  | 0 | Nugreen, Aco or Approved Equivalent
10 | Only installation of of UV filter (pentair UV-900) with required accessories. Supply shall be by the kitchen consulatnt | Nos | 0 |  | 0 | Alfa or equivalent
A | SUB TOTAL OF A |  |  |  | 0
B | DRAINAGE
1 | UPVC-SWR pipes (TYPE-B-working pressure 6kg/cm2) conforming to IS 13592/92 including fittings conforming to IS-14935/99 and agri type pipes above 100 mm dia. conforming to IS: 4985, cutting the pipes to required lengths, laying in the position to required grade and level, jointing, supporting with PVC cleat,hot deep galvanised bracket supports,hot deep galvanised nut-bolts, anchor fastners, PVC coated U-clamp, testing and rectifying leakages for piping within vertical shafts / supported on wall / hung below slab etc. with all material & labor complete and as directed. [The Rate shall include supply and fixing of hotdip galvanised bracket nut bolts/ PVC Coated U-Clamp and screws] Vertical line bracket shall be fixed at every 0.8 mtr to 1.00 mtr.] (INTERNAL /VERICAL PIPING-DRAINAGE) |  |  |  |  | Supreme / Finolex / Prince / Oriplast / or Approved Equivalent
1.1 | 40mm Dia | R.mt | 2 |  | 0
1.2 | 50mm Dia | R.mt | 2 |  | 0
1.3 | 65mm Dia | R.mt | 0 |  | 0
1.4 | 75mm Dia | R.mt | 3 |  | 0
1.5 | 100 mm Dia | R.mt | 0 |  | 0
1.6 | 150 mm Dia | R.mt | RO
2 | Heavy PVC multi floor trap as per drawings with cockroach trap and 40 mm minimum seal complete with M-150 cement concrete all around and below the trap, including supplying and fixing S.S. / C.P grating etc all complete. |  |  |  | 0
2.1 | 100 mm Dia | Nos. | 2 |  | 0
3 | Heavy PVC floor trap as per drawings with cockroach trap and 40 mm minimum seal complete with M-150 cement concrete all around and below the trap, including supplying and fixing S.S. / C.P grating etc all complete. |  |  |  | 0
3.1 | 100 mm Dia | Nos. | 0 |  | 0
4 | Supply, Install PVC Clean out plugs including fixing with necessary consumables.
4.1 | 100 mm Dia | Nos. | 4 |  | 0
5 | Heavy PVC P- trap as per drawings with cockroach trap and 50 mm minimum seal complete with M-150 cement concrete all around and below the trap, including supplying and fixing S.S. / C.P grating etc all complete. | Nos. | 0 |  | 0
6 | Providing core cuts as required at site for water supply and drain lines. (Optional if required at site) |  |  |  | 0
6.1 | 50mm Dia | Nos. | 0 |  | 0
6.2 | 75mm Dia | Nos. | 0 |  | 0
6.3 | 100 mm Dia | Nos. | 1 |  | 0
6.4 | 150 mm Dia | Nos. | 0
| SUB TOTAL OF B |  |  |  | 0
C | SANITARY AND C. P. FITTINGS & FIXTURES
Supply, installation, testing and commissioning of sanitary and C.P. fittings. Model no shall be as per ID preferance
1.1 | EWC with seat cover | Nos | 0 |  | 0
1.2 | Concealed flush tank | Nos | 0 |  | 0
1.3 | Concealed flush valve | Nos | 0 |  | 0
1.4 | Health Faucet | Nos | 0 |  | 0
1.5 | 2 Way Bib-Cock with connection for Health Faucet | Nos | 0 |  | 0
1.6 | Bided | Nos | 0 |  | 0
1.7 | Under Counter Wash Basin including waste Coupling | Nos | 0 |  | 0
1.8 | Wash Basin Cock | Nos | 0 |  | 0
1.9 | shower and mixer | Nos | 0 |  | 0
1.1 | Jet Spray | Nos | 0 |  | 0
1.11 | Bath Tub including waste Coupling and nessessary connections | Nos | 0 |  | 0
1.12 | Under Counter Sink including waste Coupling | Nos | 1 |  | 0
1.13 | Sink Pillar Cock | Nos | 1 |  | 0
1.14 | Bottle Trap for WHB/ sink and urinal with all connecting pipes | Nos | 1 |  | 0
1.15 | Angle Cock with PVC pipe connection upto WHB/sink/Geyser connection | Nos | 6 |  | 0
1.16 | Urinal | Nos | 0 |  | 0
1.17 | Auto Flush Valve & Sensor with connecting piping & spreader for urinal(DC) | Nos | 0 |  | 0
1.18 | Only instllations of Filter Faucet | Nos | 0 |  | 0
1.19 | Only instllations of Deck mounted mixture | Nos | 0 |  | 0
1.2 | Only instllations of Wall mounted mixture | Nos | 0 |  | 0
1.21 | Only instllations of bar Faucet | Nos | 0 |  | 0
| SUB TOTAL -C-SANITARY AND C. P. FITTINGS & FIXTURES ( ONLY INSTALLATIONS) |  |  |  | 0
D | S.S. GRATING ( ONLY INSTLLATION)
Instllation testing and commissioning of S.S.Gratings
a | Making chamber in brick work including internal tiling etc for S.S Grating size, 150mm x 150mm, in 16 swg 25mm x25mm Square Pipe around the Frame and 20mmX 20mm Square pipe in center of frame with SS perforated tray (304 SWR). Complete as per architectural detail drawing & Site Engineer's instruction. | Nos. | 1 |  | 0 |  | 4
b | Making chamber in brick work including internal tiling etc for S.S Grating size, 600mm x 300mm, in 16 swg 25mm x25mm Square Pipe around the Frame and 20mmX 20mm Square pipe in center of frame with SS perforated tray (304 SWR). Complete as per architectural detail drawing & Site Engineer's instruction. | Nos. | 0 |  | 0
c | Making chamber in brick work including internal tiling etc for S.S Grating size, 1200mm x 300mm, in 16 swg 25mm x25mm Square Pipe around the Frame and 20mmX 20mm Square pipe in center of frame with SS perforated tray (304 SWR). Complete as per architectural detail drawing & Site Engineer's instruction. | Nos. | 0 |  | 0
D | Making chamber in brick work including internal tiling etc for S.S Grating size, 3000mm x 300mm, in 16 swg 25mm x25mm Square Pipe around the Frame and 20mmX 20mm Square pipe in center of frame with SS perforated tray (304 SWR). Complete as per architectural detail drawing & Site Engineer's instruction. | Nos. | 0 |  | 0
| SUB TOTAL -D-S.S. GRATING INSTALLATION ( ONLY INSTALLATIONS) |  |  |  | 0
| GRAND - TOTAL A , B, C AND D |  |  |  | 0
NOTES :
1. Taxes and duties shall be Extra as actual
2. Supply and installation of Sanitary fixtures and fitting in th kitchen and toilets
3. Supply of S.S. gratings in kitchen

## General Notes
GENERAL NOTES
1 | The items given in this schedule are provisional. The Contractor shall be paid for the actual quantity of work executed as measured at the site at the rates tendered. The Owner reserves the right to increase or decrease any of the quantities, or to ommit totally any item of work. Any claim by the Contractor on these accounts will not be entertained.
2 | All the items of work given in this schedule of quantities shall be executed strictly in accordance with the latest Indian Standard Specifications.
3 | The Contractor shall visit the site and shall satisfy himself as to the conditions under which the work is to be performed. He shall also check and ascertain the location of any existing structure or equipment or any other situation which may affect the work. No extra claim as a consequence of ignorance or on ground of insufficient description will be allowed at a later date.
4 | All equipment and material shall be IS approved.
5 | All approvals shall be obtained from Owner / Consultant
6 | All equipment and material shall be inspected at manufacturer’s works as per relevant IS by the Owner or his representative before despatch to site.
7 | All vendor drawings shall be approved by the Owner/Consultant before fabrication work starts.
8 | All Testing and Commissioning shall be as per relevant details covered in the specifications. All these testing records are to be maintained and submitted for Owner / Owner’s representative.
9 | All items of work under this Contract shall be executed strictly to fulfill the requirements laid down under “Basis of Design” in the specifications. Type of equipment, material specification, methods of installation and testing and type of control shall be in accordance with the specifications, approved shop drawings and the relevant Indian Standards, however capacity of each component and their quantities shall be such as to fulfill the above mentioned requirement.
10 | The unit rate for all equipment or materials shall include cost in INDIAN RUPEES (INR) for equipment and materials including all taxes and duties and also including forwarding, freight, insurance and transport into Contractor’s store at site, storage, installation, testing, balancing, commissioning and other works required.
11 | The rate for each item of work included in the Schedule of Quantities shall, unless expressly stated otherwise, include cost of :
a | All materials, fixing materials, accessories, appliances tools, plants, equipment, transport, labour and incidentals required in preparation for and in the full and entire execution, testing, balancing, commissioning and completion of work called for in the item and as per Specifications and Drawings.
b | Wastage on materials and labour.
c | Loading, transporting, unloading, handling/double handling, hoisting to all levels, setting, fitting and fixing in position, protecting, disposal of debris and all other labour necessary in and for the full and entire execution and for the job in accordance with the contract documents, good practice and recognize principles.
d | Liabilities, obligations and risks arising out of Conditions of Contract.
e | All requirements of Specifications, whether such requirements are mentioned in the item or not. The Specifications and Drawings where available, are to be read as complimentary to and part of the Schedule of Quantities and any work called for in one shall be taken as required for all.
f | BOQ shall be read in conjuction with technical specification, drawings,In the event of conflict between Bill of Quantities and other documents including the Specifications and drawings, the most stringent shall apply. The interpretation of the Consultant/Project Manager shall be final and binding.
12 | The Contractor shall procure and bring Materials/Equipment to the site only on the basis of drawings approved for construction and shop drawings and not on the basis of Bill of Quantities which are approximate only. This also applies to the Contractor’s requisition for Owner supplied materials.
13 | The contractor shall cooperate with all trades and agencies working on the site. He shall make provision for hangers, sleeves, structural openings and other requirements well in advance to prevent hold up of progress of the construction schedule. All supports to the civil structure shall be provided with anchor fasteners.
14 | On award of the work, contractor shall submit a schedule of construction in the form i.e BAR chart for approval of the Project Manager.
15 | On award of the work the contractor shall be issued three (3) sets of consultant’s drawings. The drawings shall be the basis of contractor’s shop drawings.
16 | Shop drawings are detailed working drawings coordinated with other trading work, which incorporate the contractor’s details for execution of the work and incorporate equipment manufacturer’s details and dimensions to ensure that the same can be installed in the space provided.
17 | All shop drawings will be made on AutoCAD and colored prints has to be produced for site work.
18 | This Schedule shall be fully priced and the extensions and totals duly checked. The rates for all items shall be filled in INK including NIL items.
19 | No alteration whatsoever is to be made to the text or quantities of this Schedule unless such alteration is authorised in writing by Consultant. Any such alterations, notes or additions shall, unless authorized in writing, be disregarded when tender documents are considered.
20 | In the event of an error occurring in the amount of the Schedule, as a result of wrong extension of the unit rate and quantity, the unit rate quoted by the tenderer shall be regarded as firm and the extensions shall be amended on the basis of rates.
21 | Any error in totaling in the amount column and in carrying forward total shall be corrected. Any error, in description or in quantity, omission of items from this Schedule shall not vitiate this Contract but shall be corrected and deemed to be variation required by the Consultant/Project Manager.
22 | Rates have been called for a number of items of works, as alternatives which, for the present do not form part of the total value of tender. However the rates for these items shall be quoted, with due care so that in the event of choice of an alternative item of work, said rate shall form part of the contract and shall not violate the contract any way.
23 | The contractor shall , from time to time, clear away all debris and excess materials accumulated at the site failing which the same shall be done by Project Manager at contractor’s risk and cost and cost of clean up shall be deducted from the contractors prorata bill.
24 | After the devices and equipment have been installed and commissioned, contractor shall cleanup the same and remove all plaster, paints, stains, stickers and other foreign matter or discoloration leaving the same in a ready to use condition.
25 | On completion of all works, contractor shall demolish all stores, remove all surplus materials and leave the site in a broom clean condition, failing which the same shall be done by the Project Manager at the Contractor'’ risk and cost. Cost of the cleanup shall be deducted from the contractor’s bills on pro-rata basis in proportion to his contact value.
26 | Provision for scaffolding if any required at site , contactor shall need to be provided.
27 | Remove existing drain and water supply lines which are not required. Clean the site for new installations.