## F.F
S.No. | FIRE FIGHTING SYSTEM | UOA | Quantity | Rate | Amount
1 | Providing, laying, testing & commissioning of 'C' class heavy duty MS pipe conforming to IS 3589/IS 1239 including Welding, fittings like elbows, tees, flanges, tapers, nuts bolts, gaskets etc. and fixing the pipe on the wall/ceiling with suitable clamp/support frame and painting with two or more coats of synthetic enamel paint of required shade complete as required. (Make - SURYA PIPES/ JINDAL HISSAR/ TATA)
a) | 25 mm dia. | Mtr | 35 |  | 0
b) | 32 mm dia. | Mtr | 5 |  | 0
c) | 40 mm dia. | Mtr | 5 |  | 0
d) | 50 mm dia. | Mtr | 4 |  | 0
e) | 65 mm dia. | Mtr | RO
f) | 80 mm dia. | Mtr | RO
g) | 100 mm dia. | Mtr | RO
2 | Providing, fixing, testing and commissioning brass quartzoid sprinklers K-80 (UL-Underwriters Laboratories Listed) suitable for 175 psi(12 Bars) maximum working pressure and 7 psi(0.5 Bars) minimum operating pressure with 15 mm dia BSPT threaded opening complete in all respects. The type & temperature rating shall be as follows. (Make - SAFEX/ NEWAGE/ HD FIRE)
a) | Pendent Concealed Sprinklers Sprinkler (68°)- Quick response type | Each | 7 |  | 0
b) | Pendent Concealed Sprinklers Sprinkler (93°)- Quick response type | Each | RO
c) | Upright Sprinkler (68°)- Quick response type | Each | RO
3 | Supplying, installation, testing & commissioning of sprinkler flexible pipe (UL Listed) of stainless steel complete with 15 NPT on reducer thread with maximum working pressure of 175 PSI test pressure of 875 PSI (Burst) with branch line (Inlet) 25mm NPT male thread to sprinkler head (Outlet) 15mm NPT female thread with reducer, nipple, 2 side brackets, center bracket, stockbar of following sizes complete as required. (Make - SAFEX/ NEWAGE/ HD FIRE)
c) | 1500mm | Each | 7 |  | 0
d) | 2000mm | Each | RO
4 | Providing & Fixing Powder coated double plate rosette plate for pendent / side wall sprinkler where ever required. (Make - SAFEX/ NEWAGE/ HD FIRE) | Each | RO
5 | Wheel operated Butterfly Valves (PN 16) with inbuilt supervisory switch (UL listed and FM approved) with CI Body, Black Nitrile Body Liner and Nylon Coated SG Iron Disc with material and labour including hydraulic testing etc. complete as per drawing, specification & to the level of satisfaction of Site- Incharge.
a) | 50 mm dia | Each | 1 |  | 0
b) | 65 mm dia | Each | RO
7 | Providing, fixing, testing and commissioning of drain test assembly complete with pipe, drain valve, test valve, sight glass, union, tee, elbow etc. complete with bolts, nuts, gasket, washers etc. as per NBC | Each | 1 |  | 0
8 | Providing and fixing electrically operated flow indicating switches model system sensor in sprinkler branch line including tamper switch and accessories, complete with tap off socket arrangement as required with necessary junction box installed in accessible place including Wiring from switches to panel | Each | RO
| Total |  |  |  | 0