## HVAC
BILL OF QUANTITIES
PROJECT: | IN-DEL-GORDON RAMSAY | [5 empty] | DATE: | 2024-12-21
[7 empty] | REV: | R0
HVAC SERVICE - WORKS BILL OF QUANTITIES | [6 empty] | STATUS: | TENDER
GENERAL NOTES :
All measurements and figures provided below are indicative only and must be confirmed by the contractor. The contractor shall have full responsibility for measurements or surveys, and no additional costs or charges will be accepted. The scope of work and quantities mentioned in the MEP BOQ pertain to the MEP services only inside the site location (e.g., within the unit demise). If any termination or connection of services is required outside the site location (i.e., connection of the unit M&E to the airport M&E or service termination to the airport external façade or roof, etc.), then the contractor must plan, design, and detail these connections in consultation with the airport. The contractor is to do all necessary site surveys to verify the optimal routing for the services in such cases. The contractor shall include in their scope end point termination of all MEP points for equipment based on supplied equipment and airport regulations, No additional costs shall be claimable for end point terminations. Any service penetration inside the unit must be made good after installation, and any fire penetrations on site must be detailed as per Airport requirements. The contractor is to verify at the site and also with Airport authorities whether there are provisions at the site to suit the design. Example: The contractor should check for provisions and the extent of power, plumbing, chilled water, ducting, fire and gas provisions, etc. available at the site and satisfy himself that there are no risks to the design intent.
ITEM | DESCRIPTION | UNITS | QTY | MATERIAL COST |  | LABOUR COST |  | TOTAL AMOUNT
|  |  |  | UNIT COST | TOTAL | UNIT COST | TOTAL
|  |  |  | (INR) | (INR) | (INR) | (INR) | (INR)
A | CONNECTING / INTEGRATING UNIT MEP SERVICES TO AIRPORT MEP SERVICES/ BUILDING
A.1 | If any termination or connection of the unit services is required outside the site location (i.e., connection/termination of the MEP unit to the airport MEP service or airport external façade or roof, etc.), then the contractor has to work in consultation with the airport to plan, design, and detail such connections. The contractor is to do all necessary site surveys to verify the optimal routing for the services in such cases. Finally, the contractor is to make good on any penetrations after installation, including providing fire seals as required as per airport requirements. |  |  | Included
B | HVAC EQUIPMENTS
VENTILATION FANS
B.1 | Supply, Installation, Testing and Commissioning of Double Skinned ceiling suspended Kitchen Exhaust Air Fan of approved make with minimum 25 mm thick panels of minimum 40 Kg/m3 density with 0.60 mm precoated GSS outer skin and 0.60 plain inner skin, Motor shall be of IE 3, the fan motor should be located outside of the hot air stream, Class H insulation. Fans should be AMCA certified for Air & Sound. Manufacturer shall submit “Certificate of conformity for 250 deg for 2 hours operation as per EN12101-3: 2002 issued by Internationally recognized Independent Fire Laboratory should be submitted along with type test report. The Type test report should clearly indicate the make of motor used during the testing and the same make/model of motor should be supplied by the fan manufacture at the site. The unit shall be suitable for 400 ± 15 volts, 50 Hz, 3 phase AC supply. Including control panel and all necessary cabling and terminations. Quote shall be inclusive of all necessary mounting and fixing arrangements for the fan, including hanging arrangements with vibration isolation as required based on the site condition. Note : External Static Pressure (ESP) is calculated based on design drawing however contractor to select fan to match with actual pressure drop based on site condition. Pressure drop calculation and selection to be submitted to consultant for review / approval. The procurement shall be processed only after pressure drop calculations & selections duly verified from the consultants.
B.1.1 | 3500 CFM @ 600 PASCAL - ESP. | Nos | 1 |  | 0 |  | 0 | 0
B.2 | Supply, installation, testing and commissioning of Double Skinned Ceiling Suspended Air Washer Units of approved make with minimum 25 mm thick panels of minimum 40 Kg/m3 density with 0.60 mm precoated GSS outer skin and 0.60 plain inner skin, filter section with EU4 Pre Filter, mist eliminator located on the air leaving end, drain tank shall be 20 gauge SS304 grade, inlet makeup & overflow connections with pump also considered. Fan shall be ACMA certified direct driven backward curved Plenum plug fan with aerofoil design blades including control panel. The Fan shall be suitable for 400 ± 15 volts, 50 Hz, 3 phase AC supply. Quote shall be inclusive of all necessary mounting and fixing arrangements for the equipment, including hanging arrangements with vibration isolation as required based on the hanging structure above. Note : External Static Pressure (ESP) is calculated based on design drawing however contractor to select fan to match with actual pressure drop based on site condition. Pressure drop calculation and selection to be submitted to consultant for review / approval. The procurement shall be processed only after pressure drop calculations & selections duly verified from the consultants.
B.2.1 | 2800 CFM @ 300 PASCAL - ESP. | Nos | 1 |  | 0 |  | 0 | 0
AIR CLEANING EQUIPMENTS
B.3 | Supply, installation, testing and commissioning of Double Skinned ceiling suspended Dry Scrubber of approved make with minimum 25 mm thick panels of minimum 40 Kg/m3 density with 0.60 mm precoated GSS outer skin and 0.60 plain inner skin, including EU4 Pre Filter, ionizer, collection plate .The Unit shall be suitable for 230V, 1 Phase, 50 Hz AC supply. Auto power cut-off when door is opened, short circuit, arc protection and auto restore power supply, Quote shall be inclusive of all necessary mounting and fixing arrangements for the equipment, including hanging arrangements with vibration isolation as required based on the hanging structure above.
B.3.1 | 3500 CFM | Nos | 1 |  | 0 |  | 0 | 0
C | AC PIPING AND ACCESSORIES
AC CONDENSATE DRAIN PIPE
C.1 | Supply, installation and testing of Rigid uPVC drain water piping of approved make with necessary supports and fittings like, U-traps, elbows, tees and reducers.
C.1.1 | 32 mm Ø | Mtr | 8 |  | 0 |  | 0 | 0
D | AIR DISTRIBUTION DUCTS
RECTANGULAR DUCTS
D.1 | Supply, installation and testing of Galvanized Iron (GI)/ Galvanized Steel (GS) 120GSM Zinc coated factory fabricated Square / Rectangular Ducts of approved make with all necessary fittings, connections, vanes, flanges, bracings, gaskets, duct collars, splitter dampers, and all necessary duct supports like MS Angle bars, slotted rails, threaded rods, anchor bolts, nuts, bolts, structural beam clamps as applicable. The ducts shall be fabricated and installed in line with SMACNA or DW-144 as required by Airport / local regulatory or approval body having jurisdiction.
D.1.1 | 24 Gauge - (0.70 mm Thick) - Supply Air Duct | Sq.mtr | 55 |  | 0 |  | 0 | 0
D.1.2 | 24 Gauge - (0.70 mm Thick) - Return Air Duct | Sq.mtr | 6 |  | 0 |  | 0 | 0
D.1.3 | 24 Gauge - (0.70 mm Thick) - Fresh Air Duct | Sq.mtr | 45 |  | 0 |  | 0 | 0
D.1.4 | 22 Gauge - (0.85 mm Thick) - Fresh Air Duct | Sq.mtr | 4 |  | 0 |  | 0 | 0
D.2 | Supply, installation and testing of Mild Steel (MS) Ducts fabricated with hot rolled or cold rolled black steel sheets Square / Rectangular Ducts of approved make with fully welded leak proof construction with Fire rated spay coat conforming to NFPA 96 Standards. with all necessary fittings, connections, vanes, flanges, bracings, gaskets, duct collars, splitter dampers, and all necessary duct supports like MS Angle bars, threaded rods, anchor bolts, nuts, bolts, structural beam clamps as applicable. Duct and all other accessories shall be fire resistant, The ducts shall be fabricated and installed in line with SMACNA or DW-144 as required by Airport / local regulatory or approval body having jurisdiction.
D.2.1 | 18 Gauge - (1.21 mm Thick) - Kitchen Exhaust Air Duct | Sq.mtr | 39 |  | 0 |  | 0 | 0
ROUND DUCTS
D.3 | Supply, installation, and testing of Galvanized Iron (GI)/ Galvanized Steel (GS) 120GSM Zinc coated factory fabricated Round Ducts of approved makes with all necessary fittings, round connectors, duct collars, splitter dampers, and all necessary duct supports like MS Angle bars, slotted rails, threaded rods, anchor bolts, nuts, bolts, structural beam clamps as applicable. The ducts shall be fabricated and installed in line with SMACNA or DW-144 as required by Airport / local regulatory or approval body having jurisdiction.
D.3.1 | 24 Gauge - (0.70 mm Thick) - Supply Air Duct | Sq.mtr | 7 |  | 0 |  | 0 | 0
DUCT ACCESS DOORS
D.4 | Supply, installation, and testing of Hinged type Duct Access Doors as per drawings and to allow easy and convenient access to equipment or any other component within ductwork with all necessary fittings, accessories and airtight gaskets etc.
D.4.1 | 300 mm X 300 mm - (MS) | Nos | 5 |  | 0 |  | 0 | 0
FLEXIBLE DUCTS
D.5 | Supply, installation, and testing of aluminum-polyester casing Round Insulated Flexible Duct of approved make reinforced with spiral wound steel wire, Temperature range -20° C to +140° C, with a standard Insulation with a 25mm thick mineral wool, covered with aluminum-polyester film casing and with all necessary connections, fixing and support arrangements.
D.5.1 | 250 mm Ø | Mtr | 5 |  | 0 |  | 0 | 0
D.6 | Supply, installation, and testing of Flexible Duct Connectors (Canvas connection) of approved make to isolate vibrations and noises caused by fans or any other equipment's connected to the duct with air tight fittings with all necessary accessories.
D.6.1 | For Air Washer Unit | Nos | 2 |  | 0 |  | 0 | 0
D.6.2 | For Kitchen Exhaust air Fan | Nos | 2 |  | 0 |  | 0 | 0
E | AIR DISTRIBUTION DUCT - THERMAL INSULATIONS & ACCOUSTIC LINNINGS
AIR DISTRIBUTION DUCT - THERMAL INSULATIONS
E.1 | Supply, installation of Thermal Insulation of approved make for duct insulation using closed-cell elastomeric nitrile rubber Class 'O' rated as per BS 476 Part 6: 1989 for fire propagation test and for Class 1 as per BS 476 Part 7, 1987 for surface spread of flame test. Water vapour permeability shall be not less than 0.024 per inch (2.48 x 10-13 Kg/m.s.Pa i.e. μ>7000: Water Vapor diffusion resistance) as per DIN 53122 part 2, DIN 52615 / EN 12086 & EN13469. Insulaton shall be black Colour with having a density of 50 ± 10 Kg/M3. Quote shall be inclusive of necessary Adhesive.
E.1.1 | 25 mm thicknesses | Sq.mtr | 117 |  | 0 |  | 0 | 0
E.2 | Supply, installation of Thermal Insulation of approved make for Kitchen exhaust ducting using Resin Bonded Fibre Glass Wool (Asbestos Free) with Aluminum Foil covering, density of not less than 48 Kg/m3. Quoute shall be inclusive of necessary Adhesive.
E.2.1 | 80 mm thicknesses - For Kitchen Exhaust | Sq.mtr | 39 |  | 0 |  | 0 | 0
F | AIR DISTRIBUTION DUCT - DAMPERS
DUCT AIR CONTROL DAMPERS
F.1 | Supply, installation, testing and commissioning of aluminum powder coated Opposed Blade Damper / Collar Damper of approved make.
F.1.1 | Size - 300 x 300 mm | Nos | 9 |  | 0 |  | 0 | 0
F.1.2 | Size - 375 x 375 mm | Nos | 4 |  | 0 |  | 0 | 0
F.2 | Supply, installation, testing and commissioning of Aluminium powder coated Low Leakage Square / Rectangular Volume Control Damper of approved make with aero-foil opposed blades and nylon gears system outside air stream with adjustable handle with position arresting bolt.
F.2.1 | Size - 350 x 200 mm | Nos | 2 |  | 0 |  | 0 | 0
F.2.2 | Size - 550 x 250 mm | Nos | 2 |  | 0 |  | 0 | 0
F.2.3 | Size - 300 x 200 mm | Nos | 2 |  | 0 |  | 0 | 0
F.3 | Supply, installation, testing and commissioning of MS powder coated Low Leakage Square / Rectangular Volume Control Damper of approved make with aero-foil opposed blades and nylon gears system outside air stream with adjustable handle with position arresting bolt. (For Kitchen Exhaust MS duct)
F.3.1 | Size - 500 x 400 mm | Nos | 1 |  | 0 |  | 0 | 0
F.3.2 | Size - 450 x 250 mm | Nos | 4 |  | 0 |  | 0 | 0
F.4 | Supply, installation, testing and commissioning of Circular Volume Control Damper of approved make with high quality Galvanized steel and Flap Blade fixed with nylon bushes, with hand locking quadrant.
F.4.1 | Size - 250 mm Ø | Nos | 2 |  | 0 |  | 0 | 0
G | AIR TERMINALS - (GRILLES, REGISTERS, DIFFUSERS & LOUVERS)
DIFFUSERS
G.1 | Supply, installation, testing and commissioning of Extruded Aluminium Square Ceiling Diffuser of approved make with Four way throw with all necessary fixing arrangements. Powder coated finish with RAL Colour as required by ID Designer / Architect.
G.1.1 | Neck Size - 300 mm X 300 mm (Outer Size - 440 mm X 440 mm) | Nos | 17 |  | 0 |  | 0 | 0
G.1.2 | Neck Size - 375 mm X 375 mm (Outer Size - 600 mm X 600 mm) | Nos | 4 |  | 0 |  | 0 | 0
H | DISMANTLING OF EXISTING DUCTS
H.1 | Remove and dispose of the existing supply air duct branch, fittings, insulation, and supports etc. and install new duct sections to match the new design, including necessary supports and hangers.
H.1.1 | Dismantling of existing ducts | Lot | 1 |  | 0 |  | 0 | 0
J | HVAC SERVICE IDENTIFICATION LABELS, SIGNS & TAGS
J.1 | All services like Ducts, Pipes need to be clearly labelled or tagged at site with service identification flow direction etc. And all equipment needs to tagged as per Airport requirements.
J.1.1 | Labelling & Tagging for Services and Equipment's | Lot | 1 |  | 0 |  | 0 | 0
K | TESTING AND BALANCING
K.1 | Air balancing of Supply, Return, Fresh air and Exhaust air system to arrive as per design air flow rates |  |  | Lumpsum
L | SHOP DRAWINGS & APPROVALS
L.1 | Preparation and submission of a detailed shop drawing for the HVAC system after a thorough study of design drawings, site surveys, and relevant airport standards with correct routing, size, and elevations. The drawings also need to be coordinated with other MEP services like Electrical, Plumbing, and fire services, with the latest Architectural and Interior design drawings, before construction. Necessary amendments to the drawings are to be made and resubmitted in case of any variations on site while at the construction stage of the project. Also prepare relevant detailed connection drawings as per selected manufacturer details and Airport standards, with necessary approval to be obtained from consultants and authority/regulatory bodies having jurisdiction, along with material submission approval with airport authorities. |  |  | Lumpsum
M | MISCELLANEOUS OR ANY ADDITIONAL ITEMS
M.1 | The contractor needs to mention any additional items or missing items that are not mentioned in the above BOQ after a detailed site survey or inspection and to be validated by consultants.
M.1.1 | Item 1 - (Contractor to describe only if there are any) | Unit | 1 |  | 0 |  | 0 | 0
M.1.2 | Item 2 - (Contractor to describe only if there are any) | Unit | 1 |  | 0 |  | 0 | 0
M.1.3 | Item 3 - (Contractor to describe only if there are any) | Unit | 1 |  | 0 |  | 0 | 0
GRAND TOTAL
Note : This BOQ is issued for costing purposes only; necessary corrections or amendments are to be made based on selected items, manufacturer details, site conditions, airports, and local regulatory or approval bodies having jurisdictional requirements and necessary approvals to be made for equipment's and material submission prior to procurement. The quantities mentioned in the above BOQ include services only inside the site location (building). If any termination of services is required outside the site location, the contractor must verify at the site and provide the quantity and cost over and above this BOQ.
General Guidelines: |  | General Guidelines:Ducting:1) Ducting shall be in accordance with IS 655, Galvanised Iron sheet to be used for all ducting works. Thermal insulation on ducts shall be 19 mm thick. Closed cell Class “O” BS 476 Part 6-7 FM Approved nitrile rubber elastomeric insulation thermal conductivity 0.033 watts per meter-kelvin (W/(M⋅K)) at 0°C for air conditioning ducting. 2) Thermal insulation on kitchen exhaust ducting shall be 80 mm thick Aluminium foil faced resin bonded fiber Glass wool of density not less than 48 kg/m33) Thermal Insulation on Fresh air, Supply Air and Return Air shall be 19mm thick closed cell antimicrobial Class “O” BS 476 and part 6 & 7 FM approved nitrile rubber elastomeric insulation thermal conductivity 0.033 watts per meter-kelvin (W/ (M⋅K)) at 0°C.4) Appropriate number of trap doors shall be provided in kitchen exhaust ducting for oil/grease cleaning purpose.5) Ducting installation with respect to fresh air intake, kitchen exhaust out from location up to louvers at façade shall be in the scope of concessioner including air washer, exhaust fan section dry scrubber etc.6) Each and every kitchen exhaust hood should be equipped with UL listed, wet chemical based, mechanically operated, automatic fire suppression system. Separate drawing to be submitted for Hood suppression system.8) Post completion of onsite work, concessionaire has to share testing and commissioning report with DIAL.9) Integration with Fire alarm system, so that AHU get switched off in case of any fire incident. 7) Supporting of ducting to be done with using angle 50x 50 x 5mm and tie rod of size minimum 10 mm dia/ As per duct size.10) For equipment placement structural details to be approved by structural consultant and same to be share with DIAL.11) Trap door with proper access to be provided for filter and copper coil cleaning.12) Kitchen ventilation shall comply to NFPA 96 guideline.Chilled Water Piping:- 1. Chilled water piping shall be confirming to IS:1239 Part I class ‘C’ heavy and fitting shall be conforming to ASTM A-105,3000lbs socket weld end (up to 50mm) & 1S:1239 Part-II HEAVY/ASTM A-234 WPB, Gr.B butt weld fitting ( above 50nb pipe size)2. Piping connection should be socket welded up to 50nb size and shall be butt weld above 50nb pipe size. Pipe flanges should be confirming to ASTM A-105 # 150 SORF and flange dimension should be in accordance with ASME/ANSI B 16.5 (150 SORF), fitting to fitting welding is not allowed. Nozzle connections/thredolets/weldolets are not allowed by puncturing the pipe. Only equal/unequal Tee’s shall be used for branch connection from header. Socket weld end Tee should be used for branch connection (up-to -50nb pipe size) w.r.t to pressure gauge/temperature gauge/Air vent/Drain point etc.3. Post installation clearance by DIAL, CHW piping shall be tested @15kgf/cm2 hydrostatics pressure for 24hrs hold time and Testing should be witnessed to DIAL Team.4. Thermal insulation on CHW and condensate drain piping line shall be 25mm thick. Closed cell antimicrobial Class “O” BS 476 and part 6 & 7 FM approved nitrile rubber elastomeric insulation thermal conductivity 0.033 watts per meter-kelvin (W/ (M⋅K)) at 0°C.5. Condensate drain piping shall be complying to IS 4985 Class 3 UPVC pipe. Solvent cement complying with ASTM D2564 shall be used for joints.6. For ceiling suspended chilled water pipe: Pipe should be hanged with tie rod of size minimum 10 mm dia. 7. Attached CHW P&ID drawing/sketch to be followed during onsite work.
Ducting:
1) Ducting shall be in accordance with IS 655, Galvanised Iron sheet to be used for all ducting works. Thermal insulation on ducts shall be 19 mm thick. Closed cell Class “O” BS 476 Part 6-7 FM Approved nitrile rubber elastomeric insulation thermal conductivity 0.033 watts per meter-kelvin (W/(M⋅K)) at 0°C for air conditioning ducting.
2) Thermal insulation on kitchen exhaust ducting shall be 80 mm thick Aluminium foil faced resin bonded fiber Glass wool of density not less than 48 kg/m3
3) Thermal Insulation on Fresh air, Supply Air and Return Air shall be 19mm thick closed cell antimicrobial Class “O” BS 476 and part 6 & 7 FM approved nitrile rubber elastomeric insulation thermal conductivity 0.033 watts per meter-kelvin (W/ (M⋅K)) at 0°C.
4) Appropriate number of trap doors shall be provided in kitchen exhaust ducting for oil/grease cleaning purpose.
5) Ducting installation with respect to fresh air intake, kitchen exhaust out from location up to louvers at façade shall be in the scope of concessioner including air washer, exhaust fan section dry scrubber etc.
6) Each and every kitchen exhaust hood should be equipped with UL listed, wet chemical based, mechanically operated, automatic fire suppression system. Separate drawing to be submitted for Hood suppression system.
7) Supporting of ducting to be done with using angle 50x 50 x 5mm and tie rod of size minimum 10 mm dia/ As per duct size.
8) Post completion of onsite work, concessionaire has to share testing and commissioning report with DIAL.
9) Integration with Fire alarm system, so that AHU get switched off in case of any fire incident.
10) For equipment placement structural details to be approved by structural consultant and same to be share with DIAL.
11) Trap door with proper access to be provided for filter and copper coil cleaning.
12) Kitchen ventilation shall comply to NFPA 96 guideline.
Chilled Water Piping:-
1. Chilled water piping shall be confirming to IS:1239 Part I class ‘C’ heavy and fitting shall be conforming to ASTM A-105,3000lbs socket weld end (up to 50mm) & 1S:1239 Part-II HEAVY/ASTM A-234 WPB, Gr.B butt weld fitting ( above 50nb pipe size)
2. Piping connection should be socket welded up to 50nb size and shall be butt weld above 50nb pipe size. Pipe flanges should be confirming to ASTM A-105 # 150 SORF and flange dimension should be in accordance with ASME/ANSI B 16.5 (150 SORF), fitting to fitting welding is not allowed. Nozzle connections/thredolets/weldolets are not allowed by puncturing the pipe. Only equal/unequal Tee’s shall be used for branch connection from header. Socket weld end Tee should be used for branch connection (up-to -50nb pipe size) w.r.t to pressure gauge/temperature gauge/Air vent/Drain point etc.
3. Post installation clearance by DIAL, CHW piping shall be tested @15kgf/cm2 hydrostatics pressure for 24hrs hold time and Testing should be witnessed to DIAL Team.
4. Thermal insulation on CHW and condensate drain piping line shall be 25mm thick. Closed cell antimicrobial Class “O” BS 476 and part 6 & 7 FM approved nitrile rubber elastomeric insulation thermal conductivity 0.033 watts per meter-kelvin (W/ (M⋅K)) at 0°C.
5. Condensate drain piping shall be complying to IS 4985 Class 3 UPVC pipe. Solvent cement complying with ASTM D2564 shall be used for joints.
6. For ceiling suspended chilled water pipe: Pipe should be hanged with tie rod of size minimum 10 mm dia.
7. Attached CHW P&ID drawing/sketch to be followed during onsite work.