## Fire Sprinkler
BILL OF QUANTITIES
PROJECT: | IN-DEL-GORDON RAMSAY | [5 empty] | DATE: | 2024-12-21
[7 empty] | REV: | R0
FIRE SERVICES - WORKS BILL OF QUANTITIES AND ESTIMATE | [6 empty] | STATUS: | TENDER
GENERAL NOTES :
All measurements and figures provided below are indicative only and must be confirmed by the contractor. The contractor shall have full responsibility for measurements or surveys, and no additional costs or charges will be accepted. The scope of work and quantities mentioned in the MEP BOQ pertain to the MEP services only inside the site location (e.g., within the unit demise). If any termination or connection of services is required outside the site location (i.e., connection of the unit M&E to the airport M&E or service termination to the airport external façade or roof, etc.), then the contractor must plan, design, and detail these connections in consultation with the airport. The contractor is to do all necessary site surveys to verify the optimal routing for the services in such cases. The contractor shall include in their scope end point termination of all MEP points for equipment based on supplied equipment and airport regulations, No additional costs shall be claimable for end point terminations. Any service penetration inside the unit must be made good after installation, and any fire penetrations on site must be detailed as per Airport requirements. The contractor is to verify at the site and also with Airport authorities whether there are provisions at the site to suit the design. Example: The contractor should check for provisions and the extent of power, plumbing, chilled water, ducting, fire and gas provisions, etc. available at the site and satisfy himself that there are no risks to the design intent.
ITEM | DESCRIPTION | UNITS | QTY | MATERIAL COST |  | LABOUR COST |  | TOTAL AMOUNT
|  |  |  | UNIT COST | TOTAL | UNIT COST | TOTAL
|  |  |  | (INR) | (INR) | (INR) | (INR) | (INR)
A | CONNECTING / INTEGRATING UNIT MEP SERVICES TO AIRPORT MEP SERVICES/ BUILDING
A.1 | If any termination or connection of the unit services is required outside the site location (i.e., connection/termination of the MEP unit to the airport MEP service or airport external façade or roof, etc.), then the contractor has to work in consultation with the airport to plan, design, and detail such connections. The contractor is to do all necessary site surveys to verify the optimal routing for the services in such cases. Finally, the contractor is to make good on any penetrations after installation, including providing fire seals as required as per airport requirements. |  |  | Included
C | FIRE SPRINKLER SYSTEM
AUTOMATIC FIRE SPRINKLER HEADS & ACCESSORIES
C.1 | Supply, Installation, Testing & Commissioning of Automatic Fire Sprinkler Heads (Bulb-type Sprinklers) of approved make with a standard temperature response with 5mm glass bulb, Temperature rating of 68° C / 93° C, Nominal Thread size of 1/2" NPT (15mm) and a Orifice size of 13mm with a Max. Working Pressure of 12 Bar (Factory hydrostatic test pressure of 35 Bar) and to be Manufactured & Certified to UL 199. The quote shall also include suspending arrangements with the ceiling, wall etc.
C.1.1 | Pendant type of 79° C (Finishing - Chrome Plated) | Nos | 4
C.2 | Supply, Installation, Testing & Commissioning of Automatic Concealed Fire Sprinkler Heads (Bulb-type Sprinklers) of approved make with adjustable Escutcheon plates (Rosette plates). standard temperature response with 5mm glass bulb, Temperature rating of 68° C, Nominal Thread size of 1/2" NPT (15mm) and an Orifice size of 13mm with a Max. Working Pressure of 12 Bar (Factory hydrostatic test pressure of 35 Bar) and to be Manufactured & Certified to UL 199. The quote shall also include suspending arrangements with the ceiling, wall etc.
C.2.1 | Concealed Pendant type of 68° C (Chrome Finish Plate Cover) | Nos | 25 |  | 0 |  | 0 | 0
C.3 | Supply, Installation, Testing & Commissioning of Automatic Fire Sprinkler Heads (Bulb-type Sprinklers) of approved make with a standard temperature response with 5mm glass bulb, Temperature rating of 68° C / 93° C, Nominal Thread size of 1/2" NPT (15mm) and a Orifice size of 13mm with a Max. Working Pressure of 12 Bar (Factory hydrostatic test pressure of 35 Bar) and to be Manufactured & Certified to UL 199. The quote shall also include suspending arrangements with the ceiling, wall etc.
C.3.1 | Upright type of 68° C (Finishing - Chrome Plated) | Nos | 5 |  | 0 |  | 0 | 0
FIRE SPRINKLER PIPING
C.4 | Supply, Installation, Testing & Commissioning of MS "C" Class Fire Sprinkler Pipe confirming to IS: 1239 with all fittings like bends, tees, flanges, nut, bolt and washers etc, and proper pipe supports to not more than 3 meter apart of the pipe length. The pipe work shall be hydrostatically tested for not less than 2 hours at 15 Bar (or 1.5 times the working) pressure without leak. The pipes are to be applied with 2 coats of primer (indicated film thickness, dry 50 microns) and 2 coats of enamel finish paint of approved colour (indicated film thickness, dry 30 microns)
C.4.1 | 25 mm Dia | Mtr | 10
C.4.2 | 32 mm Dia | Mtr | 5
C.4.3 | 50 mm Dia | Mtr | 8
C.5 | Supply & Fixing of UL Listed Stainless Steal Braided Flexible Sprinkler Hose with a working pressure of 12 Bar, Inlet Nipple(1" (25mm) BSPT/ NPT connection),Outlet Reducer (1/2" (15mm) BSPT / NPT connection), Isolation Ring, Gasket, Snap Clamp, T-bar bracket (TBL or TBS),Stock bar and Nuts etc.
C.5.1 | Assembly Length of (1500 mm) | Nos | 29
D | FIRE EXTINGUISHERS
D.1 | DRY POWDER STORED FIRE EXTINGUISHER
D.1.1 | Supply and fixing of 4 KG ABC Dry Powder (Stored Pressure) Type Fire Extinguisher. pressurized with dry nitrogen gas at 15 bar. Design, construction and testing as per IS 15683 with BIS Fire rating 2A : 21B, Body Hydrotested at 35 bar, Operating temperature -30°C to +55°C, external epoxy powder coating with PO Red Shade No. 538 of IS 5, Supplied with standard accessories. | Nos | 7 |  | 0 |  | 0 | 0
D.2 | CO2 PORTABLE FIRE EXTINGUISHER
D.2.1 | Supply and fixing of 4.5 KG CO2 (Carbon-dioxide type) of approved make Fire Extinguisher. Design, construction and testing as per local Fire Authority Rating, Body Hydrotested at 250 bar, Operating temperature -30°C to +55°C, external epoxy powder coating with PO Red Shade, Supplied with standard accessories. | Nos | 2 |  | 0 |  | 0 | 0
D.3 | K CLASS STORED PRESSURE FIRE EXTINGUISHER WITH SS BODY
D.3.1 | Supply and fixing of 6 Ltr Class K wet chemical Type Fire Extinguisher of approved make and as per local Fire authority Rating, Pressurized with nitrogen gas at 10 bar and body Hydrotested at 35 bar, Operating temperature +5°C to +60°C, Supplied with standard accessories. | Nos | 2 |  | 0 |  | 0 | 0
D.4 | FIRE EXTINGUISHER MOUNTING BRACKET / MOUNTING STAND
D.4.1 | Supply and fixing of Mounting Bracket / Stand for Fire Extinguishers fabricated out of good quality M.S, Pipe / Plate & Fittings duly painted with primer and final enamel paint coat as per the regulatory authority or to match with the ID design to suit the above Fire Extinguishers. | Nos | 11
D.5 | FIRE BLANKET
D.5.1 | Supply and fixing of wall mounted Fire Blanket with Fire Blankets of approved make made up of a Fire-retardant material, folded and packaged in a quick-release contraption for easier storage as per local Fire Authority regulations, Supplied with standard accessories. | Nos | 2 |  | 0 |  | 0 | 0
E | KITCHEN EXHAUST HOOD FIRE SUPPRESSION SYSTEM
E.1 | Detail Design, Supply, Installation, Testing & Commissioning of Kitchen Hood Fire Suppression System of approved make should be provided by specialist vendor as per local Fire Authority regulations. Supplied with standard accessories.
E.1.1 | For Kitchen Exhaust Hood | Nos | 1 |  | 0 |  | 0 | 0
F | DISMANTLING OF EXISTING FIRE SPRINKLER PIPES
F.1 | Remove and dispose of the existing fire sprinkler pipe branch, fittings and supports etc. and install new fire sprinkler pipe sections to match the new design, including necessary supports.
F.1.1 | Dismantling of existing fire sprinkler pipe | Lot | 1 |  | 0 |  | 0 | 0
G | TESTING AND BALANCING
G.1 | Checking the functionality of all installed devices, conducting alarm tests, verifying proper communication between control panels and devices, and other systems. Testing should be done in the presence of Airport Concerned Persons. |  |  | Lumpsum
G.2 | Sprinkler pipe Pressure testing hydrostatic pressure test of no less than 14 bar (200PSI) for 2 hours with zero loss in pressure at the reference gauge or visual observation of a leak. Testing should be done in the presence of Airport Concerned Persons. |  |  | Lumpsum
G.3 | Ensure all extinguishers are properly labelled, mounted, and ready for use. Training for staff on correct usage should be included. Testing should be done in the presence of Airport Concerned Persons. |  |  | Lumpsum
H | SHOP DRAWINGS & APPROVALS
H.1 | Preparation and submission of a detailed shop drawing for the Fire Detection & Fire Protection systems after a thorough study of design drawings, site surveys, and relevant airport standards with correct routing, size, and elevations. The drawings also need to be coordinated with other MEP services like HVAC, Electrical and Plumbing, with the latest Architectural and Interior design drawings, before construction. Necessary amendments to the drawings are to be made and resubmitted in case of any variations on site while at the construction stage of the project. Also prepare relevant detailed connection drawings as per selected manufacturer details and Airport standards, with necessary approval to be obtained from consultants and authority/regulatory bodies having jurisdiction, along with material submission approval with airport authorities. |  |  | Lumpsum
J | MISCELLANEOUS OR ANY ADDITIONAL ITEMS
J.1 | The contractor needs to mention any additional items or missing items that are not mentioned in the above BOQ after a detailed site survey or inspection and to be validated by consultants.
J.1.1 | Item 1 - (Contractor to describe only if there are any) | Unit | 1 |  | 0 |  | 0 | 0
J.1.2 | Item 2 - (Contractor to describe only if there are any) | Unit | 1 |  | 0 |  | 0 | 0
J.1.3 | Item 3 - (Contractor to describe only if there are any) | Unit | 1 |  | 0 |  | 0 | 0
GRAND TOTAL
Note : This BOQ is issued for costing purposes only; necessary corrections or amendments are to be made based on selected items, manufacturer details, site conditions, airports, and local regulatory or approval bodies having jurisdictional requirements and necessary approvals to be made for equipment's and material submission prior to procurement. The quantities mentioned in the above BOQ include services only inside the site location (building). If any termination of services is required outside the site location, the contractor must verify at the site and provide the quantity and cost over and above this BOQ.