## Plumbing
BILL OF QUANTITIES
PROJECT: | IN-DEL-GORDON RAMSAY | [5 empty] | DATE: | 2024-12-21
[7 empty] | REV: | R0
PLUMBING - WATER SUPPLY & DRAINAGE SYSTEMS - WORKS BILL OF QUANTITIES | [6 empty] | STATUS: | TENDER
GENERAL NOTES :
All measurements and figures provided below are indicative only and must be confirmed by the contractor. The contractor shall have full responsibility for measurements or surveys, and no additional costs or charges will be accepted. The scope of work and quantities mentioned in the MEP BOQ pertain to the MEP services only inside the site location (e.g., within the unit demise). If any termination or connection of services is required outside the site location (i.e., connection of the unit M&E to the airport M&E or service termination to the airport external façade or roof, etc.), then the contractor must plan, design, and detail these connections in consultation with the airport. The contractor is to do all necessary site surveys to verify the optimal routing for the services in such cases. The contractor shall include in their scope end point termination of all MEP points for equipment based on supplied equipment and airport regulations, No additional costs shall be claimable for end point terminations. Any service penetration inside the unit must be made good after installation, and any fire penetrations on site must be detailed as per Airport requirements. The contractor is to verify at the site and also with Airport authorities whether there are provisions at the site to suit the design. Example: The contractor should check for provisions and the extent of power, plumbing, chilled water, ducting, fire and gas provisions, etc. available at the site and satisfy himself that there are no risks to the design intent.
ITEM | DESCRIPTION | UNITS | QTY | MATERIAL COST |  | LABOUR COST |  | TOTAL AMOUNT
|  |  |  | UNIT COST | TOTAL | UNIT COST | TOTAL
|  |  |  | (INR) | (INR) | (INR) | (INR) | (INR)
A | CONNECTING / INTEGRATING UNIT M&E SERVICES TO AIRPORT M&E SERVICES/ BUILDING
A.1 | If any termination or connection of the unit services is required outside the site location (i.e., connection/termination of the MEP unit to the airport MEP service or airport external façade or roof, etc.), then the contractor has to work in consultation with the airport to plan, design, and detail such connections. The contractor is to do all necessary site surveys to verify the optimal routing for the services in such cases. Finally, the contractor is to make good on any penetrations after installation, including providing fire seals as required as per airport requirements. |  |  | Included
B | DRAINAGE & VENT SYSTEMS
DRAINAGE EQUIPMENTS
B.1 | Installation and Testing of Grease Trap (Above Ground/floor) of approved make of 304-grade stainless steel material with interceptor body, perforated bucket, baffles, integral trap, inlet, and outlet pipe sleeve, and stainless steel interceptor cover with all necessary fittings & connectors, etc.
B.1.1 | 8 GPM - Flow Rate (0.30 LPS / 18 LPM) | Nos | 2 |  | 0 |  | 0 | 0
B.1.2 | 14 GPM - Flow Rate (0.46 LPS / 28 LPM) | Nos | 1 |  | 0 |  | 0 | 0
B.1.3 | 20 GPM - Flow Rate (0.63 LPS / 38 LPM) | Nos | 1 |  | 0 |  | 0 | 0
VALVES & ACCESSORIES
B.2 | Supply, Installation and Testing of Air Admittance Valve of approved make conforming to EN 12380, with an air admittance air flow rate of 6.1 LPS and a temperature range of operation from -20 ˚C to + 60 ˚C with all necessary adapters, fittings and connectors etc.
B.2.1 | 32 mm Dia | Nos | 4 |  | 0 |  | 0 | 0
DRAINS, TRAPS & CLEANOUTS
B.3 | Supply & installation of S.S Grating size, 300mm x 300mm, in 16 swg 25mm x25mm Square Pipe around the Frame and 20mmX 20mm Square pipe in center of frame with SS closed tray (304 SWR). Complete as per architectural detail drawing & Site Engineer's instruction. (100 mm Dia S.S 304 grade finish unions reducers/coupling or 75mm Dia S.S 304 grade finish unions reducers/coupling or 50mm Dia S.S 304 grade finish unions reducers/coupling)ntire Chamber will be made in 16 SWG SS 304 , Testing of Chamber as per DIAL Guideline
B.3.1 | 50 mm Dia - Outlet | Nos | 2 |  | 0 |  | 0 | 0
B.4 | Supply & installation of S.S Grating size, 250mm x 750mm, in 16 swg 25mm x25mm Square Pipe around the Frame and 20mmX 20mm Square pipe in center of frame with SS closed tray (304 SWR). Complete as per architectural detail drawing & Site Engineer's instruction. (100 mm Dia S.S 304 grade finish unions reducers/coupling or 75mm Dia S.S 304 grade finish unions reducers/coupling or 50mm Dia S.S 304 grade finish unions reducers/coupling)ntire Chamber will be made in 16 SWG SS 304 , Testing of Chamber as per DIAL Guideline
B.4.1 | 50 mm Dia - Outlet | Nos | 1 |  | 0 |  | 0 | 0
B.5 | Supply, Installation and Testing of uPVC Multi Floor Trap of approved make with stainless steel slotted top cover, flap, and air-tight cleaning eye, odor water seal trap with all necessary adapters, fittings, and connectors, etc.
B.5.1 | ( 3 Nos X 50 mm Dia - Inlet ) 75 mm Dia - Outlet | Nos | 1 |  | 0 |  | 0 | 0
B.6 | Supply, Installation and Testing of of uPVC 'P' Trap (self-cleaning type) of approved make with odor water seal trap with all necessary adapters, fittings and connectors, etc.
B.6.1 | 32 mm Dia - Outlet | Nos | 5 |  | 0 |  | 0 | 0
B.7 | Supply, Installation and Testing of Inspection Chamber of approved make with cast iron air tight cover plate with all necessary civil water proofing, gas tight rubber seal, perforated mesh, pipe inlet & outlet connections etc. construction details as advised by Airport authorities.
B.7.1 | 450 mm x 450 mm | Nos | 1 |  | 0 |  | 0 | 0
DRAINAGE & VENT SYSTEMS PIPING
B.8 | Supply, Installation and Testing of of uPVC Pipe of approved make conforming to IS 13592, for drainage with all necessary fittings such as bends, wye's, reducers, san tee's, double wye's, double combinations, san cross, and cleanout plugs etc, with all necessary supports/clamps for the above-raised floor pipes as per standards and site conditions/requirements.
B.8.1 | 32 mm Dia | Mtr | 8 |  | 0 |  | 0 | 0
B.8.2 | 40 mm Dia | Mtr | 10 |  | 0 |  | 0 | 0
B.8.3 | 50 mm Dia | Mtr | 28 |  | 0 |  | 0 | 0
B.8.4 | 75 mm Dia | Mtr | 1 |  | 0 |  | 0 | 0
TESTING & COMMISSIONING
B.9 | Water / Air Test for Drainage and Vent system pipes for leak detection
B.9.1 | The drainage and vent system shall be water/air tested with all openings in the piping tightly closed, except the highest opening to detect any water leakage in the system. The test is to be conducted after the complete installation of all drainage and vent system pipes and accessories as per the proposed design. | Set | 1 | Lumpsum
C | WATER SUPPLY SYSTEM
WATER SUPPLY EQUIPMENTS
C.1 | Supply, Installation, Testing, and commissioning of Electric Water Heater of approved make with safety valve arrangement and accessories like angle valve, flexible pipes, C.P bolts, screws, washers, etc. The unit shall be suitable for 230 ± 10 volts, 50/60 Hz, 1 phase AC supply and proper supports necessary as per standards and site condition/requirements.
C.1.1 | 30 Liters vertical storage water heater | Nos | 1 |  | 0 |  | 0 | 0
C.1.2 | 40 Liters horizontal storage water heater | Nos | 1 |  | 0 |  | 0 | 0
C.2 | Supply, Installation, Testing of Multi-Jet water meter of approved make conforming to IS: 779/94 and Class B of ISO: 4064, with Brass body and coupling, hermetically sealed water meter with magnetically driven totalizer, sealed against tampering, leakproof having dry dial, etc. and shall be operated with a working condition of water temperature upto 50°C and a Maximum pressure of 16 Bar.
C.2.1 | 25 mm Dia | Nos | 1 |  | 0 |  | 0 | 0
C.3 | Supply, Installation, Testing, and commissioning of RO Filter with inbuild pump of approved make of compact size for supplying pure filtered potable water to equipment like Combi-steamers & and baking ovens, Fresh water taps and coolers, Coffee/ Espresso machines, Post-mix machines, Ice-machines, and Boiling-water taps etc. with Indicating panel, Dust proof cover, filter cartridges, Pressure pump, mounting brackets, shutoff valves, flushing valves, pressure gauges, and suitable connectors etc. The final make, model, and details are to be finalized by the specialist vendor after examining the water test report of the incoming water supply provided at the site.
C.3.1 | 1.5 Ltrs / Min - Flow Rate | Nos | 1 |  | 0 |  | 0 | 0
WATER SUPPLY PIPE VALVES & ACCESSORIES
C.4 | Supply, Installation and Testing of Brass Ball Valve of approved make with full bore lever operated, SS ball and stem with a pressure rating of 16 Bar with all necessary fittings.
C.4.1 | 20 mm Dia | Nos | 2 |  | 0 |  | 0 | 0
C.4.2 | 25 mm Dia | Nos | 4 |  | 0 |  | 0 | 0
C.5 | Supply, Installation and Testing of chrome plated Angle Valve of approved make with wall flange/rosette for all plumbing equipment/fixtures with a pressure rating of 16 Bar with all necessary fittings. Including making good the wall/partition as per Architectural / Interior Design and as per relevant standards.
C.5.1 | 15 mm Dia Inlet (Outlet size to fit with plumbing eqp/fixture connection) | Nos | 17 |  | 0 |  | 0 | 0
C.5.2 | 20 mm Dia Inlet (Outlet size to fit with plumbing eqp/fixture connection) | Nos | 2 |  | 0 |  | 0 | 0
C.6 | Supply, Installation and Testing of Water Hammer Arrester of approved make with Factory air charged and permanently sealed for an Air pre-load of 4.2 Bar, Designed to operate at a working pressure of 10.6 Bar, and temperature range of 0.5°C to 82°C with all necessary fittings & connectors etc.
C.6.1 | 25 mm Inlet Dia | Nos | 3 |  | 0 |  | 0 | 0
COLD WATER SUPPLY PIPING
C.7 | Supply, Installation and Testing of (Chlorinated Poly Vinyl Chloride) CPVC Pipe of approved make conforming to IS 15778, ASTM D 2846, in SDR 11 Class 1, (temperature range of maximum 82°C) with all necessary fittings such as sockets, bends, elbows, tees, reducers, unions, etc, and proper supports were necessary as per standards and site condition/requirements.
C.7.1 | 15 mm Dia | Mtr | 12 |  | 0 |  | 0 | 0
C.7.2 | 20 mm Dia | Mtr | 15 |  | 0 |  | 0 | 0
C.7.3 | 25 mm Dia | Mtr | 27 |  | 0 |  | 0 | 0
HOT WATER SUPPLY / RETURN PIPING
C.8 | Supply, Installation and Testing of Copper Pipe of approved make conforming to BS 2871 / EN 1057, (continuous operating temperature range of maximum 90°C) with all necessary fittings such as sockets, bends, elbows, tees, reducers, unions, etc., and proper supports necessary as per standards and site condition/requirements.
C.8.1 | 15 mm Dia | Mtr | 11 |  | 0 |  | 0 | 0
C.8.2 | 22 mm Dia | Mtr | 20 |  | 0 |  | 0 | 0
PIPING THERMAL INSULATION
C.9 | Supply & fixing of Pipe Insulation 13 mm thick, with Polyethylene-based, closed-cell foam pipe insulation and polymer protective coating of approved make to prevent external mechanical damage for Hot water pipe with an operating temperature range of 0°C to 100°C, Thermal conductivity (λ) 0.038 W/m-K @ 40°C including suitable adhesives to fix the insulation to pipe.
C.9.1 | For 15 mm Pipe Dia | Mtr | 11 |  | 0 |  | 0 | 0
C.9.2 | For 22 mm Pipe Dia | Mtr | 20 |  | 0 |  | 0 | 0
D | PLUMBING SERVICE IDENTIFICATION LABELS, SIGNS & TAGS
D.1 | All services for pipes Like Type of water, pipe size, Flow direction need to be clearly labelled or tagged at site with service identification flow direction etc. And all equipment needs to tagged as per Airport requirements.
D.1.1 | Labelling & Tagging for Services and Equipment's | Lot | 1 |  | 0 |  | 0 | 0
E | TESTING & COMMISSIONING
E.1 | Water Quality Analysis Report
E.1.1 | Supplied incoming water samples are to be tested for pH value, Conductivity, TDS, Total Hardness, Mineral contents, Total Chlorine, Bacteria presence, color, odor, etc. to identify whether the supplied water is suitable for drinking purposes and also to finalize the selection/design of water filtration/treatment system. The test/analysis is to be conducted before any construction related to the water supply system at the site. | Set | 0
E.2 | Incoming water supply tap-off point water pressure and flow test
E.2.1 | Incoming water supply tap-off point water pressure is to be tested at the site to identify whether the water supply has sufficient pressure and flow to serve the remote end plumbing fixture/equipment with minimum flow pressure requirement to the fixture. (The proposed water supply design is based on the assumption that the supplied water has enough pressure and flow to serve the plumbing fixtures/equipment). The test is to be conducted prior to any construction related to the water supply system at the site. | Set | 1 | Included
E.3 | Pressure test for Water supply system pipes for leak detection
E.3.1 | Water supply system pipes are to be pressure tested at the site with a Test pressure / Head of 10 Bar for a duration of 24 Hours to detect any water leakage in the system. The test is to be conducted after the complete installation of all water supply system pipes and accessories as per the proposed design. | Set | 1 | Included
F | SHOP DRAWINGS & APPROVALS - DRAINAGE & WATER SUPPLY
F.1 | Preparation and submission of a detailed shop drawing for the Plumbing system after a thorough study of design drawings, site surveys, and relevant airport standards with correct routing, size, and elevations. The drawings also need to be coordinated with other MEP services like HVAC, Electrical, and fire services, with the latest Architectural and Interior design drawings, before construction. Necessary amendments to the drawings are to be made and resubmitted in case of any variations on site while at the construction stage of the project. Also prepare relevant detailed connection drawings as per selected manufacturer details and Airport standards, with necessary approval to be obtained from consultants and authority/regulatory bodies having jurisdiction, along with material submission approval with airport authorities. |  |  | Included
G | MISCELLANEOUS OR ANY ADDITIONAL ITEMS - DRAINAGE & WATER SUPPLY
G.1 | The contractor needs to mention any additional items or missing items that are not mentioned in the above BOQ after a detailed site survey or inspection and to be validated by consultants.
G.1.1 | Item 1 - (Contractor to describe only if there are any) |  |  |  | 0 |  | 0 | 0
G.1.2 | Item 2 - (Contractor to describe only if there are any) |  |  |  | 0 |  | 0 | 0
G.1.3 | Item 3 - (Contractor to describe only if there are any) |  |  |  | 0 |  | 0 | 0
GRAND TOTAL
Note : The quantities mentioned in the above BOQ include services only inside the site location (building). If any termination of services is required outside the site location, the contractor must verify at site and provide the quantity and cost over and above this BOQ. Any service penetration is to be made good after installation. Fire sealing is to be done for penetrations as per site requirements.
Water Supply: General comments |  | Water Supply: General commentsKindly note our water meter is digital which will be integrated with the BMS, so whatever cable will be installed during the shifting of water meter, will concessionaire scope.Water meter /Isolation valve shall have adequate space and access for maintenance of valve & water meter and taking reading of water meter and water meter power supply should be on UPS source.General Guidelines (Water Supply) .Water supply pipe laying for FOH, should be laid in niche with openable cover, for BOH it could be exposed. Supply Line installation check & leakage testing to be done, before connection with DIAL tapping point.Specification for Supply pipe- 1) CPVC ASTM D-2846 SDR-11 Class-1, CPVC solvent ASTM F-493 for normal waterFor Hot water: Copper pipe EN 1057 with thermal insulation. Thermal insulation shall be conforming to BS 476 Part 6&7 FM approved, Fittings BN-1254-1, Pipe installation in walls (except washroom and shower room) shall be through niches with openable SS cover.All materials/items to be used at site are subjected to prior inspection and approval from DIAL Engg. Data sheet with respect to all material need to be submitted for prior approval. Test certificate with respect to all material need to be submitted prior to installation during MIR Process.Make– Astral/Supreme for Pipe and Fittings.· All pipes should be installed freely from ceiling void area. Water Supply piping from floor is not allowed. Piping drops from ceiling inside BOH areas are recommended to be exposed on walls/partitions. In FOH areas, piping drops from ceiling can be installed through niche in walls with openable S.S. covers. Needs to be mentioned in drawing.· Existing Water Meter should be easily accessible.· Hydro-testing of pipe to be done at a pressure of 15Kgf/cm² for 24 hrs and get it inspected from DIAL- EnggWater meter /Isolation valve shall have adequate space and access for maintenance of valve & water meter and taking reading of water meter. Kindly share section drawing of same and water meter power supply should be on UPS source. Data Sheet, material inspection & Catalogue needs to be submitted for prior approval from DIAL-Engg.Kindly note our water meter is digital which will be integrated with the BMS, so whatever cable will be installed during the shifting of water meter, will concessionaire scope.General Guidelines (Drainage) . To be followed during execution workGrease trap Make shall be as per TDM and selection and backup calculation shall be as per TDM and have adequate space for opening of top cover for maintenance. Kindly share the details.Cleanout provisioning for maintenance and cleaning purpose to be provided.Water proofing for wet & Dry to be done as per TDM/Airport guideline.Pipe laying to be done within trench, and trench flooring should have openable cover.Power to be provided for existing Digital Water meter. Drain Line testing to be done, before connection with DIAL tapping point.Required JB/Openable trench cover/Grating/Floor trap/IC to be provided.Specification for Drain Pipe- uPVC IS:4985 Class 5 & IS:7834 Class 5 for fittings, uPVC solvent- ASTM D-2564, Makes – Astral/Supreme for Pipe and Fittings.Pipe installation in raised flooring should be through trench with openable cover.Each and every drain should go through Grease Traps. Only Condensate drain of HVAC Units are allowed to be conned without Grease Trap. Calculations w.r.t drain flow rate with grease capacity need to be submitted w.r.t selection of Grease Traps Capacities. Only S.S. Grease Traps are allowed. Data Sheet & Catalogue needs to be submitted for prior approval from DIAL-Engg. Size of IC should not be less than 600MMx600MM. S.S. grating with dia 5mm holes should be permanently welded inside IC at discharge end.Y- Connections to be provided instead of Tee in uPVC waste pipe.Note- Before execution, all Material inspection to be done along with TDS & required test certificates.Installation check to be done, before closing of ceiling & FlooringPost completion of onsite work, As Built Drawing to be submitted.DIAL Shared Guideline to be followed
Kindly note our water meter is digital which will be integrated with the BMS, so whatever cable will be installed during the shifting of water meter, will concessionaire scope.
Water meter /Isolation valve shall have adequate space and access for maintenance of valve & water meter and taking reading of water meter and water meter power supply should be on UPS source.
General Guidelines (Water Supply) .
Water supply pipe laying for FOH, should be laid in niche with openable cover, for BOH it could be exposed.
Supply Line installation check & leakage testing to be done, before connection with DIAL tapping point.
Specification for Supply pipe- 1) CPVC ASTM D-2846 SDR-11 Class-1, CPVC solvent ASTM F-493 for normal water
For Hot water: Copper pipe EN 1057 with thermal insulation. Thermal insulation shall be conforming to BS 476 Part 6&7 FM approved, Fittings BN-1254-1,
Pipe installation in walls (except washroom and shower room) shall be through niches with openable SS cover.
All materials/items to be used at site are subjected to prior inspection and approval from DIAL Engg. Data sheet with respect to all material need to be submitted for prior approval.
Test certificate with respect to all material need to be submitted prior to installation during MIR Process.
Make– Astral/Supreme for Pipe and Fittings.
· All pipes should be installed freely from ceiling void area. Water Supply piping from floor is not allowed. Piping drops from ceiling inside BOH areas are recommended to be exposed on walls/partitions. In FOH areas, piping drops from ceiling can be installed through niche in walls with openable S.S. covers. Needs to be mentioned in drawing.
· Existing Water Meter should be easily accessible.
· Hydro-testing of pipe to be done at a pressure of 15Kgf/cm² for 24 hrs and get it inspected from DIAL- Engg
Water meter /Isolation valve shall have adequate space and access for maintenance of valve & water meter and taking reading of water meter. Kindly share section drawing of same and water meter power supply should be on UPS source.
Data Sheet, material inspection & Catalogue needs to be submitted for prior approval from DIAL-Engg.
Kindly note our water meter is digital which will be integrated with the BMS, so whatever cable will be installed during the shifting of water meter, will concessionaire scope.
General Guidelines (Drainage) . To be followed during execution work
Grease trap Make shall be as per TDM and selection and backup calculation shall be as per TDM and have adequate space for opening of top cover for maintenance. Kindly share the details.
Cleanout provisioning for maintenance and cleaning purpose to be provided.
Water proofing for wet & Dry to be done as per TDM/Airport guideline.
Pipe laying to be done within trench, and trench flooring should have openable cover.
Power to be provided for existing Digital Water meter.
Drain Line testing to be done, before connection with DIAL tapping point.
Required JB/Openable trench cover/Grating/Floor trap/IC to be provided.
Specification for Drain Pipe- uPVC IS:4985 Class 5 & IS:7834 Class 5 for fittings, uPVC solvent- ASTM D-2564, Makes – Astral/Supreme for Pipe and Fittings.
Pipe installation in raised flooring should be through trench with openable cover.
Each and every drain should go through Grease Traps. Only Condensate drain of HVAC Units are allowed to be conned without Grease Trap. Calculations w.r.t drain flow rate with grease capacity need to be submitted w.r.t selection of Grease Traps Capacities. Only S.S. Grease Traps are allowed. Data Sheet & Catalogue needs to be submitted for prior approval from DIAL-Engg.
Size of IC should not be less than 600MMx600MM. S.S. grating with dia 5mm holes should be permanently welded inside IC at discharge end.
Y- Connections to be provided instead of Tee in uPVC waste pipe.
Note-
Before execution, all Material inspection to be done along with TDS & required test certificates.
Installation check to be done, before closing of ceiling & Flooring
Post completion of onsite work, As Built Drawing to be submitted.
DIAL Shared Guideline to be followed