## TechItemDoc
ItemCode | Item Name | UOM | Qty | Unit Price | Remarks
A | CONNECTING / INTEGRATING UNIT MEP SERVICES TO AIRPORT MEP SERVICES/ BUILDING
A.1 | If any termination or connection of the unit services is required outside the site location (i.e., connection/termination of the MEP unit to the airport MEP service or airport external façade or roof, etc.), then the contractor has to work in consultation with the airport to plan, design, and detail such connections. The contractor is to do all necessary site surveys to verify the optimal routing for the services in such cases. Finally, the contractor is to make good on any penetrations after installation, including providing fire seals as required as per airport requirements.
FIRE ALARM SYSTEM - DETECTION DEVICES
B.1 | Supply, Installation, Testing, and Commissioning of Addressable Type Optical Smoke Detector of approved make conforming by local fire authorities, with standard detector mounting Base, IP30 Ingress Protection, suitable area coverage (subject to local standard), 360° Angle Visibility, Operating Temperature (-10°C to +50°C), Approved by LPCB, with all necessary mounting and fixing arrangements.
B.1.1 | Optical Smoke Detector | Nos | 9
B.1.2 | Optical Smoke Detector (Above Ceiling) | Nos | 8
B.2 | Supply, Installation, Testing, and Commissioning of Addressable Type Fixed Temperature Heat Detector of approved make conforming by local fire authorities, with standard detector mounting base, IP30 Ingress Protection, suitable area coverage (subject to local standard), 360° Angle Visibility with suitable class approved by LPCB, with all necessary mounting and fixing arrangements.
B.2.1 | Heat Detector - 79°C fixed temperature | Nos | 2
B.2.2 | Heat Detector - 79°C fixed temperature (Above Ceiling) | Nos | 2
B.3 | Supply, Installation, Testing, and Commissioning of Addressable Type Manual Call Point Conforming to EN54 with Break glass, ABS material enclosure, IP30 Ingress Protection, Operating Temperature (-10°C to +50°C) of approved make along with suitable size 2 core cable clipped to structure/wall/ceiling / through GI or Heavy Duty PVC Conduits with suitable cable clips/saddles suitable for flush and surface mounting with all necessary mounting, termination and fixing arrangements.
B.3.1 | Manual Call Point - (Wall / Partition Mounted) | Nos | 1
FIRE ALARM SYSTEM - AUDIBLE AND VISUAL NOTIFICATION DEVICES
B.4 | Supply, Installation, Testing and commissioning of Addressable type Sounder Strobe with inbuilt Isolator & and operating temp (- 10 degrees to + 55 degrees) complete as required and duly approved by LPCB / EN54 along with suitable size 2 core cable clipped to structure/wall/ceiling / through GI or Heavy Duty PVC Conduits with suitable cable clips/saddles.
B.4.1 | Sounder Strobe - (Wall / Partition Mounted) | Nos | 1
B.5 | Supply, Installation, Testing, and Commissioning of Addressable Type Response Indicator of approved make conforming by local fire authorities with high bright LED, for Fire Detectors to indicate quickly the source of an alarm signal from detectors, which are not easily accessible or visible with IP30 Ingress Protection, Operating Temperature (-10°C to +50°C) approved by LPCB, with all necessary mounting and fixing arrangements.
B.5.1 | Response Indicator / Remote Indicator | Nos | 10
FIRE ALARM SYSTEM - MODULE DEVICES
B.6 | Supply, Installation, Testing, and Commissioning of Addressable Type Isolator Module of approved make to identify the shorted and de-wired detectors and devices in the circuit duly approved by LPCB / EN54, with all necessary mounting, termination and fixing arrangements.
B.6.1 | Isolator Module | Nos | 1
B.7 | Supply, Installation, Testing, and Commissioning of Addressable Type Control Module of approved make for connect other sources from fire Alarm Control Panel for evacuation purpose, Address Switch to program the modules, complete approved by LPCB / EN54, with all necessary mounting, termination and fixing arrangements.
B.7.1 | Control Module | Nos | 1
FIRE ALARM SYSTEM - CABLING
B.8 | Supply, Installation, Testing and Commissioning FRLS/ FP200 PVC insulated and PVC sheathed armoured multi-stranded Copper conductor of approved make RED coloured cable clipped to structure/wall/ceiling / through approved make GI or Heavy Duty PVC Conduits with suitable cable clips/saddles suitable for flush and surface mounting with all necessary mounting, termination, tap-off connections and fixing arrangements.
B.8.1 | 2C x 1.5 Sq. mm Cu Cable | Mtr | 130