## Summary-2 (hidden)
Summary
#REF!
S. No. | Description of Item | #REF!
|  | PO Amount | RA=-01
1 | Civil & Interior
a | DISMENTLING & CLEANING WORKS | #REF!
b | CIVIL WORK | #REF!
c | FLOORING WORK/CLADDING WORK | #REF!
d | DOOR WINDOW WORK | #REF!
e | OTHER WOOD WORK FOR WALL PANELLING, PARTITIONS & STORAGES | #REF!
f | FALSE CEILING WORK | #REF!
g | FINISHING WORK | #REF!
h | MISC WORK | #REF!
2 | Structural Steel | 546000
3 | Electrical Work
a | SUB-HEAD I WIRING | 2253020
b | SUB-HEAD II CABLES & RACEWAYS | 424200
c | SUB-HEAD III DISTRIBUTION BOARD & ELECTRICAL PANEL | 727650
d | SUB-HEAD IV FIRE DETECTION & PA SYSTEM | 519300
e | SUB-HEAD V CCTV SYSTEM | 114550
4 | PHE and FF
a | SANITARY FIXTURES AND FITTINGS | 538400
b | WATER SUPPLY | 97725
c | DRAINAGE | 94480
d | FIRE FIGHTING | 499170
5 | HVAC
a | DUCTWORK AND AIR DISTRIBUTION | 1148700
b | VENTILATION FANS AND ARRANGEMENT | 490000
6 | Furniture | 3636500
7 | Light Fixtures | 1905480
| Total Basic Amount (in Rs.) | #REF!
| GST @18% | #REF!
| Total Amount (in Rs.) | #REF!

## Inv Summary
Semolina Projects
Project : CIP Lounge, Lucknow
Details: Project invoicing AHU
PO No : Order Number : Semolina/PO/23-24/000754
CIP Lounge - Bill Summary
S.N | Item | PO Value | RA-01 Value | Cumulative | Varition ( In Amt ) | JMR status
1 | AHU WORK | 607280 | 602450 | 4830 | 602450 | Done
Total |  | 607280 | 602450 | 4830 | 602450
GST @ 18% |  | 109310.4 | 108441 | 869.4 | 108441
Grand Total |  | 716590.4 | 710891 | 5699.4 | 710891
Material advance amount=
Semolina Projects
Project : CIP Lounge, Lucknow
Details: Project invoicing AHU
PO No : Order Number :
CIP Lounge - Bill Summary
S.N | Item | PO Value | RA-02 Value | Cumulative | Varition ( In Amt ) | JMR status
1 | AHU EXTRA WORK QTY | 0 | 141265 | -141265 | 141265 | Done
Total |  | 0 | 141265 | -141265 | 141265
GST @ 18% |  | 0 | 25427.7 | -25427.7 | 25427.7
Grand Total |  | 0 | 166692.7 | -166692.7 | 166692.7
Material advance amount=

## Abstract AHU CIP Lounge
Company Name : | Semolina Kitchens Private Limited
Project Name : | AHU work for CIP Lounge at Terminal-03, CCSI Airport, Lucknow (Order Number : Semolina/PO/23-24/000754)
Sr No | Particulars | Code / Area Specified | Units | Qty | Impulse Branding |  | RA-01 |  | RA-02 Extra Qty |  | Cumulative |  | Variance
[5 empty] | Unit Price | Total Amount | QTY | Amount | QTY | Amount | QTY | Amount | QTY | Amount
1 | A. EQUIPMENT 1 Supplying, installing, testing and commissioning of double skin construction draw thru type AIR HANDLING UNITS (AHU) as per specification, each complete with following a) Supply air centrifugal fan with efficiency >60% b) Pre filter (MERV 8) and Bag Filter (MERV 13) in supply air stream. c) Six row deep cooling coil of copper tube and aluminum construction sized at maximum face velocity of 500 fpm. Cooling coil frame work and coil end plate shall be of SS304 construction. d) VFD designed for HVAC applications for supply air fan e) Squirrel cage induction motors IE-2 (EFF-1) suitable for 415 ± 10% volts, 50 Hz, AC supply meeting criterion as per ASHRAE standard 90.1-2013 and 90% or higher efficiency. f) Vibration isolators. g) Fan outlet velocity not exceeding 10 mps. h) Height of Ceiling Suspended AHU shall not exceed 700 mm. i) Minimum 30mm(WC) external static pressure shall be considered; however the total static pressure Motor rating shall be determined by contractor considering pressure drop across all accessories on supply air streams. j) Sound level at 1 m distance not exceeding 60 dB(A). TAG. SPACE LOCATION CFM TR SUGGESTED SUGGESTED NO. FEED STATIC PRESSURE MOTOR K.W. (MM W.G.) 1.1 AHU- Domestic ---- 6500 17 65 3.8 1 CIP Lounge 1 No. 1.00 382,950.00 382,950.00 Total
| AHU |  | Nos | 1 | 382950 | 382950 | 1 | 382950
A | AHU Amount |  |  |  |  | 382950 |  | 382950
2 | Supply, Installation, testing and commissioning of electronic, AUTOMATIC PRESSURE INDEPENDENT BALANCING VALVE type dynamic balancing Valve with integrated 2 way modulating Control valves in a single body. The actuator shall be capable of accepting 2-10VCD, 4- 20 mA electric signal and shall provide similar transduced feedback output signal to control system. The valves actuators shall be compatible with Building Automation System. HVAC consractor shall ensure the required power supply to the valve for proper working.The minimum close off Pressure of actuator must be 1.5 times shut off head of pump . The valve shall be suitable for following pipe sizes 50 mm dia pipes for AHU |  | Nos | 1 | 42500 | 42500 | 1 | 42500
3 | Supply, installation, testing and commissioning of THERMOSTAT for cooling. The thermostat shall be electronic room temperature controller with digital display fan speed control, capable of providing individual space temperature control for cooling application. The controller shall be designed to modulate two control devices such as 2 way motorized valves for chilled water cooling in 2 pipe system. Thermostat for AHU |  | Nos | 1 | 4830 | 4830 |  | 0
4 | PIPING-CHILLED WATER | [6 empty] | 0
5 | Providing and fixing in position the following MS class ‘C’ pipes cut to required lengths and installed with all welded joints, providing and fixing in position the necessary fittings like elbows, tees and reducers, sockets for probe meter with necessary supports by MS structural steel if required, hangers, clamp supports from walls, floors and ceiling including cutting holes and chases in brick, R.C.C. work, making good the same to original condition complete in all respects with painting with one coat of primer and | [6 empty] | 0
6 | Note All chilled water and condenser water pipes and all fittings shall be Mild Steel - Class `C’ (Heavy Class) conforming to relevant BIS-1239 Code from 20 mm to 250 mm dia. Factory rolled pipes 250 mm dia above shall have 8 mm wall thickness confirming to IS-3589. Entire piping shall have welded joints conforming to relevant BIS Codes. 50 mm dia MS pipes |  | Rmt | 10 | 1750 | 17500 | 10 | 17500 | 14.5 | 25375
7 | Providing and fixing in position the following GI class ‘B’ pipes cut to required lengths and installed with all screwed joints, and providing and fixing in position the necessary elbows, tees and reducers as per specifications with necessary supports by MS structural steel if required, hangers, clamp supports from walls, floors and ceiling including cutting holes and chases in brick, R.C.C. work, making good the same to original condition complete in all respects with painting with one coat of primer and two coats of paint to supports of MS work 25 mm dia MS pipes |  | Rmt | 10 | 2540 | 25400 | 10 | 25400 | 11 | 27940
8 | Providing and fixing in position the following Butterfly Valve Valves 50 mm dia Valves. |  | Nos | 2 | 6500 | 13000 | 2 | 13000
9 | Providing and fixing in position the following ‘Y’ Strainers 50 mm dia Valves |  | Nos | 1 | 8600 | 8600 | 1 | 8600 | 1 | 8600
10 | Supplying, installation, testing and commissioning of Auto air vents. |  | Nos | 1 | 1800 | 1800 | 1 | 1800
11 | Providing and fixing in position the industrial type pressure gauges with gun metal including GI nipple valves. |  | Nos | 2 | 5500 | 11000 | 2 | 11000 | 1 | 5500
12 | Providing and fixing in position the mercury-in- glass industrial type thermometers within brass encasing |  | Nos | 1 | 3500 | 3500 | 1 | 3500 | 14.5 | 50750
13 | Supplying, installing and testing of 25 mm thick expanded polystyrene pre moulded pipe section insulation along with aluminium cladding on chilled water piping and fitting like valves, flanges union, etc. as per the approved shop drawings and specifications. 50 mm dia pipes |  | Rmt | 10 | 2100 | 21000 | 10 | 21000 | 11 | 23100
14 | 25mm dia condensate drain pipes |  | Rmt | 10 | 320 | 3200 | 10 | 3200
15 | Providing and fixing electric water storage heater (geyser) wall hung with glass lined tank and 40 -50 mm insulation. The system should be single phase 50 Hz it should be all necessary feature like adjustable thermostat, protective anode rod including making inlet outlet connections. | [6 empty] | 0
16 | Capacity 20 litre |  | Nos | 2 | 18500 | 37000 | 2 | 37000
17 | Capacity 50 litre |  | Nos | 1 | 35000 | 35000 | 1 | 35000
B | HVAC Low side work |  |  |  |  | 224330 |  | 219500 |  | 141265
[5 empty] | Sub Total | 607280 |  | 602450 |  | 141265

## HVAC JMR RA Bill 01
IMPULSE BRANDING SOLUTIONS
03/204, SUNDAR DARSHAN CHSL, MIRA BHAYANDER, THANE - 401107
Date:- 10.08.2024
Project : Adani CIP Lounge T3 Lok
W/O No : PO/23-24/000754
Name of the Work : HVAC Work T3 Lok
FDS MEASUREMENT SHEET OF HVAC
S. No. | Item. Code | Specification | Description | W | H | Unit | Nos | Qty. | Extra QTY
1 |  | HVAC RA Bill 01
1
| 1 | A. EQUIPMENT 1 Supplying, installing, testing and commissioning of double skin construction draw thru type AIR HANDLING UNITS (AHU) as per specification, each complete with following a) Supply air centrifugal fan with efficiency >60% b) Pre filter (MERV 8) and Bag Filter (MERV 13) in supply air stream. c) Six row deep cooling coil of copper tube and aluminum construction sized at maximum face velocity of 500 fpm. Cooling coil frame work and coil end plate shall be of SS304 construction. d) VFD designed for HVAC applications for supply air fan e) Squirrel cage induction motors IE-2 (EFF-1) suitable for 415 ± 10% volts, 50 Hz, AC supply meeting criterion as per ASHRAE standard 90.1-2013 and 90% or higher efficiency. f) Vibration isolators. g) Fan outlet velocity not exceeding 10 mps. h) Height of Ceiling Suspended AHU shall not exceed 700 mm. i) Minimum 30mm(WC) external static pressure shall be considered; however the total static pressure Motor rating shall be determined by contractor considering pressure drop across all accessories on supply air streams. j) Sound level at 1 m distance not exceeding 60 dB(A). TAG. SPACE LOCATION CFM TR SUGGESTED SUGGESTED NO. FEED STATIC PRESSURE MOTOR K.W. (MM W.G.) 1.1 AHU- Domestic ---- 6500 17 65 3.8 1 CIP Lounge 1 No. 1.00 382,950.00 382,950.00 Total
|  | AHU | Nos |  |  |  | 1
|  | Total Qty |  |  |  |  | 1
|  | WO Qty |  |  |  |  | 1
|  | RA 01Qty |  |  |  |  | 1
| 2 | Supply, Installation, testing and commissioning of electronic, AUTOMATIC PRESSURE INDEPENDENT BALANCING VALVE type dynamic balancing Valve with integrated 2 way modulating Control valves in a single body. The actuator shall be capable of accepting 2-10VCD, 4- 20 mA electric signal and shall provide similar transduced feedback output signal to control system. The valves actuators shall be compatible with Building Automation System. HVAC consractor shall ensure the required power supply to the valve for proper working.The minimum close off Pressure of actuator must be 1.5 times shut off head of pump . The valve shall be suitable for following pipe sizes 50 mm dia pipes for AHU
|  |  | Nos |  |  |  | 1
|  | Total Qty |  |  |  |  | 1
|  | WO Qty |  |  |  |  | 1
|  | RA 01Qty |  |  |  |  | 1
| 3 | Supply, installation, testing and commissioning of THERMOSTAT for cooling. The thermostat shall be electronic room temperature controller with digital display fan speed control, capable of providing individual space temperature control for cooling application. The controller shall be designed to modulate two control devices such as 2 way motorized valves for chilled water cooling in 2 pipe system. Thermostat for AHU
Nos
|  | Total Qty |  |  |  |  | 0
|  | WO Qty |  |  |  |  | 1
|  | RA 01Qty |  |  |  |  | 0
| 6 | All chilled water and condenser water pipes and all fittings shall be Mild Steel - Class `C’ (Heavy Class) conforming to relevant BIS-1239 Code from 20 mm to 250 mm dia. Factory rolled pipes 250 mm dia above shall have 8 mm wall thickness confirming to IS-3589. Entire piping shall have welded joints conforming to relevant BIS Codes. 50 mm dia MS pipes
|  | 50 mm dia MS pipes | Rmt |  |  |  | 24.5
|  | Total Qty |  |  |  |  | 24.5
|  | WO Qty |  |  |  |  | 10 |  | 14.5
|  | RA 01Qty |  |  |  |  | 10
| 7 | Providing and fixing in position the following GI class ‘B’ pipes cut to required lengths and installed with all screwed joints, and providing and fixing in position the necessary elbows, tees and reducers as per specifications with necessary supports by MS structural steel if required, hangers, clamp supports from walls, floors and ceiling including cutting holes and chases in brick, R.C.C. work, making good the same to original condition complete in all respects with painting with one coat of primer and two coats of paint to supports of MS work.
|  | 25 mm dia MS pipes | Rmt |  |  |  | 21
|  | Total Qty |  |  |  |  | 21
|  | WO Qty |  |  |  |  | 10 |  | 11
|  | RA 01Qty |  |  |  |  | 10
| 8 | Providing and fixing in position the following Butterfly Valve Valves 50 mm dia Valves.
|  | 50 mm dia Butterfly Valve Valves | Nos |  |  |  | 2
|  | Total Qty |  |  |  |  | 2
|  | WO Qty |  |  |  |  | 2
|  | RA 01Qty |  |  |  |  | 2
| 9 | Providing and fixing in position the following ‘Y’ Strainers 50 mm dia Valves
|  | Strainers 50 mm dia Valves | Nos |  |  |  | 2
|  | Total Qty |  |  |  |  | 2
|  | WO Qty |  |  |  |  | 1 |  | 1
|  | RA 01Qty |  |  |  |  | 1
| 10 | Supplying, installation, testing and commissioning of Auto air vents.
|  | Auto air vents. | Nos |  |  |  | 1
|  | Total Qty |  |  |  |  | 1
|  | WO Qty |  |  |  |  | 1
|  | RA 01Qty |  |  |  |  | 1
| 10 | roviding and fixing in position the industrial type pressure gauges with gun metal including GI nipple valves
|  | pressure gauges | Nos |  |  |  | 2
|  | Total Qty |  |  |  |  | 2
|  | WO Qty |  |  |  |  | 2
|  | RA 01Qty |  |  |  |  | 2
| 11 | Providing and fixing in position the mercury-in- glass industrial type thermometers within brass encasing
|  | thermometers | Nos |  |  |  | 2
|  | Total Qty |  |  |  |  | 2
|  | WO Qty |  |  |  |  | 1 |  | 1
|  | RA 01Qty |  |  |  |  | 1
| 12 | Supplying, installing and testing of 25 mm thick expanded polystyrene pre moulded pipe section insulation along with aluminium cladding on chilled water piping and fitting like valves, flanges union, etc. as per the approved shop drawings and
|  | THERMAL INSULATION 50 mm dia pipes | Rmt |  |  |  | 24.5
|  | Total Qty |  |  |  |  | 24.5
|  | WO Qty |  |  |  |  | 10 |  | 14.5
|  | RA 01Qty |  |  |  |  | 10
| 13 | Supplying, installing and testing of 25 mm thick expanded polystyrene pre moulded pipe section insulation along with aluminium cladding on chilled water piping and fitting like valves, flanges union, etc. as per the approved shop drawings and
|  | THERMAL INSULATION 25 mm dia pipes | Rmt |  |  |  | 21
|  | Total Qty |  |  |  |  | 21
|  | WO Qty |  |  |  |  | 10 |  | 11
|  | RA 01Qty |  |  |  |  | 10
| 14 | Providing and fixing electric water storage heater (geyser) wall hung with glass lined tank and 40 -50 mm insulation. The system should be single phase 50 Hz it should be all necessary feature like adjustable thermostat, protective anode rod including making inlet outlet connections.
|  | (geyse Capacity 20 litre | Nos |  |  |  | 2
|  | Total Qty |  |  |  |  | 2
|  | WO Qty |  |  |  |  | 2
|  | RA 01Qty |  |  |  |  | 2
| 15 | Providing and fixing electric water storage heater (geyser) wall hung with glass lined tank and 40 -50 mm insulation. The system should be single phase 50 Hz it should be all necessary feature like adjustable thermostat, protective anode rod including making inlet outlet connections.
|  | (geyse Capacity 50 litre | Nos |  |  |  | 1
|  | Total Qty |  |  |  |  | 1
|  | WO Qty |  |  |  |  | 1
|  | RA 01Qty |  |  |  |  | 1