## Sheet1
BOQ @ MOD - Hyd Arrival Airport
| Brand - Mad Over Donuts |  |  | Date | 2024-02-08
Type: Food Court
Location: Hyd Arrival Airport
Area: 341 SqFt
Sub: Interior Works
Dear Sir,
With reference to discussions at site. Please find our offer as follows.
ITEM CODE | ITEM NAME | UOM | QTY | UNIT COST | REMARKS
A | HVAC SYSTEM EQUIPMENTS
KITCHEN EQUIPMENTS
A.1 | Supply, installation, testing, commissioning and field performance of ceiling suspended Kitchen Exhaust Fan with all necessary supports and fittings.
A.1.1 | 4000 CFM | Nos | 1
A.2 | Supply, installation, testing, commissioning and field performance of ceiling suspended Electrostatic Precipitator (for removal of Kitchen Grease and Smoke particles) with all necessary supports and fittings.
A.2.1 | 4000 CFM | Nos | 1
A.3 | Supply, installation, testing, commissioning and field performance of ceiling suspended Air Washer Unit with all necessary supports and fittings.
A.3.1 | 3000 CFM | Nos | 1
B | AC PIPING
HVAC CONDENSATE DRAIN PIPE
B.1 | Supply and fixing in position of Rigid PVC condensate drain water piping with necessary supports and fittings like, U-traps, elbows, tees and reducers insulated with 9mm nitrile rubber and BOPP tape.
B.1.1 | 25 mm Ø | Mtr | 6
C | AIR DISTRIBUTION DUCTS
RECTANGULAR DUCTS
C.1 | Supply, installation and testing of Galvanized Steel / Galvanized Iron, factory fabricated square / rectangular ducts, complete with TDF flanges and bracing necessary supports using thread roads and anchor bolts, supply air collars, vanes, splitters dampers. The ducts shall be fabricated and installed in line with SMACNA standards. (for Supply Air Duct)
C.1.1 | 24 Gauge (for low pressure duct with duct size larger side 0 - 1000 mm) | Sq.Mtr | 25
C.2 | Supply, installation and testing of Galvanized Steel / Galvanized Iron, factory fabricated square / rectangular ducts, complete with TDF flanges and bracing necessary supports using thread roads and anchor bolts, supply air collars, vanes, splitters dampers. The ducts shall be fabricated and installed in line with SMACNA standards. (for Make-up Air Duct)
C.2.1 | 24 Gauge (for low pressure duct with duct size larger side 1001 - 1200 mm) | Sq.Mtr | 15
C.3 | Supply, installation and testing of Mild Steel / Black Steel, factory fabricated square/rectangular ducts, complete with MS flanges and bracing necessary supports using thread roads and anchor bolts, collar risers fully welded construction, duct and all other acessaries shall be fire resistant.The ducts shall be fabricated and installed in line with SMACNA standards. (for Kitchen Exhaust Air Duct)
C.3.1 | 20 Gauge | Sq.Mtr | 20
D | AIR DISTRIBUTION DUCT INSULATION & LINNING
D.1 | Supply, installation & testing of Thermal Insulation of ducting using closed-cell elastomeric nitrile rubber, Black Colour with silver foil covering, Thermal Conductivity λ - 0.036 W/(m-K) at 0° C and Fire performance according to building regulations - Class "O" as per BS 476 with necessary adhesives.
D.1.1 | 19 mm thicknesses | Sq.Mtr | 40
D.2 | Supply, installation & testing of Thermal Insulation of ducting using glass wool with silver foil covering, density 40 Kg/m3, Thermal Conductivity λ - 0.030 W/(m-K) at 0° C and Fire performance according to building regulations - Class "O" as per BS 476.
D.2.1 | 80 mm thicknesses | Sq.Mtr | 20
E | AIR DISTRIBUTION DUCT ACCESSORIES
E.1 | Supply, installation, tetsing and commissioning of Extruded Aluminium Low Leakage square / rectangular Volume Control Damper with aero-foil opposed blades and nylon gears system outside air stream with adjustable handle with position arresting bolt.
E.1.1 | Size - 250 x 250 mm | Nos | 2
E.2 | Supply, installation, tetsing and commissioning of Extruded Aluminium Opposed Blade Damper / Collar Damper with Nylon gears and lever on face side for smooth operation.
E.2.1 | Size - 300 x 300 mm | Nos | 4
E.2.2 | Size - 350 x 350 mm | Nos | 4
F | AIR TERMINALS - (GRILLES, REGISTERS, DIFFUSERS & LOUVERS)
F.1 | Supply, installation, tetsing and commissioning of Extruded Aluminium Square Grille with fixed Aerofoil Blades, with 30° deflection - 2 Way with rigid frame of 16mm flange as standard.
F.1.1 | Neck Size - 250 x 250 mm | Nos | 1
F.2 | Supply, installation, tetsing and commissioning of Extruded Aluminium Linear Slot Diffuser with vertical deflections blades to adjust direction of air flow with 25 mm slot opening.
F.2.1 | 3 Slot with OBD x Length - 1000 mm (For Supply Air) | Nos | 6
G | TESTING & COMMISIONING
G.1 | Air Balancing & Chilled Water Testing & Commisioning | Lot | 1
GRANT TOTAL NET
NOTE: The quantities mentioned in the above BOQ includes services only inside the site location (building). If any termination of services required outside the site location contractor to verify at site and provide the quantity and cost over and above this BOQ. Any service penetration to be made good after installation. Fire sealing to be done for penetrations as per Airport requirement.