## Summary
Summary -TFS Base Kitchen - Matiyala
S No | Description | Amount
1 | CIVIL | 0
2 | Electrical | 0
3 | Fire Fighting | 0
4 | HVAC | 0
5 | Plumbing | 0
| TOTAL | 0
| GST 18% | 0
| GRAND TOTAL | 0

## Civil BOQ
Matiala TFS Kitchen Civil BOQ
2024-09-21
S.NO | ITEM/ DESCRIPTION | QTY | UNITS | Rates | Amount
1 | CIVIL WORK
1.1 | Providing and constructing 4" thick siporex wall with minimum compressive strength in Cement Mortar 1:6 (1 cement : 6 coarse sand ) proportion,in straight as per plan in walls, including scaffolding, curing and providing RCC band or reinforcement at at every lVth cours complete at all levels and locations and as directed. | 1390 | sq.ft |  | 0
1.1 | Providing and constructing 9" thick siporex wall with minimum compressive strength in Cement Mortar 1:6 (1 cement : 6 coarse sand ) proportion,in straight as per plan in walls, including scaffolding, curing and providing RCC band or reinforcement at at every lVth cours complete at all levels and locations and as directed. | 2180 | sq.ft |  | 0
1.2 | Providing & laying full brick (230mm thick) partition walls with well burnt 1st class table molded, good quality approved brick In cement mortar 1:4 (1cement : 4 coarse sand) including 2 nos. of 6mm dia. MS round bars at every lVth course. Cost should include scaffolding curing. rubbing the surface. racking out the joints etc., complete asdirected and specified for walls platform supports etc. | RO | Cu.ft
1.3 | PLASTER - providing and Applying Boh area 10 - 12mm thick plaster in cement mortar 1:4(1 cement : 4 coars sand) to all specified walls (small or big) surfaces induding, wall tops, jambs and cill etc. in line level and plumb including chicken wire mesh on junction and joints smooth cement finish, including providing necessary grooves at all the junctions of walls and ceiling, walls and frames for doors or window, around skirting/ dado or at other places as directed including raking the joints or roughening the RCC surfaces, necessary curing, scaffolding etc., complete as directed and specified | 6747 | sq.ft |  | 0
1.4 | LIGHT WEIGHT CONCRETE FILLING + PCC TOP : Providing and Filling on RCC slab areas @400mm at BOH AREA with light weight concrete block waste of approximately 600 kg per cum density laid, levelled, finished, smooth, including finishing with 30-60mm top layer of 1:2:4 PCC as per specification. | 0 | CU.ft |  | 0
1.5 | Providing and Laying 30 mm to 50mm thk. Plain Cement Concrete (PCC) 1:4:8 (1 cement :4 coarse sand : 8 graded stone aggregate 40mm nominal size), in raft/bases of column footing/brick wall footings/base of floor and as screed over rough areas to make up levels or to form sloges/ as base for main flooring and laid to required levels and grade at all locations, consolidated finished fair and cured.Cost should be complete and inclusive of all side forms as required. | 3650 | sq.ft |  | 0
1.6 | WATERPROOFING WORKS :- Providing, applying & testing water proofing treatment of RCC sunken slabs (Kichen) to specified areas & wall surface up to 300mm height from FFL by providing a 3MM thick bitumen based membrane comprising of the following operations. Including preperation of surface and plastering of surface with 12mm thick protective plaster 1:4 (1 cement : 4 coarse sand) over treated surface etc complete. (Quoted rate to include grouting of RCC surface for any cracks/ fissures) This treatment shall be upto 300mm height on all walls from finished floor level, all around water proof area. "Special warranty for 10 yrs to be out lined along with autorized specialized applicator executing the job" | 4414 | sq.ft |  | 0
1.8 | Casting of lintels above doors and wherever neccesary in R.C.C. of size | 65 | r.ft |  | 0
2 | CEILING WORK
2.1 | Reparing of existing ceiling using plaster and acrylic putty after proper curing, please note the surface area to be measured | 3850 | Sqft |  | 0
3 | FLOORING & Wall Tiling
3.1 | Providing and Fixing of 25 mm thick kota stone on a PCC bed surface in brick pattern with groove of 3 mm filled by epoxy MYK laticrete grout as applicable as per site condition. Cost should be Inclusive of Skirting .of all the area basic price of kota @40 Rs/Sq.ft. | 3630 | sq.ft |  | 0
3.2 | Providing and fixing of ceramic Wall TiIe for all kitchen area. Tile thickness to be 8-10mm with under cement mortar of 20mm thick or as applicable as per site condition. (base rate of tiles 40 Rs/Sq.Ft.)Tile size of 300 X 450 in landscape orientation. | 4896 | sq.ft |  | 0
5 | DOOR and WINDOW
NOTES:
a | Door Frames as mentioned in the specification below
b | Ail flush doors in 40mm BWP Flush Doors of Green / Kit ply / Garnet / Duro make. Oakwood finish laminate with kick plate, push plate.
c | Hardware- hafele / Dorma / Geze
5.1 | Providing and fixing Door with frames in 1st class Arau Chaap wood as per design. Rate shalL Include fixing of chaukhat in position with grouting hold fast in cement concrete 1:2:4 (1 cement: 2 coarse sand : 4 aggregate average 20mm size). Rate to include Hardwood Lipping with Melamine Polish of required shade including Hardwood frame 100mm x 65mm including all hardware, Door closer, door stopper, All Hardwares Doorset or Equivalent Make and necessary hardware . | 300 | r.ft |  | 0
a | 750 X 2100 washroom flush doors shutter 35 mm thick | 3 | Nos |  | 0
b | 900 x 2100 MM Flush door Shutter 35mm thick with SS kick Plate | 4 | Nos |  | 0
c | 2100 MM highsliding door Shutter 35mm thick for the wall opening of 2285 mm | 1 | Nos |  | 0
d | 750 X 2100 sliding door shutter 35 mm thickness | 1 | Nos |  | 0
e | 1200x2100 MM Double leaf flush Door | 2 | Nos |  | 0
f | Hardware for Above Doors - Lock, Latch, Door Handle & Door Closer | 3 | SET(S) |  | 0
g | MS Fire Door with wired glass vision panel, having parallel push bar/ lock /, automatic door closer and all the necessary fittings, contractor needs to provide fire door certificate. 2200 X2100 X40 | 1 | No. |  | 0
h | MS Fire Door with wired glass vision panel, having parallel push bar/ lock /, automatic door closer and all the necessary fittings, contractor needs to provide fire door certificate. 1200X2100 X40 | 2 | No. |  | 0
6 | FIXED WOOD & MS WORKS
6.1 | Providing and Fixing wooden workstation as per layout having wire manager, lockable stoage pedestal 800 X 500 X 700(h) oakwod finished laminate, hettich fittings, | 1 | NOS. |  | 0
6.2 | Providing and Fixing wooden workstation as per layout having wire manager, lockable stoage with 3 no. pedestal 500 mm depth X 700(h) oakwod finished laminate, hettich fittings, | 12.6875 | Sqft |  | 0
6.3 | Office chair : Providing High back ergonomic office chair having adjustable seat and back bend and lockable system (executive chair) | 5 | NOS. |  | 0
6.4 | Cafateria table top finished with merinolam 22099 slate ML 1 mm thich laminate, top to be fixed on MS round hollow pipe of 60 mm painted black to give support on two side of top | 2 | NOS. |  | 0
6.5 | Cafateria table top finished with merinolam 22099 slate ML 1 mm thich laminate, top to be fixed on MS round hollow pipe of 60 mm painted black to give support on two side of top (2 seater) | 1 | NOS. |  | 0
6.6 | Cafteria chair- p/F of cafeteria chair with dark brown upholstery stitched over EP foam pasted on 19 mm ply base having ms legs with nylon buffer | 10 | NOS. |  | 0
7 | PAINTING AND FINISHING
7.1 | BOH area open ceiling (PLASTIC PAINT) P/A 2 coats of plastic black matt paint as per app.. ASIAN PAINTS by sand papering the surface, applying one coat of primer, prepare the surface with sand papering again, repeating a coat of primer, applying one coat of plastic paint, touching up with putty & applying two final roller coats of plastic paint, to internal wall/slab surfaces incl. preparing the surface by cleaning scrapping, smooth filling crevices, scaffolding etc. | 6830 | SQ.FT |  | 0
8 | MISCELLANEOUS WORKS
8.1 | Debris Removal to be verified by site engineer and security guard which should be maintained in IN/Out register | 25 | NOS. |  | 0
8.3 | Temporary plumbing, electricity connection to start the execution works. | 1 | set |  | 0
8.4 | SS corner Guard on all edges W type as per the specs | 250 | RFT |  | 0
8.5 | Dismantling for HVAC, plumbing and other services, | 500 | SQ.FT |  | 0
\ | TOTAL |  |  |  | 0

## electrical work
Comparative Electrical Work
S. No | Description | Unit | Qty | Rate | Amount
SECTION-I- WIRING/POINT WIRING & CONDUTING
1.1 | Supply and Installation of all materials, accessories and labour for wiring for light/ equipment circuit main using PVC insulated stranded copper conductor FRLS wires of 1100V grade drawn through heavy gauge rigid PVC/MS conduit ( The cost of the conduit will be taken separately ) using necessary conduit accessories, PVC pull/junction boxes, G.I. fish wire etc. The rate shall include the cost of providing PVC insulated stranded copper conductor earth wire in each conduit alongwith other circuit main wires. Lugs to be use at both the ends. FRLS Type only.
1.1.1 | Supply & Installation of 1.5 Sq.mm copper FRLS wires | Rmt | 30 |  | 0
1.1.2 | Supply & Installation of 2.5 Sq.mm copper FRLS wires | Rmt | 50 |  | 0
1.1.3 | Supply & Installation of 4 Sq.mm copper FRLS wires | Rmt | 30 |  | 0
1.1.4 | Supply & Installation of 6 Sq.mm copper FRLS wires | Rmt | 30 |  | 0
1.1.5 | Supply & Installation of 10 Sq.mm copper FRLS wires | Rmt | 50 |  | 0
1.1.6 | Supply & Installation of 16 Sq.mm copper FRLS wires | Rmt | 50 |  | 0
1.2 | Supplying and installing all materials, accessories and labour for conduiting & the accessories for light/ Equipment circuit main.The conduit should be Medium gauge rigid 1.6 mm thick FRLS type PVC conduits conforming to IS-2509 of 1973 . The conduits shall be clamped by G.I./ PVC saddles of minimum 20 gauge or be clamps fabricated from M.S. strips of minimum 25 mm x 3 mm. The M.S. clamps/supports shall be duly painted with 2 coats of red oxide and 2 coats of black enamelled paint.The clamps/supports shall be fixed to the underside of the ceiling by means of nylon rawl plugs and brass screws of 3 mm size. Anchor fasteners of suitable sizes shall be provided if necessary.The conduits shall be supported at regular intervals of 500 mm. Additional supports shall be provided on either side of bends, JB's & terminations. The conduits shall be bent with bending springs to provide smooth bends. Use of ready made bends shall be kept to a minimum. The jointing of PVC conduits shall be done with couplers and PVC solvent cement. Conduits to be terminated in M.S. Boxes shall be terminated with female adaptors with bushes. All conduits assembled (PVC & M.S.) without wiring shall be provided with G.I. pull wire of minimum thickness of 14SWG. And end portion of the conduit to be provided with end caps where ever necessary. The cost should include the cost of heavy gauge rigid PVC conduit with necessary conduit accessories, PVC pull/junction boxes, G.I. fish wire etc & laying of the same. FRLS Only
1.2.1 | 20mm PVC Conduit | Rmt |  |  | 0
1.2.2 | 25mm PVC Conduit | Rmt | 100 |  | 0
1.2.3 | 32mm PVC Conduit | Rmt |  |  | 0
1.2.4 | PVC Flexible Conduit Dia 20 mm | Rmt |  |  | 0
1.2.5 | PVC Flexible Conduit Dia 25 mm | Rmt | 150 |  | 0
1.2.6 | PVC Flexible Conduit Dia 32 mm | Rmt |  |  | 0
1.2.7 | 20mm MS Conduit | Rmt |  |  | 0
1.2.8 | 25mm MS Conduit | Rmt | 724 |  | 0
1.2.9 | 32mm MS Conduit | Rmt | 30 |  | 0
1.2.10 | 40mm MS Conduit | Rmt | 60 |  | 0
1.2.11 | MS Flexible Conduit Dia 20 mm | Rmt |  |  | 0
1.2.12 | MS Flexible Conduit Dia 25 mm | Rmt | 500 |  | 0
1.2.13 | MS Flexible Conduit Dia 32 mm | Rmt |  |  | 0
POINT WIRING WITH FRLS PVC/MS CONDUITES
1.3 | Lighting Circuit - SITC of Wiring for following Light points with 3x1.5 sq.mm FRLS PVC insulated flexible copper conductor multi Strand wires of 1100 V grade in recess or surface with FRLS PVC ISI marked conduit with accessories such as bends, junction boxes, pull wire including 1.5 sq.mm copper conductor green color earth wire for earthing of all metal boxes, light fixtures, exhaust fan etc. complete as required including circuit wiring with 2x2.5 + 2.5 sq. mm FRLS wires from DB to Switch Board, switch Board to Light & switch board to switch board. (NOTE-NO ADDITIONAL CIRCUIT LENGTH WILL BE MEASURED DURING BILL CERTIFICATION PROCESS)
1.3.1 | Primary light points including the cost of 5A switch (Average - Length upto 18 Mtrs) | Nos |  |  | 0
1.3.2 | Primary light points directly controlled from DB (Average - Length upto 18 Mtr) | Nos |  |  | 0
1.3.3 | Secondary light points looped from the above point (Average - Length upto 8 mtrs) | Nos |  |  | 0
1.4 | Same Item with MS Conduit
1.4.1 | Primary light points including the cost of 5A switch (Average - Length upto 18 Mtrs) | Nos | 18 |  | 0
1.4.2 | Primary light points directly controlled from DB (Average - Length upto 18 Mtr) | Nos | 3 |  | 0
1.4.3 | Secondary light points looped from the above point (Average - Length upto 8 mtrs) | Nos |  |  | 0
1.5 | Equipment Power Points - Primary Point - 6/16A power point with wiring - (Phase & Neutral from DB /panel to power points : 2 x 2.5 sq. mm1.1KV grade FRLS flexible wire Earth : 2.5sqmm Cu FRLS flexible wire with FRLS PVC Conduits (Average Circuit Length 15 mtrs) | Nos |  |  | 0
1.5.1 | Equipment Power Points - Secondary point - 6/16A Power point with wiring - (Phase & Neutral from DB /panel to power points : 2x2.5 Sqmm Cu FRLS flexible wire (1.1 KV) Earth : 2.5 Sqmm FRLS flexible wire with FRLS PVC Conduits (Average Circuit Length 8 mtrs) | Nos |  |  | 0
1.6 | Same Primary Point Item with MS Conduit | Nos | 8 |  | 0
1.6.1 | Same Secondary Point Item with MS Conduit | Nos | 12 |  | 0
1.7 | Equipment Power Points - Primary Point - 6/16A power point with wiring - (Phase & Neutral from DB /panel to power points : 2 x 4.0 sq. mm1.1KV grade FRLS flexible wire Earth : 4.0sqmm Cu FRLS flexible wire with FRLS PVC Conduits (Average Circuit Length 15 mtrs) | Nos |  |  | 0
1.7.1 | Equipment Power Points - Secondary point - 6/16A Power point with wiring - (Phase & Neutral from DB /panel to power points : 2x4.0 Sqmm Cu FRLS flexible wire (1.1 KV) Earth : 4.0 Sqmm FRLS flexible wire with FRLS PVC Conduits (Average Circuit Length 8 mtrs) | Nos |  |  | 0
1.8 | Same Primary Point Item with MS Conduit | Nos | 16 |  | 0
1.8.1 | Same Secondary Point Item with MS Conduit | Nos | 22 |  | 0
1.9 | Air curtain Power Point - Primary Point - 6/16A power point with wiring for Air Curtain (Phase & Neutral from DB /panel to power points : 2 x 2.5 sq. mm1.1KV grade FRLS flexible wire Earth : 2.5sqmm Cu FRLS flexible wire with FRLS PVC Conduits (Average Circuit Length 18 mtrs).Cost should include surface box for switch & Socket.(NOTE-NO ADDITIONAL CIRCUIT LENGTH WILL BE MEASURED DURING BILL CERTIFICATION PROCESS) | Nos |  |  | 0
1.10' | Same Item with MS Conduit | Nos | 2 |  | 0
1.11 | Fly Catcher - Primary Point - 6/16A power point with wiring for Fly Catcher (Phase & Neutral from DB /panel to power points : 2 x 2.5 sq. mm1.1KV grade FRLS flexible wire Earth : 2.5sqmm Cu FRLS flexible wire with FRLS PVC Conduits (Average Circuit Length 15 mtrs).(NOTE-NO ADDITIONAL CIRCUIT LENGTH WILL BE MEASURED DURING BILL CERTIFICATION PROCESS) | Nos |  |  | 0
1.11.1 | Same Item with MS Conduit | Nos | 8 |  | 0
1.12 | Circuit WIRING
1.12.1 | Circuit mains wiring using 2 runs of 2.5 sq.mm +1x2.5 Sqmm FRLS insulated copper wires in existing Conduit. | Mtr | 240 |  | 0
1.12.2 | Circuit mains wiring using 2 runs of 4 sq.mm +1x4 Sqmm FRLS insulated copper wires in existing Conduit. | Mtr | 550 |  | 0
1.12.3 | Circuit mains wiring using 2 runs of 6 sq.mm +1x6 Sqmm FRLS insulated copper wires in existing Conduit. | Mtr | 300 |  | 0
1.12.4 | Circuit mains wiring using 4 runs of 4 sq.mm +2x4 Sqmm FRLS insulated copper wires in existing Conduit. | Mtr | 200 |  | 0
1.12.5 | Circuit mains wiring using 4 runs of 6 sq.mm +2x6 Sqmm FRLS insulated copper wires in existing Conduit | Mtr | 420 |  | 0
1.12.6 | Circuit mains wiring using 4 runs of 10 sq.mm +2x10 Sqmm FRLS insulated copper wires in existing Conduit | Mtr | 220 |  | 0
1.12.7 | Circuit mains wiring using 4 runs of 16 sq.mm +2x16 Sqmm FRLS insulated copper wires in existing Conduit | Mtr | 150 |  | 0
1.12.8 | Circuit mains wiring using 4 runs of 25 sq.mm +2x16 Sqmm FRLS insulated copper wires in existing Conduit | Mtr | 100 |  | 0
| TOTAL OF SECTION I |  |  |  | 0
SECTION-II-SUPPLY & INSTALLATION OF SWITCH SOCKET OUTLETS
2.1 | Supply & Installation of the following Industrial Plug & Socket DBs
2.1.1 | 6/32A DP Metal Clad switch socket with SP MCB | Nos. | 22 |  | 0
2.1.2 | 6/32A DP Metal Clad switch socket with DP MCB | Nos. |  |  | 0
2.1.3 | 40/63A DP Metal Clad switch socket with DP MCB | Nos. | 3 |  | 0
2.1.4 | 6/32A TP Metal Clad switch socket with TP MCB | Nos. |  |  | 0
2.1.5 | 40/63A TP Metal Clad switch socket with TP MCB | Nos. |  |  | 0
2.1.6 | 6/32A FP Metal Clad switch socket with FP MCB | Nos. | 13 |  | 0
2.1.7 | 40/63A FP Metal Clad switch socket with FP MCB | Nos. | 1 |  | 0
2.2 | Supply & Installation of the following Sockets, Switches including the front plate & Back boxes and all accessories
2.2.1 | 6A, Switch for lighting control. | No. | 18 |  | 0
2.2.2 | 6A, 5 Pin Switch socket outlet | No. | 24 |  | 0
2.2.3 | 1 no. 6 /16A 6 Pin Switch Socket Outlets (Raw Power) | No. | 5 |  | 0
2.2.4 | 1 no. 6 /16A 6 Pin Switch Socket Outlets (UPS) Black Colour | No. | 5 |  | 0
2.2.5 | 16A Flat pin switch socket outlet (white colour) | No. |  |  | 0
2.2.6 | 16A Flat pin switch socket outlet (Black colour) | No. |  |  | 0
2.2.7 | 2 no. 6 /16A 6 Pin Switch Socket Outlets (Raw Power) | No. | 6 |  | 0
2.2.8 | 2 no. 6 /16A 6 Pin Switch Socket Outlets (UPS) Black Colour | No. | 9 |  | 0
2.2.9 | 3 no. 6 /13A Universal Socket +1 no. 16A Switch Outlets (UPS) Black Colour | No. |  |  | 0
2.2.7 | Bell Switch | No. | 2 |  | 0
2.3 | Supply & Installation of Wall mounted fan with connecting wires and all required accessories complete, etc. | No. |  |  | 0
2.4 | Supply & Installation of celling fan with connecting wires and all required accessories complete, etc. | No. |  |  | 0
| TOTAL OF SECTION II |  |  |  | 0
SECTION III-TELEPHONE / DATA SYSTEM AND TV
3.1 | Supply & Installation of the CAT-6 information outlet with face plate. (For data) | Nos. | 6 |  | 0
3.2 | Supply & Installation of RJ11 telephone outlet with front plate | Nos. | 6 |  | 0
3.3 | Supply & Installation of CAT-6 Data cable in 20mm/25mm dia conduits | Mtr | 450 |  | 0
3.4 | Supply & Installation of CAT-5 telephone cable in 20mm/25mm dia conduits | Mtr |  |  | 0
3.5 | Supply & Installation of 10pair Telephone Tag block with enclosure | No. | 1 |  | 0
3.6 | TV boxes with 4 way connector | No. | 1 |  | 0
3.7 | Supplying and fixing of television socket outlet in MS boxes | No. | 2 |  | 0
3.8 | Supply & Installation of RG-6 TV cable in 20mm/25mm dia conduits | Mtr | 60 |  | 0
| TOTAL OF SECTION III |  |  |  | 0
SECTION-IV-SUPPLY & INSTALLATION OF LIGHTING FIXTURES
4.1 | Supply & Installation of the following light fittings
4.1.1 | LED Down lighters (Recessed / Surfaces Mounted) on ceiling | Nos | 20 |  | 0
4.1.2 | 600mmx600mm LED Recessed mounted LED Lights | Nos |  |  | 0
4.1.3 | Surface mounted Batten Type luminaire with 1x28/36W | Nos | 40 |  | 0
4.1.4 | Patti Type luminaire with 1x14W T5 FTL | Nos |  |  | 0
4.1.5 | Track lights with track patti | Nos |  |  | 0
4.1.6 | 7W LED Emergency exit light | Nos |  |  | 0
4.1.7 | LED Strip light at Back Bar Counter & ceiling | Nos |  |  | 0
4.1.8 | Decorative Hanging Lights | Nos |  |  | 0
4.1.9 | Picture Lights | Nos |  |  | 0
4.1.10 | External Wall light , Up & Down light 35w | Nos |  |  | 0
4.1.11 | Pole lights | Nos |  |  | 0
4.1.12 | Outdoor luminaire Lamp70/150W MH for Top compartment & Flurorescent 36WT-8,for the pole compartment.protection:- IP55. | Nos |  |  | 0
| TOTAL OF SECTION IV |  |  |  | 0
SECTION-V PANELS, DISTRIBUTION BOARDS
5.1 | Installation, Testing & Commissioning of following Panels including placemnt on point (same floor), proper cable dressing upto satisfaction of site incharge
5.1.1 | Installation, Testing & Commissioning of Main LT Panel as per SLD. | No. | 1 |  | 0
5.1.2 | Installation, Testing & Commissioning of SUB LT Panel. | No. | 1 |  | 0
5.1.3 | Installation, Testing & Commissioning of SERVO BY PASS Panel. | No. | 1 |  | 0
5.1.4 | Installation, Testing & Commissioning of AC Panel. | No.
5.2 | Supply Installation Testing & Commissioning of following Distribution boards/ Starters of following wall mounted (flush / surface) as per drawings and specifications and as required. The distribution board shall be of sheet steel enclosure powder coated with all accessories and hardware as required complete. ( Double Door Type ).The DB shall have suitable insulated fork type indipendent neutral bus bars for each phase and earth terminal block to facilitate easy termination of wires. All wires inside the DBs shall be terminated using copper end terminations. ( Standard Prefebricated DB to be use.) (With necessary dummy plate as required, with cable gland plate at top and bottom with knockouts provided with hinged lockable covers
5.2.1 | 6 Way TPN with 1 nos 32 A FP MCB + 3 nos 25 A DP ELCB 100mA (30 mA) as incomer and 12 nos 6-32 A SP MCB as Outgoings | Nos. | 1 |  | 0
5.2.2 | 6 way VTPN DB with 1 nos 40/63 A FP MCB as Incomer and 15 nos 6/10/16/32A SP MCBs + 1 nos 32A TP MCB as Outgoings | Nos. |  |  | 0
5.2.3 | 8 Way TPN with 40/63 A FP MCB + 3 nos 40/63 A DP ELCB 100mA (100 mA) as incomer and 18 nos 6 to 32 A SP MCBs as Outgoings as per SLD & load sheet | Nos. |  |  | 0
5.2.4 | 12 Way TPN with 40/63 A FP MCB + 3 nos 40/63 A DP ELCB 100mA (100 mA) as incomer and 30 nos 6 to 32 A SP MCBs as Outgoings as per SLD & load sheet | Nos. |  |  | 0
5.2.5 | 8 way SPN with 40/32 DP MCB + ELCB 100mA as Incomer and 8 nos 16A SP MCBs as outgoings | Nos. | 1 |  | 0
5.2.6 | 16 way SPN with 32 A DP MCB + ELCB 100mA as Incomer and 16 nos 10 10 32 A SP MCBs as Outgoings | Nos. | 1 |  | 0
5.2.7 | 4 way SPN with 25 A DP MCB + ELCB 100mA as Incomer and 4 nos 6A SP MCBs as Outgoings | Nos. |  |  | 0
5.2.8 | 4 way VTPN DB with 1 nos 40/63 A FP MCB as Incomer and 9 nos 6/10/16/32A SP MCBs + 1 nos 32A TP MCB as Outgoings | Nos. |  |  | 0
5.2.9 | 12 way VTPN DB with 1 nos 125A FP MCCB as Incomer and 20 nos 6/10/16/32A SP MCBs + 4 nos 32/40A TP MCB as Outgoings | Nos. |  |  | 0
5.2.8 | L&T make MF1 DOL stater (1PH) | Nos. |  |  | 0
5.2.9 | L&T make MK1 DOL stater (3PH) | Nos. |  |  | 0
5.2.10 | L&T make DOL starter in SS Housing for 3.8KW Fan with auxilliary contactor arrangement for tripping/switching On fan in case of fire | Nos. |  |  | 0
5.2.11 | L&T make star/delta starter in SS Housing for 15KW Fan with auxilliary contactor arrangement for tripping/switching On fan in case of fire | Nos. | 2 |  | 0
5.3 | Supply Installation Testing & Commissioning of following MCB/Switch Socket in Enclosures
5.3.1 | 6/16A Switch Socket in Weather Proof Enclosure | Nos. |  |  | 0
5.3.2 | 40/63A FP MCB in Weather Proof Enclosure | Nos. | 2 |  | 0
5.3.3 | 6/32A FP MCB in Weather Proof Enclosure | Nos. |  |  | 0
5.3.4 | 40/63A FP MCB in Enclosure Box | Nos. |  |  | 0
5.3.5 | 6/32A FP MCB in Enclosure Box | Nos. |  |  | 0
5.3.6 | 40/63A DP MCB in Weather Proof Enclosure | Nos. |  |  | 0
5.3.7 | 6/32A DP MCB in Weather Proof Enclosure | Nos. | 4 |  | 0
5.3.8 | 40/63A DP MCB in Enclosure Box | Nos. |  |  | 0
5.3.9 | 6/32A DP MCB in Enclosure Box | Nos. |  |  | 0
5.3.10 | 40/63A FP ELCB 100mA in Enclosure Box | Nos. | 4 |  | 0
5.3.11 | 6/32A FP ELCB 100mA in Enclosure Box | Nos. |  |  | 0
5.3.12 | 40/63A DP ELCB 100mA in Weather Proof Enclosure | Nos. |  |  | 0
5.3.13 | 6/32A DP ELCB 100mA in Weather Proof Enclosure | Nos. |  |  | 0
5.3.14 | 40/63A DP ELCB 100mA in Enclosure Box | Nos. |  |  | 0
5.3.15 | 6/32A DP ELCB 100mA in Enclosure Box | Nos. |  |  | 0
5.3.15 | 100A FP MCCB in Enclosure Box | Nos. | 1 |  | 0
| TOTAL OF SECTION V |  |  |  | 0
SECTION-VI -CABLING & EARTHING
6.1 | Supply of Installation of Following cables 1.1 KV grade PVC/XLPE insulated Armoured Aluminium /Copper conductor cables. The cables shall be laid as per dwgs or on cable trays laid over MS supports cable racks or fixing on walls including clamping the cable to supports in an approved manner as required complete with earthing as specified and rate including cable Terminations Single/Double compression type chrome plated brass glands and lugs(crimping type), PVC taping as required and all accessories complete.(The cost of the cable trays or ladders, excavation and back filling of trenches will be measured separate. The unit cost of the cable shall include clamps, fasteners etc. as required for proper installation. Earthing will be measured separately and need not be quoted under this item). All complete as required and as per final instruction as given by consultant/site engineer. The cables should be properly dressed and to be tied to the cable trays using appropriate cable ties.
6.1.1 | 3.5 C X 300 Sq.mm AL. XLPE Armoured Cable- | Mtr | 80 |  | 0
6.1.2 | 3.5 C X 240 Sq.mm AL. XLPE Armoured Cable- | Mtr |  |  | 0
6.1.3 | 3.5 C X 185 Sq.mm AL. XLPE Armoured Cable- | Mtr |  |  | 0
6.1.4 | 3.5 C X 150 Sq.mm AL. XLPE Armoured Cable- | Mtr |  |  | 0
6.1.5 | 3.5 C X 120 Sq.mm AL. XLPE Armoured Cable- | Mtr | 30 |  | 0
6.1.6 | 3.5 C X 95 Sq.mm AL. XLPE Armoured Cable- | Mtr |  |  | 0
6.1.7 | 3.5 C X 70 Sq.mm AL. XLPE Armoured Cable | Mtr | 50 |  | 0
6.1.8 | 3.5 C X 50 Sq.mm AL. XLPE Armoured Cable | Mtr |  |  | 0
6.1.9 | 3.5 C X 35 Sq.mm AL. XLPE Armoured Cable | Mtr |  |  | 0
6.1.10 | 4 C X25 Sq.mm AL.XLPE Armoured Cable | Mtr | 80 |  | 0
6.1.11 | 4 C X16 Sq.mm AL.XLPE Armoured Cable | Mtr | 80 |  | 0
6.1.12 | 4 C X 10 Sq.mm AL.XLPE Armoured Cable | Mtr |  |  | 0
6.1.13 | 4 C X 6 Sq.mm AL.XLPE Armoured Cable | Mtr |  |  | 0
6.1.14 | 4 C X 4 Sq.mm AL.XLPE Armoured Cable | Mtr |  |  | 0
6.1.15 | 4 C X 25 Sq.mm Cu. Armoured Cable | Mtr |  |  | 0
6.1.16 | 4 C X 16 Sq.mm Cu. Armoured Cable | Mtr |  |  | 0
6.1.17 | 4 C X 10 Sq.mm Cu. Armoured Cable | Mtr |  |  | 0
6.1.18 | 4 C X 6 Sq.mm Cu Armoured Cable | Mtr |  |  | 0
6.1.19 | 4 C X 4 Sq.mm Cu. Armoured Cable | Mtr |  |  | 0
6.1.20 | 4 C X 2.5 Sq.mm Cu .Armoured Cable | Mtr |  |  | 0
6.1.21 | 4 C X 1.5 Sq.mm Cu .Armoured Cable | Mtr |  |  | 0
6.1.22 | 3 C X 6 Sq.mm Cu Armoured Cable | Mtr |  |  | 0
6.1.23 | 3C X 4 Sq.mm Cu Armoured Cable | Mtr | 90 |  | 0
6.1.24 | 3C X 2.5 Sq.mm Cu Armoured Cable | Mtr |  |  | 0
6.1.25 | 2 C X 4 Sq.mm Cu Armoured Cable | Mtr |  |  | 0
6.1.26 | 2 C X 2.5 Sq.mm Cu Armoured Cable | Mtr |  |  | 0
6.1.27 | 3 C X 16 Sq.mm Cu XLPE Unarmoured | Mtr |  |  | 0
6.1.28 | 4 C X 25 Sq.mm Cu XLPE UnArmoured | Mtr |  |  | 0
6.1.29 | 4 C X 16 Sq.mm Cu XLPE Unarmoured | Mtr |  |  | 0
6.1.30 | 3 C X 10 Sq.mm Cu XLPE Unarmoured | Mtr |  |  | 0
6.1.31 | 1C x 16sqmm Cu Cable | Mtr |  |  | 0
6.1.32 | 1C x 10sqmm Cu Cable | Mtr |  |  | 0
6.1.33 | 1C x 6sqmm Cu Cable | Mtr |  |  | 0
6.1.34 | Supply & Laying of 3C x 1.5 sq mm Flexible Cable | Mtr |  |  | 0
6.1.35 | Supply & Laying of 3C x 2.5 sq mm Flexible Cable | Mtr |  |  | 0
6.2 | Supply of Installation of Following Cable Trays of 2mm thick MS steel fabricated ladder type cable trays of the following sizes.Ladder type cable trays shall be fabricated from 50 x 50 x 5 mm M.S. angles on the sides with 25 x 6 mm M.S. strips welded at intervals of 300 mm. The trays shall be painted with 2 coats of red oxide & 2 coats of synthetic enamel paint of approved colour. All trays should have coupler plates with 4 number of bolt and nuts of galvanized hardware.Trays should be supported at ecvery 1.5 mtr interval.
6.2.1 | 150mm wide ladder type Cable tray with support | Mtr |  |  | 0
6.2.2 | 300mm wide ladder type Cable tray with support | Mtr |  |  | 0
6.2.3 | 300mm wide Perforated Cable tray with support | Mtr | 45 |  | 0
6.2.4 | 150mm wide Perforated type Cable tray with support | Mtr | 30 |  | 0
6.2.5 | 450mm wide Perforated Cable tray with support | Mtr |  |  | 0
6.2.6 | Supply & Installation of 50 mm x 50 mm GI Raceway | Mtr |  |  | 0
6.2.7 | Supply & Installation of 50 mm x 100 mm GI Raceway | Mtr |  |  | 0
6.3 | Supply of Installation of Following Earthing Material wire including necessary accessories, clamping to walls, cables etc. as required and interconnection between lengths as per specifications and as per good installation practice. The rate shall include all supports, accessories and hardware necessary for proper installation. (All GI strips should be welded on a lap joint practice and two coats of bitumin paint of should be applied on the same to avvoid corrosion in future. And all copper strips should be brazed on a lap joint parctice and should be insulated with PVC sleeve while running on cable trays / wall.) And GI / Al / Cu SWG wires should be terminared using ring types lugs.
6.3.1 | 25 x 6 mm cu. Strip | Mtr |  |  | 0
6.3.2 | 25 x 3 mm cu. Strip | Mtr |  |  | 0
6.3.3 | 25 x 6 mm GI. Strip | Mtr | 50 |  | 0
6.3.4 | 25 x 3 mm GI. Strip | Mtr |  |  | 0
6.3.5 | 8 SWG hard drawn bare GI wire | Mtr | 400 |  | 0
6.3.6 | 8 SWG hard drawn bare Cu. wire | Mtr |  |  | 0
6.3.7 | 12 SWG hard drawn bare GI wire | Mtr |  |  | 0
6.3.8 | 12 SWG hard drawn bare Cu. wire | Mtr |  |  | 0
6.4 | Providing and laying 1C x 25 sqmm insulated copper wire as earthing conductor including necessary accessories, clamping to walls, cables etc. as required and interconnection between lenghts as per specifications and as per good installation practice. | Mtr | 50 |  | 0
6.4.1 | Providing and laying 1C x 16 sqmm insulated copper wire as earthing conductor including necessary accessories, clamping to walls, cables etc. as required and interconnection between lenghts as per specifications and as per good installation practice. | Mtr | 50 |  | 0
6.4.2 | Providing and laying 1C x 10 sqmm insulated copper wire as earthing conductor including necessary accessories, clamping to walls, cables etc. as required and interconnection between lenghts as per specifications and as per good installation practice. | Mtr |  |  | 0
6.4.3 | Providing and laying 1C x 6 sqmm insulated copper wire as earthing conductor including necessary accessories, clamping to walls, cables etc. as required and interconnection between lenghts as per specifications and as per good installation practice. | Mtr |  |  | 0
6.4.4 | Providing and laying 1C x 4 sqmm insulated copper wire as earthing conductor including necessary accessories, clamping to walls, cables etc. as required and interconnection between lenghts as per specifications and as per good installation practice. | Mtr |  |  | 0
6.4.5 | Chemical Earthing - Supply Installation Testing & commissioning of Chemical earthing with GI electrode Pipe earth pits with 40 Dia, two meters length pipe with specially developed on Pipe in pipe/Strip concept filled with highly conductive & anticorrosive crystalline conductive mixture. The back fill is to be done by special compound which retains moisture & enhance conductivity. The rate should be inclusive of making bore & finish & terminated in chamber, masonry chamber with concrete base, manhole, lockable cover with frame (300 x 300 mm) For dedicated Earth, make ASHOK or equivalent | Nos. | 4 |  | 0
6.4.6 | Normal Earthing - Supply & Installation of 38 mm Dia, 2.5 Mtr. long G.I. pipe electrode earthing station complete with manholes, brick masonry chambers, covers, funnels etc., The Copper plate should be of 600 x 600 x 5mm thickness & GI pipe bolted with plate & top funnel for recharging. The cost shall also include providing of salt and charcoal layer by layer, excavation and back filling etc., all complete with manhole chamber, medium duty C.I cover and shall be installed as per I.S 3043 | Nos. |  |  | 0
6.4.7 | Supply and Installation of 25x6mm GI Earth Bus in Powder coated Box | Nos. |  |  | 0
6.4.8 | Supply and Installation of 25x3mm Cu. Earth Bus in Powder coated Box | Nos. |  |  | 0
| TOTAL OF SECTION VI |  |  |  | 0
SECTION-VII -FIRE DETECTION SYSTEM
7.1 | CONVENTIONAL TYPE
7.1.1 | Supply & Installation of wiring for Smoke detector/ MCP/Hooter/ control module etc. devices with 2C x 1.5 Sqmm FRLS Cu armored cable - | Mtr | 330 |  | 0
7.1.2 | Supply & Installation of Smoke Detector with base ,with required accessories for fixing , including cable termination etc. | Nos | 20 |  | 0
7.1.3 | Supply & Installation of Heat Detector with base ,with required accessories for fixing , including cable termination etc. | Nos | 12 |  | 0
7.1.4 | Supply & Installation of Manual Break glass Unit ,with required accessories for fixing , including cable termination etc. | Nos | 3 |  | 0
7.1.5 | Supply & Installation of Hooter ,with required accessories for fixing , including cable termination etc. | Nos | 3 |  | 0
7.1.6 | Supply & Installation of Response Indicator ,with required accessories for fixing , including cable termination etc. | Nos |  |  | 0
7.1.7 | Supply & Installation of Four Zone Fire Alarm Panel with Auto Dialing Facility | Nos |  |  | 0
7.1.8 | Supply, Installation Testing Commissioning of 4 Zone Fire Panel with 30 min battery backup. The Panels should have Capability to integrated with Developer's Addressable FAP & cost for the same should be included in this items | Nos | 1 |  | 0
| TOTAL OF SECTION VII |  |  |  | 0
SECTION-VIII-MUSIC SYSTEM
8.1 | Supply & Installation of 2 core shielde microphone cable | Rmt |  |  | 0
8.2 | Supply & Installation of 2c shielded Speaker cable inexisting Conduit (Conduit cost extra) | Rmt | 100 |  | 0
8.4 | Installation of 6/9/15W speakers to be mounted on Column /wall/Ceiling | Nos. | 1 |  | 0
8.5 | Installation, testing & commissioning of amplifier 120W for music system suitable to operate on 230V AC/12V DC, with low impedance microphone input & two auxiliary inputs, tone control, protection circuit complete for the speakers output 4/8/16 lines | Nos. | 1 |  | 0
8.6 | Installation of volume control cum ON OFF switch flush mounted on wall along with other electrical switch flush mounted on wall along with other electrical switches .The size and plate of the regulating knob should match with other switches nearby | Nos. | 1 |  | 0
8.7 | Installation of Table Top Microphone | Nos. |  |  | 0
| TOTAL OF SECTION VIII |  |  |  | 0
SECTION-IX-SERVO STABILIZER/ INVERTOR/UPS
9.1 | Installation of Single Phase Servo Stabilizer-Online systems | Nos. |  |  | 0
9.2 | Installation of Invertor with 20 minutes battery back up-Online Systems | Nos. |  |  | 0
9.3 | Installation of UPS with 20min battery back-up- make Online Systems | Nos. | 1 |  | 0
9.4 | Installation of Single Phase UPS with 20min battery back-up- make Online Systems | Nos. |  |  | 0
| TOTAL OF SECTION IX |  |  |  | 0
SECTION-XI-CCTV SYSTEM
10.1 | Laying of Following Items
10.1.1 | RG6 Co-axial cable | Mtr |  |  | 0
10.1.2 | 2 X 1.5 Sqmm FRLS Flexible Wire | Mtr |  |  | 0
10.1.3 | CAT-6 UTP cable for IP CAMERA | Mtr | 300 |  | 0
| TOTAL OF SECTION X |  |  |  | 0
SECTION-XI-MISCELLANEOUS
11.1 | Supplying the following data prior to handing over the installation to the owner. | job | 0 |  | 0
i) Megger Test Results in quadruplicate of all mains/submains/circuits/load feeders in tabulated format
i) In quadruplicate all`As built' drawings on blue prints, separate for
a | indoor lighting
b | outdoor lighting
c | Electrical cable system with sizes and routes
d | Main Earthing grid
f | conduit layout-to all the points from controlling DB's to be drawn along with indoor lighting
In general the drawings should show the sizes of cables, conduits and number of wires laid in conduit, outlets and lighiting layout,earthing conductor sizes, single line diagrams of each panel. Any other data like specifications, test certificates and maintenance manual of panels, Main LT panel etc. should also be furnished in quadriplicate
11.2 | Provision of ample amount of Temporary lights & sockets during construction stage | LS |  |  | 0
11.2.1 | Fixing of Hand Drier | Nos | 2 |  | 0
11.2.2 | Fixing of Pest-O-Flash | Nos | 8 |  | 0
11.2.3 | Supply & fixing of 100 x 100mm PVC Truff | Mtrs |  |  | 0
11.2.4 | Supply & fixing of Bulk Head Fitting | Nos |  |  | 0
11.2.5 | Fixing of Aircurtain | Nos | 2 |  | 0
11.2.6 | Supply & Laying of Rubber Mat, thinkness 10mm | Nos | 3 |  | 0
11.2.7 | Fixing of Wall Mounting Fan | Nos |  |  | 0
11.2.8 | Fixing of Heavy Duty Exhaust Fan | Nos |  |  | 0
11.2.9 | S & F of 6 & 16 Amp 3 Pin Top | Nos |  |  | 0
11.2.10 | Supply of 16" dia Wall Fan, make-havells/crompton/usha | Nos |  |  | 0
11.2.11 | Supply of 12" dia exhaust fans Normal PVC -make-havells/crompton/usha | Nos
11.2.12 | Supply & Fixing of Buzzer | Nos | 3 |  | 0
TOTAL OF SECTION XI
SECTION-XII-GAS DETECTION SYSTEM (Only Installation)
12.1 | 4 X 1.5 Sqmm FRLS Flexible Wire | Mtr |  |  | 0
12.2 | Installation Zicom make Gas Detector | No. |  |  | 0
12.3 | Installation Gas detection panel | No. |  |  | 0
| TOTAL OF SECTION XII |  |  |  | 0
SECTION-XIII-HUME PIPES
13 | PROVIDING AND LAYING HDPE/CPVE/HUME PIPES INSIDE THE TRENCH FOR UNDERGROUND CABLE PROTECTION
HDPE PIPES
13.1 | 100MM | Mtr. |  |  | 0
13.1 | 50MM | Mtr. |  |  | 0
13.1 | 32MM | Mtr. |  |  | 0
13,2 | Providing and fixing 230mm thick brick masonary inspection chamber of 450x 450mm size 1:4:8 C.C foundations 1:2:4 C.C including excavation smooth plastering from inside and rough plastering from oustisde, air tight cement cover lid with frame | No. |  |  | 0
| TOTAL OF SECTION XIII |  |  |  | 0

## FIRE FIGHTING
TFS DWARKA BASE KITCHEN MATIYALA
SUB-HEAD - A ( Fire Piping, Hydrants, Sprinklers and Accessories)
S.NO | DESCRIPTION | QTY | UNIT | RATE | AMOUNT
1 | Providing, laying, jointing and testing of following sizes of pipes conforming to IS-1239 with all accessories like all fittings (upto 50mm dia threaded M.S.forged fittings and above 50 mm dia MS fittings with welded joints shall be used)fittings including tees, elbows, reducers, flanges, rubber gaskets, nuts bolts, washer. And fixing the pipe on floor / wall /ceiling with suitable size clamps, hangers, structural steel supports as per specification. And PVC pipe sleeve to be provided wherever the pipes are crossing the walls/floors and sealing the sleeves as per consultants requirements including cutting holes and chases in brick, R.C.C work and making good the same to original conditions complete in all respects.Arrows showing direction of flow to be marked(with paint of approved colour) on each pipe at locations as decided at site.
(a) | For Fire fighting & sprinkler System - M.S. `C' Heavy class pipe
| a)25 mm dia(4.04mm thickness) screwed joint | 90 | RM |  | 0
| b)32 mm dia(4.05mm thickness)screwed joint | 10 | RM |  | 0
| c) 40 mm dia(4.05mm thickness)screwed joint | 20 | RM |  | 0
| d) 50 mm dia(4.5mm thickness)screwed joint | 15 | RM |  | 0
| e) 65 mm dia(4.5mm thickness) | 20 | RM |  | 0
| f) 80 mm dia(4.85mm thickness) | 100 | RM |  | 0
| g)100 mm dia(5.4mm thickness) | 10 | RM |  | 0
2 | Providing two coats of synthetic enamel paint of approved shade over a coat of primer. Including painting of legends both direction arrow as per the approval of the architects / consultants.
| a)25 mm dia | 90 | RM |  | 0
| b)32 mm dia | 10 | RM |  | 0
| c) 40 mm dia | 20 | RM |  | 0
| d) 50 mm dia | 15 | RM |  | 0
| e) 65 mm dia | 20 | RM |  | 0
| f) 80 mm dia | 100 | RM |  | 0
| g)100 mm dia | 10 | RM |  | 0
3 | Providing and fixing gun metal ball valve suitable for pressure 15 Kg/Cm2 and confirming to IS: 778 of the following size including providing necessary union / flange.
| a) 25 mm dia | 1 | NO. |  | 0
| b) 50 mm dia | 1 | NO. |  | 0
4 | Providing & fixing of butterfly valve suitable for pressure 15 Kg/Sqcm. with flanges, nut bolts & gaskets complete required.
| a) 65 mm dia | 1 | NO. |  | 0
| b) 80 mm dia | 3 | NOS |  | 0
| c) 100 mm dia | 2 | NOS |  | 0
5 | Providing and fixing of C.I. wafer type check valve suitable for pressure 15 Kg/Sqcm. with flanges, Nut, bolts & washers, painting etc. complete as required.
| a) 80 mm dia | 1 | NOS. |  | 0
| b) 100 mm dia | QR | NOS.
6 | Providing and fixing C.I.`Y' strainer with bronze perforated sheet basket tested to a pressure of 15 Kg/sqcm including rubber gasket, flanges, nuts, bolts and washers, complete as required.
| b) 100 mm dia | 1 | NO. |  | 0
7 | Providing & fixing gun metal fire hydrant valve with 80 mm N.B. flanged inlet, brass spindal, one no. 63 mm dia female instantaneous outlet type. G.M. coupling,blank cap, chain. Conforming to IS:5290. Including tapping from wet riser complete as required. | 1 | NOS |  | 0
8 | Providing & fixing swinging type First Aid hose reel in red colour with 36 mts long and 20 mm dia dia heavy duty rubber water hose, 20 mm dia globe valve stop cock, terminating with G.M. coupling & nozzle of 5mm outlet with shut off valve confirming to IS 8090 - 1976 complete with drum and brackets for fixing on wall, bolts & nuts conforming to IS:884-1969 complete as required. | 1 | NOS |  | 0
9 | Providing and Fixing Hose pipe, 63 mm dia and 15 mts long, duly reinforced, rubber lined suitable for brusting pressure not less than 22 Kg/Sqcm. conforming to IS 636-1988 type A with gun metal heavy duty instantaneous type coupling ( Pair male & female parts) conforming to IS 903. Complete as required (two nos. for each hydrant) | 2 | NOS |  | 0
10 | Providing and Fixing 63 mm dia instantaneous pattern branch short gunmetal pipe, 16 mm dia nozzle conforming to IS 903, suitable for inter connection to hose pipe coupling complete as required. | 1 | NOS |  | 0
11 | Providing and fixing standard firemans axe with heavy rubber handle. | 1 | NOS |  | 0
12 | Providing and fixing inlet breaching having C.I. body Two way gun metal 63 mm dia instantaneous inlets conforming to IS 903 fitted with non return valves, 25 mm dia gun metal drain cock, blank cap, brass chains and 100 mm dia flanges with all accessories suitable for local fire tender complete as required. | 1 | NO |  | 0
13 | Providing and fixing 4 mm thick glass door of size 2.1 m x 1.2 m with anodized aluminium frame of size 0.10 x 0.05 M with centre opening for fire hose cabinet. Suitably marked on the outside with the letters "FIRE HOSE" including locking arrangement. All aluminium work to be in Red P.O. colour. | 1 | NOS |  | 0
14 | Providing and fixing ISI Marked of approved make Fire Extinguishers complete with all accessories as per manufacturer's specifications.
| a) CO2 gas nozzle type - 4.5kg capacity (IS:15683). | 10 | NOS |  | 0
| b) Mechanical Foam gas cartridge type. 6 lts capacity (IS:15683). | 6 | NOS |  | 0
| c) ABC dry powder stored pressure type 9 kg capacity (IS:15683). | 10 | NOS |  | 0
15 | Supplying, installing, testing and commissioning of HDPE water storage tank including holes for inlet, outlet, overflow level indicator drain and vent points, manhole cover suitable supporting structure complete.
| a) Capacity 5000 Lts. | 4 | NOS |  | 0
16 | Approval of fire (NOC) system from local fire authority at initial & various other stages of works, including preperation of report / integration with Fire alarm system and preparation of drawings as per local fire authority. Contractor shall include cost of all liasion works which are not explicity mentioned above but are mendatory to have fire authority approved. | 1 | No |  | 0
17 | Providing & fixing C.P.brass quartzoid bulb sprinklers of size 15mm dia to be operated at 68Deg.C complete.Make of rosette plate- Veekay/Sainath fire/Safeworld/approved equal.
| a) Pendant type with heavy duty adjustable SS rosette plate | 44 | NOS. |  | 0
| b) Side wall extended throw type with heavy duty adjustable SS rosette plate | 2 | NOS. |  | 0
| c) Concealed type | QR | NOS.
| d) Upright type | QR | NOS.
18 | Providing & Fixing of installation control valve with turbine type automatic Alarm Gong to be connected with control valve, drain & test valve as per manufacturer's specifications complete.
| a) 80 mm dia | 1 | NO |  | 0
19 | Providing, jointing and testing of sprinklers through flexible connections(internal diameter 25mm & outlet connection15mm dia.) as per requirement at site.Make-SeungJin-Korea.The flexible connectors shall be supported through false ceiling through clamps or as directed at site.The flexible connector shall be suitable for working pressure12 kg/sqcm . | 44 | NOS |  | 0
20 | Providing & installing MS 24 gauge fire buckets ( capacity of each bucket = 9 lts) filled with sand including MS stand for hanging the buckets.All MS items shall be painted with two coats of primer & two coats of paint of approved colour.
| Set of four buckets with stand | 2 | NOS |  | 0
21 | Supply, installation, testing and commissioning of Down comer pump comprising of the following:
(a) | Horizontally mounted centrifugal pump, suitable for operation on 415 volts ± 10%, 3 phase, 50 HZ A.C supply. Fire pump having C.I. body, bronze impeller and S.S. Shaft with mechanical seal, capable for deliverying 900 LPM of water at 35 mts. head. Complete with necessary pressure gauge with gun metal shut off cock and syphon on delivery side. The pump should meet the condition of Local fire Authority. Cost shall include electrical control panel with wiring/cabelling /control cabelling complete to make the system operational as per requirement of Fire Authorities.
(b) | Squirrel cage induction motor TEFC type for operation on 415 V, 3 phase 50 HZ AC supply for the above pump with a synchronous speed of 2900 R.P.M. with flexible coupling and coupling guard etc. as required.
(c) | Common base plate for (a) and (b) from M.S. channel as required size.
(d) | Suitable cement concrete foundation with plaster, Antivibration arrangement of cushy foot mounting. | 1 | NO |  | 0
| TOTAL CARRIED TO SUMMARY |  |  |  | 0

## HVAC
SCHEDULE OF QUANTITIES (as on 26-09-24)-R0
S. NO | ITEM DESCRIPTION | UNIT | QTY. | RATE | AMOUNT | REMARKS
SECTION 'A' - HVAC WORK
1.0 | EQUIPMENT
1.1 | SPLIT UNITS
Supply , Installation, Testing and Commissioning of split units, each comprising of an outdoor and a single indoor unit as shown on the drawings and as per the specifications. Enclosures shall be factory fabricated and painted to a smooth finish. Oudoor unit shall consist of hermatically sealed/ semi- hermatic scroll/rotary compressor/s, air cooled condenser with fan. Indoor unit shall consist of fan section with dynamically balanced centrifugal fan/s driven by FHP/TEFC squirrel cage induction motor, multirows deep DX- copper cooling coil with aluminium fins, thermostatic expansion valve, synthetic fibre filters, insulated drain pan, safety controls, safety controls, thermostat all complete in a unit. The quoted price shall be inclusive of full charge of refrigerant gas, vibration isolation arrangement.
Refrigerant Shall be R-32/R410A/R407C
A. | Three phase ductable split units with Scroll compressor :
Unit should be suitable to handle total 35-40RM inter
unit referigerant piping inlcuding 12-15RM vertical length.
a. | 11.0TR nominal capacity, split unit with single ductable type indoor unit and factory fitted electrical arrangement & corded remote. | No | - |  |  | Rate Only
b. | 8.5TR nominal capacity, split unit with single ductable type indoor unit and factory fitted electrical arrangement & corded remote. | No | 1 |  | 0
c. | 5.5TR nominal capacity, split unit with single ductable type indoor unit and factory fitted electrical arrangement & corded remote. | No | - |  |  | Rate Only
d. | 4.0TR nominal capacity, split unit with single ductable type indoor unit and factory fitted electrical arrangement & corded remote. | No | - |  |  | Rate Only
e. | 3.5TR nominal capacity, split unit with single ductable type indoor unit and factory fitted electrical arrangement & corded remote. | No | - |  |  | Rate Only
B. | Three phase non-ductable split units with rotary compressor (Three Star Rating) :(Units should be suitable to handle piping length upto 24-25 RM)
a. | 2.5TR nominal capacity, split unit with single Cassette type indoor unit and cordless control . Price shall be inclusive of copper power cabling from indoor to outdoor unit as required. | No | - |  |  | Rate Only
C. | Single phase Non-ductable split units with Rotary compressor (Three Star Rating) :(Units should be suitable to handle piping length upto 24-25 RM)
a. | 1.5TR nominal capacity, split unit with single Wall Mounted type indoor unit and cordless control . Price shall be inclusive of copper power cabling from indoor to outdoor unit as required. | No | 2 |  | 0
b. | 1.5TR nominal capacity, split unit with single Cassette type indoor unit and cordless control . Price shall be inclusive of copper power cabling from indoor to outdoor unit as required. | No | - |  |  | Rate Only
1.2 | Supply, Installation , Testing and
Commissioning of PLC for Auto Sequencing
of Split units with micrprocessor based
controller along with enclosure/accessories & Control wiring
having facility for configuration of the same
as per requirement for sequenced Start/Stop
for following split units :
a. | Three number Split units including one standby for Server Room. | Sets | - |  |  | Rate Only
1.3 | REFRIGERANT PIPING
Supply, Installation,Testing & Commissioning of copper refrigerant piping complete with copper fittings & charge of regrigerant gas for the above split units. Piping associated with split units to be insulated with 19mm thick closed cell elastomeric insulation with Class 'O' in tubing form as required. Piping shall be laid over duly painted slotted angle trays fixed with GI clamps. Quoted Price shall be inclusive of UV protection paint for all exposed pipes of approved make. Price shall be inclusive of copper power cabling from indoor to outdoor unit as required. Referigerant piping shall be epoxy coated to prevent erosion.
a. | Pair of hard drawn copper refrigerant piping for the above split units with scroll compressor. | RM | 25 |  | 0
b. | Pair of Soft refrigerant piping for non ductable split units with rotary compressor. | RM | 55 |  | 0
1.4 | STABILISERS
Supply, Installation,Testing & Commissioning of automatic voltage stabilisers suitable for operation on 140-280 V incoming supply supply with time delay relay for single phase split units.
| a. 4 KVA Capacity | No | - |  |  | Rate Only
| b. 5 KVA Capacity | No | - |  |  | Rate Only
1.5 | DRAIN PUMP
Supply, Installation,Testing & Commissioning of drain pump for Hi-wall split units complete with all accessories as required. Drain Pump shall be suitable for operation on 220+6 % volts 50 Hz,1phase AC power supply.
a. | Drain pump for Hi-wall split units (Server Room / UPS Room) | Nos. | - |  |  | Rate Only
1.6 | MS FRAME FOR ODUs
Supply and Erection of MS base frame duly
applied with red-oxide primer & followed by
| black enamel paint for mounting of outdoor units. | Kg | 55 |  | 0
SUB TOTAL (EQUIPMENT) Rs. | TOTAL ITEM NO. 1 (EQUIPMENT) |  |  | Rs. | 0
2.0 | PIPING
2.1 | CONDENSATE DRAIN PIPING
2.1.1 | USING GI PIPING
Supply, Installation , Testing and Commissioning of GI medium class (Class 'B') pipes cut to requird lengths and installed with all screwed joints for condensate drain. Quoted price shall be inclusive of supply and fixing in position the necessary fittings like elbows, tees reducers etc., and supporting arrangement in accordance with the approved shop drawings and specifications.Pipes shall be insulated with 9mm thick closed cell elastomeric insulation with class 'O' fire retardant properties in tubing form . Pipes shall be of following sizes :
a. | 65mm dia | RM | - |  |  | Rate Only
b. | 50mm dia | RM | - |  |  | Rate Only
c. | 40mm dia | RM | - |  |  | Rate Only
d. | 25mm dia | RM | - |  |  | Rate Only
2.1.2 | CONDENSATE DRAIN PIPING -cPVC
Supply, Installation, Testing and Commissioning of cPVC pipes cut to required lengths and installed for condensate drain. Quoted price shall be inclusive of supply and fixing in position the necessary fittings like elbows, tees reducers etc. and supporting arrangement in accordance with the approved shop drawings and specifications. Pipes shall be insulated with 9mm thick closed cell elastomeric insulation with class 'O' fire retardant properties in tubing form . Pipes shall be of following sizes :
a. | 50mm dia | RM | 5 |  | 0
b. | 40mm dia | RM | 10 |  | 0
c. | 32mm dia | RM | 2 |  | 0
d. | 25mm dia | RM | 5 |  | 0
| TOTAL ITEM NO. 2 (PIPING ) |  |  | Rs. | 0
3 | DUCTWORK/AIR TERMINALS
3.1 | FACTORY FABRICATED DUCTING
Supply , Installation and Testing of factory fabricated GSS ducting complete with vanes, splitter dampers, fire retardant gaskets hanging arrangement including fully threaded GI rods and GI "C" channels, GI "C" channels etc. as approved by clients/consultants in accordance with the approved shop drawings and specifications. Quoted price shall be inclusive of necessary scaffolding charges towards installation of supply/exhaust air ducts outside or within building wherever required. Quoted price should also include necessary charges towards duct supporets including MS angle/channel arrangement as required for ducts being installed outside or within building wherever required.
Spacing between duct supports should not exceed 2m. All duct support to be provided with check nuts (lock nuts).
While selecting the duct supports vendor shall ensure vibration free installation.Quoted price shall be inclusive of smoke test using smoke bombs.
a. | 1mm to 899mm -- 26G GSS with TDC Joints | SqM | 5 |  | 0
b. | 900mm to 1200mm -- 24G GSS with TDC Joints | SqM | 10 |  | 0
c. | 1201mm to 1800mm - 22G GSS with TDC Joints | SqM | 5 |  | 0
d. | 1801mm to 2100mm - 20G GSS with TDC Joints | SqM | - |  |  | Rate Only
e. | 2101mm to 2700mm - 18G GSS with TDC Joints | SqM | - |  |  | Rate Only
3.2 | SITE FABRICATED DUCTING
Supply, Fabrication, Installation and Testing of sheet
metal ducts complete with vanes, splitter dampers,
hanging arrangement including check nuts in
accordance with the approved shop drawings
and specifications
| a. 0.63mm (24 gauge) GSS | SqM | 10 |  | 0
| b. 0.8 mm (22 gauge) GSS | SqM | 5 |  | 0
| c. 1.0mm (20 gauge) GSS | SqM | - |  |  | Rate Only
| d. 1.25mm (18 gauge) GSS | SqM | - |  |  | Rate Only
3.3 | FLAT OVAL SPIRAL DUCT
Supply, Installation and Testing of factory fabricated & factory internally insulated GSS flat oval spiral ducting complete with vanes,splitter dampers, fire retardant gaskets hanging arrangement including fully threaded GI rods , GI straps and GI "C" channels/ rolled steel wires or Gripple Wire Rope Hangers & Supports complete with end fixing, GI "C" channels etc. as approved clients/consultants in accordance with the approved shop drawings and specifications.Quoted price shall be inclusive of necessary scaffolding charges towards installation of supply/exhaust air ducts outside or within building wherever required.
Duct Insulation shall be as follows :
20mm thick open cell nitrile rubber insulation of density within 140-180 Kg/m3 with perforated aluminium foil.
Ducts shall be factory powder coated of colour and
shade as approved by the Architects for exposed spiral
ducts. Quoted price shall be inclusive of powder coating.
Necessary compliance to be submitted by vendors.
Without Powder Coated-With 9mm thick insulation
a. | 1mm to 600mm -- 24G GSS | SqM | - |  |  | Rate Only
b. | 601mm to 1200mm -- 22G GSS | SqM | - |  |  | Rate Only
c. | 1201mm to 1700mm -- 20G GSS | SqM | - |  |  | Rate Only
Without Powder Coated-With 13mm thick insulation
a. | 1mm to 600mm -- 24G GSS | SqM | - |  |  | Rate Only
b. | 601mm to 1200mm -- 22G GSS | SqM | - |  |  | Rate Only
c. | 1201mm to 1700mm -- 20G GSS | SqM | - |  |  | Rate Only
3.4 | ENAMEL PAINT (For Exposed Duct) - LOW VOC
| Supply and Application of minimum two coats of Enamel of colour and shade as approved by the Architects for exposed ducts. Quoted price shall be inclusive of primer before paint and all neceesary arrangement as required for providing the paint over duct. | SqM | - |  |  | Rate Only
3.5 | FLEXIBLE CANVASS CONNECTIONS
| Supply, Installation, Testing of 125mm deep antivibration flexible joints at the outlet of air handling units/ductable split units//inline fans. Flexible connections shall be constructed using imported fire retardant fabric with extruded aluminium frame/flange on both sides of approved make. | RM | 4 |  | 0
3.6 | SUPPLY AIR DIFFUSERS
3.6.1 | Supply, Installation, Testing and Balancing of square supply air diffusers with removable key operated volume control dampers with opposed blades as per the approved shop drawings and specifications.The diffusers shall be anti-smudge ring type/flat type as approved by the interior designer. Diffusers shall be with removable core for the following neck sizes. The diffusers shall be suitable for fixing in the gypsum ceiling. The diffusers shall be of regular type and with outer dimension of 450 x 450mm, 375mmx375mm & 300mmx300mm.
| Powder coated extruded aluminium diffusers of approved colour & shade. | SqM | - |  |  | Rate Only
3.5.2 | Supply, Installation, Testing and Balancing of square supply air diffusers with removable key operated volume control dampers with opposed blades & 150mm high GSS plenum as per the approved shop drawings and specifications.The diffusers shall be anti-smudge ring type/flat type as approved by the interior designer. Diffusers shall be with removable core for the following neck sizes. The diffusers shall be suitable for fixing in the gypsum/grid ceiling. The diffusers shall be of regular type and with outer dimension of 600 x 600mm.
| 600x600 Powder coated extruded aluminium diffusers of approved colour & shade suitable for fixing in grid ceiling. | No | - |  |  | Rate Only
3.6 | RETURN AIR DIFFUSERS
3.6.1 | Supply, Installation,Testing and Balancing of square return air diffusers same as supply air diffusers but without volume control dampers as per the approved shop drawings and specifications. The diffusers shall be anti -smudge ring type.
| Powder coated extruded aluminium diffusers of approved colour & shade. | SqM | - |  |  | Rate Only
3.6.2 | Supply, Installation,Testing and Balancing of square return air diffusers same as supply air diffusers but without volume control dampers as per the approved shop drawings and specifications. The diffusers shall be anti -smudge ring /flat type.
| 600x600 Powder coated extruded aluminium diffusers of approved colour & shade suitable for fixing in grid ceiling. | No | - |  |  | Rate Only
3.7 | LINEAR GRILLES
Supply, Installation , Testing and Balancing of one way blow linear supply cum return air grilles complete with fixed core as per approved shop drawings and specifications. The grilles shall be of approved colour & shade.
Powder coated aluminium grilles of extruded sections with integral flanges on both sides & ends as required complete with corner pieces.
| i. 100/150/200/250 mm High grilles | SqM | 1 |  | 0
3.7 | DOUBLE LOUVERED GRILLES
Supply, Installation ,Testing and Balancing of double
louvered supply air grilles as per approved shop drawings
and specifications complete with key operated aluminium
volume control dampers.
| a. Powder coated extruded aluminium grilles. | SqM | 0.5 |  | 0
3.8 | AIR TRANSFER GRILLES
| Supply, Installation and Testing of extruded aluminium powder coated air transfer grilles to be provided at the door of toilets/pantry. | SqM | 0.2 |  | 0
3.9 | Supply, Installation, Testing and Balancing of linear slot diffusers with Hit & Miss type extruded aluminium volume control dampers at supply air outlets as per the approved shop drawings and specifications.
a. | 3 slot/2slot, powder coated extruded aluminium diffusers of approved colour & shade for supply air with Hit & Miss type dampers | SqM | - |  |  | Rate Only
b. | 3 slot/2slot, powder coated extruded aluminium diffusers of approved colour & shade for return air without Hit & Miss type dampers | SqM | - |  |  | Rate Only
3.1 | ROUND DIFFUSERS
Supply, Installation, Testing and Balancing of
round supply air diffusers with removable key operated
butterfly volume control dampers as per the approved shop
drawings and specifications.The diffusers shall be anti-
smudge flush type as approved by the interior designer.
Diffuser shall be complete with GI cone with circular
connection at the rear.
Powder coated extruded aluminium diffusers of
approved colour & shade :
3.10.1 | With Volume Control Dampers
a. | 400mm dia round diffuser with GI cone | No | - |  |  | Rate Only
b. | 300mm dia round diffuser with GI cone | No | - |  |  | Rate Only
c. | 200mm dia round diffuser with GI cone | No | - |  |  | Rate Only
3.10.2 | Without Volume Control Dampers
a. | 400mm dia round diffuser with GI cone | No | - |  |  | Rate Only
b. | 300mm dia round diffuser with GI cone | No | - |  |  | Rate Only
c. | 200mm dia round diffuser with GI cone | No | - |  |  | Rate Only
3.11 | Supply, Installation,Testing and Balancing of
flexible ducting comprising of inner as well as outer
skin constructed out of aluminium & fibre glass
insulation 25mm thick of minimum 24 kg/cu.m density
insulation sandwitched in between. Duct should confirm
to fire rating standards BS-476 part 5, 6 & 7. Flexible
Ducts of following sizes as per approved shop drawings,
specifications :
a. | 300 mm dia | RM | - |  |  | Rate Only
b. | 250 mm dia | RM | - |  |  | Rate Only
c. | 200 mm dia | RM | - |  |  | Rate Only
d. | 150 mm dia | RM | - |  |  | Rate Only
3.12 | Supply, Installation and Testing of single
piece GI round spigot made out of spinning process
with 50mm height and having grooves on both sides
and circular flanges. Spigots shall be installed on main
ducts to facilitate connection of flexible ducts.
a. | 300 mm dia | No | - |  |  | Rate Only
b. | 250 mm dia | No | - |  |  | Rate Only
c. | 200 mm dia | No | - |  |  | Rate Only
d. | 150 mm dia | No | - |  |  | Rate Only
3.13 | Supply, Installation and Testing of Butterfly damper
of aluminium sheet construction with two flap with
sleeve as per thespecifications and shop drawings.
a. | 200 mm dia | No | - |  |  | Rate Only
b. | 250 mm dia | No | - |  |  | Rate Only
c. | 300 mm dia | No | - |  |  | Rate Only
d. | 375 mm dia | No | - |  |  | Rate Only
3.14 | Supply, Installation and Testing of GI box type
volume control dampers as per the specifications
| and shop drawings.- For Rectangular Duct | SqM | 0.5 |  | 0
3.15 | Supply, Installation and Testing of GI box type
volume control dampers as per the specifications
| and shop drawings.- For Flat Oval Ducts | SqM | - |  |  | Rate Only
3.16 | Supply, Installation and Testing of GI multi blade
type louver dampers as per the specifications
| and shop drawings. | SqM | 1 |  | 0
3.17 | Supply, Installation,Testing and Commissioning
of motorised fire dampers suitable for at least
90 minutes fire rating as per the specifications
and approved shop drawings. Quoted price shall
be inclusive of copper control wiring as required.
a. | Bare Fire Dampers | SqM | - |  |  | Rate Only
b. | Spring return action type actuator complete with
| control panel and temperature sensor. Torque not less | No | - |  |  | Rate Only
than 16NM
3.18 | Supply, Installation and Testing of fresh air
grilles of powder coated / anodised extruded
aluminium with GI wire mesh, inlet louvers,
Box type VCD & bird screen, as per the approved
| shop drawings and specifications. | SqM | -- |  |  | Rate Only
3.19 | Supply, Installation and Testing of extruded aluminium
powder coated louver with GI wire mesh to be installed
outside for discharge of exhaust air from exhaust fans
as per the specifications and shop drawings.
Sample of louvers to be got approved from consultants
| and Clients prior to procurement. | SqM | -- |  |  | Rate Only
3.2 | Supply, Installation and Testing of Bird Screens with GI
wire mesh to be installed at the suction of fresh air/discharge
of Exhaust air as per the specifications and shop drawings.
Sample of bird screen to be got approved from consultants
| and Clients prior to procurement. | SqM | -- |  |  | Rate Only
3.21 | Supply, Installation and Testing of non return dampers.
NRDs to be installed in the ducts as per
the specifications and shop drawings.
Sample of NRDs to be got approved from consultants
| and Clients prior to procurement. | SqM | -- |  |  | Rate Only
3.22 | Motorised VCD
a. | Supply, Installation and Testing of multiblade box type zero leakage extruded aluminium dampers for ducts to be provided with suitable links, levers and quadrants for manual control of volume of air flow and for proper balancing of the air distribution system as per the approved shop drawing and specifications. | SqM | -- |  |  | Rate Only
b. | Supply and fixing of actuators of suitable rating of torque complete with, conrtrol panel, transformer, copper wiring from the junction box and actuator associated with the above VCDs.
| Actuator shall be suitable for duct size as shown in the drawing. | No | -- |  |  | Rate Only
TOTAL (AIR DISTRIBUTION) Rs. | TOTAL ITEM NO.3 (Ducting & Air Terminals) |  |  | Rs. | 0
4 | INSULATION
4.1 | ACOUSTIC LINING OF DUCTS
4.1.1 | Using Open Cell Nitrile Rubber
Supply and Application of internal acoustic lining of supply air ducting using open cell nitrile rubber insulation with density within 140-180 Kg/m3 as per the approved shop drawings and specifications. Insulation material shall be bonded with the ducts using metal screw and washers to facilitate grip to the GI sheet. Adhesive used shall be Low VOC type.
a. | 10mm thick lining | SqM | 5 |  | 0
4.1.2 | Using Fibre Glass
Supply and Application of internal acoustic
lining of supply/return air ducting using resin bonded
fibre glass insulation of density not less than 32Kg/CuM
as per the approved shop drawings and specifications.
Quoted price shall be inclusive of GSS channel, metal
screws, washers, fibre glass tissue, perforated sheet
etc. as required for complete installation.
a. | 25mm thick lining | SqM | 10 |  | 0
4.2 | THERMAL INSULATION OF DUCTS
(Using Factory Laminated aluminium foil faced,
Class 'O' Closed Cell Elastomeric insulation)
Supply and Application of internal / external thermal insulation of
supply /return air ducting using closed
cell elastomeric insulation with class 'O' fire retardant
properties as per the specifications and drawings.
Adhesive used shall be Low VOC type.
a. | 9mm thick insulation- S/Air Duct in contact with R/Air | SqM | -- |  |  | Rate Only
b. | 13mm thick insulation | SqM | 30 |  | 0
c. | 16mm thick insulation (Fresh air duct in ac area) | SqM | -- |  |  | Rate Only
TOTAL (AIR DISTRIBUTION) Rs. | TOTAL ITEM NO. 4 (INSULATION) |  |  | Rs. | 0
SECTION "B" : KITCHEN VENTILATION SYSTEM
S.NO | ITEM DESCRIPTION | UNIT | QTY. | RATE | AMOUNT | AMOUNT
1 | EQUIPMENT
1.1 | DOUBLE SKIN AIR COOLING MACHINES - With Fresh Air Intake Section
(AIR WASHERS)
Supply , Installation, Testing and Commissioning of
double skin type evaporative air cooling machines
(packaged type) each comprising of following as
per the specifications :
a. | Casing of air washer shall be in double skin | Casing of air washer shall be in double skin construction. Inner skin shall be constructed out of24 gauge plain GS sheet & outer skin in 24 gauge pre-plasticized GS sheet sandwitched between 50mm thick injected PU foam insulation of density not less than 40 Kg /CuM and complete with marine light,limit switch & inspection doors including control wiringas required. Air washer shall have access for all parts.
construction. Inner skin shall be constructed out of
24 gauge plain GS sheet & outer skin in 24 gauge
pre-plasticized GS sheet sandwitched between
50mm thick injected PU foam insulation of density
not less than 40 Kg /CuM and complete with marine light,
limit switch & inspection doors including control wiring
as required. Air washer shall have access for all parts.
b. | Fan section complete with backward curved DIDW | Fan section complete with backward curved DIDW type centrifugal fan/s, EFF1, IE3, IP-55, rated TEFC squirrel cageinduction motor suitable to operate on 415+10%V, 50Hz,3 phase AC power supply and belt drive package.Centrifugal fans shall be coated with epoxy paint as specified. Fan outlet velocity shall not be more than 2000 FPM (10.16 MPS).All fans should be AMCA certified.
type centrifugal fan/s, EFF1, IE3, IP-55, rated TEFC squirrel cage
induction motor suitable to operate on 415+10%V, 50Hz,
3 phase AC power supply and belt drive package.
Centrifugal fans shall be coated with epoxy paint as specified.
Fan outlet velocity shall not be more than 2000 FPM
(10.16 MPS).
All fans should be AMCA certified.
c. | AirWasher shall be provided with Intake Section with | AirWasher shall be provided with Intake Section withF/A openings as per approved shop drawing.
F/A openings as per approved shop drawing.
d. | Air washer wet section shall be complete with 300mm | Air washer wet section shall be complete with 300mm thick cellulose based paper fills, drift eliminators,water distribution system complete with FRP spray headers, strainer of fine mesh brass screen, globe valve,float valve, quick fill, over flow & drainconnections, GI medium class piping and 3/1 phasemonobloc pumps of 1HP/ 1.5HP/2HP motor rating as required according to the capacity of air cooling machines. Inner skin of wet section including fills mounting frame shall be constructed out of stainless steel SS- 304 A grade of appropriate thickness .Sump shall be made out of 1.25mm thick SS-304 A grade stainless steel .Velocity across the paper fills not to exceed 500 FPM.
thick cellulose based paper fills, drift eliminators,
water distribution system complete with FRP spray
headers, strainer of fine mesh brass screen, globe valve,
float valve, quick fill, over flow & drain
connections, GI medium class piping and 3/1 phase
monobloc pumps of 1HP/ 1.5HP/2HP motor rating
as required according to the capacity of air cooling
machines. Inner skin of wet section including fills
mounting frame shall be constructed out of stainless
steel SS- 304 A grade of appropriate thickness .Sump
shall be made out of 1.25mm thick SS-304 A grade
stainless steel .Velocity across the paper fills not to
exceed 500 FPM.
e. | Filter section complete with 50mm thick aluminium | Filter section complete with 50mm thick aluminiumwire mesh viscous metallic filters. Velocity across the filters shall not exceed 500 FPM. Airwasher should be provided with adequate space between eliminator & fan to avoid water carryover.The Evaporative Air Cooling Machines (EAC) shall be of following duty parameters :M/c No Capacity S.P Motor Area to (Cfm) (mmWG) Rating be fed (HP)EAC-1 1x22500 58-60 1x15.0 Kitchen
wire mesh viscous metallic filters. Velocity across
the filters shall not exceed 500 FPM.
Airwasher should be provided with adequate space between eliminator & fan to avoid water carryover.
The Evaporative Air Cooling Machines (EAC) shall
be of following duty parameters :
M/c No Capacity S.P Motor Area to
(Cfm) (mmWG) Rating be fed
(HP)
| EAC-1 1x22500 58-60 1x15.0 Kitchen | No | 1 |  | 0
1.2 | SCRUBBER (For Kitchen Exhaust)
1.2.1 | WET TYPE SCRUBBER
Supply , Installation , Testing and Commissioning of
wet type scrubber (packaged type) comprising
of following as per the specifications :
a. | Fan section complete with backward curved DIDW
type centrifugal fan/s, TEFC squirrel cage induction
motor suitable to operate on 415+10%V, 50Hz,
3 phase AC power supply and belt drive package.
Casing of wet type scrubber shall be constructed
out of 16 gauge GS sheet complete with inspection
doors as required. Centrifugal fans shall be coated
with epoxy paint as specified. Fan outlet velocity
shall not be more than 2000 FPM (10.16 MPS).
b. | Wet section complete with double bank spray header in
GI construction and nozzles, louvers PVC mist eliminators
& mist collection tray made out of 16G GSS,
strainer of fine mesh brass screen, globe valve,
float valve, quick fill, over flow & drain
connections, GI medium class piping and 3 phase
monobloc pump of 1.5HP motor rating
as required according to the capacity of scrubber
machines. Wet section including sump will be made of
1.25mm thick SS-304 A grade stainless steel .
c. | In addition to the above, scrubber shall be
provided with adequate vibration isolation pads
and fire retardent flexible canvass connections made
out of canvass sleeve.
The Scrubber Machines (EAC) shall be of following
duty parameters :
M/c No Capacity S.P Motor Area to
(Cfm) (mmWG) Rating be fed
(HP)
| WS-1 28000 68-70 20.0 Kitchen Area | No | 1 |  | 0
1.3 | AIR CURTAIN
Supply , Installation and Testing of
air curtains with noiseless, statically & dynamically
balanced aluminium blowers, cleanable type
pre-filters, motor & powder coated
aluminium enclosure as per the specifications.
Unit shall be complete with Plug Top & necessary
power cable.
a. | 2.4 M long air curtain | No | - |  |  | Rate Only
b. | 2.1 M long air curtain | No | 1 |  | 0
c. | 1.5 M long air curtain | No | 2 |  | 0
d. | 1.2 M long air curtain | No | -- |  |  | Rate Only
(Actual size & qty of air Curtain shall be as per approved shop drawing)
1.4 | VENTILATION FANS
1.4.1 | INLINE FANS (Single Phase)
Supply, Installation, Testing & Commissioning of circular /rectangular inline fans for exhaust air complete with sheet metal casing, direct driven centrifugal fan, motor with proper protection and inspection door. Fan shall be suitable for operation on 220+6 % volts, 50 Hz,1phase AC power supply. Fan shall be installed as shown in the drawings and will be of following characteristics : All single phase inline fans shall be provided with factory fitted speed regulators. All Fans Should be complete with Plug Top & necessary power cable.
Fan Capacity S.P Area to
No. (Cfm) (mmWG) to be exhausted
| IF-1(Circular) 300 14-15 Pantry | No | 1 |  | 0
| TOTAL ITEM NO. 1 (EQUIPMENT) |  |  | Rs. | 0
2 | DUCTWORK/AIR TERMINALS - INCLUDING IN SECTION 'A'
2.1 | FACTORY FABRICATED DUCTING
Supply, Installation and Testing of factory fabricated GSS ducting complete with vanes,splitter dampers, fire retardant gaskets, hanging arrangement including fully threaded GI rods and GI "C" channels/ rolled steel wires or Gripple Wire Rope Hangers & Supports complete with end fixing, GI "C" channels etc. as approved by clients/consultants in accordance with the approved shop drawings and specifications. Quoted price shall be inclusive of necessary scaffolding charges towards installation of supply/exhaust air ducts outside or within building wherever required.
Spacing between duct supports should not exceed 2m in both cases i.e GI rods with GI "C" channels & Gripple Wire Rope Hanger support . In case of Gripple Wire Rope Hanger support for duct sizes above 1800mm, MS angles duly painted with black enamel paint should be used along with neoprene pad in between the duct & MS angle. All duct supports shall be provided with check nuts (lock nuts).
While selecting the duct supports vendor shall ensure
vibration free installation.Quoted price shall be inclusive of smoke
test using smoke bombs.
For Air-Cooling ducts
a. | 1mm to 899mm -- 24G GSS with TDC Joints | SqM | 50 |  | 0
b. | 900mm to 1500mm -- 22G GSS with TDC Joints | SqM | 50 |  | 0
c. | 1501mm to 2100mm - 20G GSS with TDC Joints | SqM | 10 |  | 0
d. | 2101mm to 2700mm - 18G GSS with TDC Joints | SqM | -- |  |  | Rate Only
2.2 | DUCO PAINT (For Exposed Duct)
| Supply and Application of minimum two coats of Duco of colour and shade as approved by the Architects for exposed ducts. Quoted price shall be inclusive of primer before paint and all neceesary arrangement as required for providing the paint over duct. | SqM | -- |  |  | Rate Only
2.3 | SITE FABRICATED DUCTING
Supply, Fabrication, Installation and Testing of sheet metal ducts complete with vanes, splitter dampers, hanging arrangement including check nuts in accordance with the approved shop drawings and specifications.
| a. 0.63mm (24 gauge) GSS | SqM | 15 |  | 0
| b. 0.8 mm (22 gauge) GSS | SqM | 5 |  | 0
| c. 1.0mm (20 gauge) GSS | SqM | 5 |  | 0
| d. 1.25mm (18 gauge) GSS | SqM | - |  |  | Rate Only
2.4 | For Kitchen Exhaust
Supply, fabrication, Installation and testing of MS ducting
for kitchen exhaust contructed out of 2mm thick
MS sheet using MS angle iron flanges in line with
good engineering practice. Entire ducting shall be
applied with minimum two coats of red oxide primer.
| Duct shall be provided with oil trap as required | SqM | 140 |  | 0
2.5 | FLEXIBLE CANVASS CONNECTIONS
| Supply, Installation, Testing of 125mm deep antivibration flexible joints at the outlet of air handling units/ductable split units//inline fans. Flexible connections shall be constructed using imported fire retardant fabric with extruded aluminium frame/flange on both sides of approved make. | RM | 8.5 |  | 0
2.6 | LINEAR GRILLES
Supply, Installation , Testing and Balancing of one way blow linear supply cum return air grilles complete with fixed core as per approved shop drawings and specifications. The grilles shall be of approved colour & shade.
Powder coated aluminium grilles of extruded sections with integral flanges on both sides & ends as required complete with corner pieces.
| i. 100/150/200/250 mm High grilles | SqM | 8 |  | 0
2.7 | AIR TRANSFER GRILLES
| Supply, Installation and Testing of of extruded aluminium powder coated air transfer grilles to be provided at the door of toilets/pantry. | SqM | - |  |  | Rate Only
2.8 | Supply, Installation and Testing of GI box type
volume control dampers as per the specifications
| and shop drawings. | SqM | 3.5 |  | 0
2.9 | Supply, Installation and Testing of Aluminium multi blade
type louver dampers as per the specifications
| and shop drawings. | SqM | 6 |  | 0
2.1 | Supply, Installation and Testing of fresh air
powdered coated / anodised extruded aluminium
louvers to be installed outside for suction ( airwashers),
as per approved shop drawings and specifications.
Sample of louvers to be got approved from consultants
| and Clients prior to procurement. | SqM | 1 |  | 0
2.11 | Supply, Installation and Testing of Bird Screens with GI
wire mesh to be installed at the suction of fresh air/discharge
of Exhaust air as per the specifications and shop drawings.
Sample of bird screen to be got approved from consultants
| and Clients prior to procurement. | SqM | 1 |  | 0
2.12 | Supply, Installation and Testing of non return dampers.
NRDs to be installed in the ducts as per
the specifications and shop drawings.
Sample of NRDs to be got approved from consultants
| and Clients prior to procurement. | SqM | - |  |  | Rate Only
| TOTAL ITEM NO. 2 (Ducting & Air Terminals) |  |  | Rs. | 0
3.0 | INSULATION
3.1 | THERMAL INSULATION OF DUCTS-(FOR AIR SCRUBBER DUCT)
(Using Factory Laminated fibre glass insulation)
Supply and Application of external thermal
insulation of supply /return air ducting using
aluminium foil faced fibre glass insulation of density
not less than 24Kg/CuM and aluminium foil thickness of 22
microns as per the specifications and drawings. Quoted
price shall be inclusive of Low VOC adhesive as required,
aluminium tape straps.
a. | 25mm thick insulation | SqM | - |  |  | Rate Only
b. | 50mm thick insulation | SqM | 140 |  | 0
3.2 | THERMAL INSULATION OF DUCTS-(FOR AIR SCRUBBER DUCT) - EXPOSED
(Using Factory Laminated fibre glass insulation)
Supply and Application of external thermal
insulation of supply /return air ducting using
aluminium foil faced fibre glass insulation of density
not less than 24Kg/CuM and aluminium foil thickness of 22
microns as per the specifications and drawings. Quoted
price shall be inclusive of Low VOC adhesive as required,
aluminium tape straps. Insulation shall be covered necessary
glass cloth & UV protection paint.
a. | 25mm thick insulation | SqM | - |  |  | Rate Only
b. | 50mm thick insulation | SqM | 15 |  | 0
3.3 | THERMAL INSULATION OF DUCTS - Air Washer
(Using aluminium foil faced Class 'O' Fire Retardant Properties Closed Cell Elastomeric insulation)
Supply and Application of external thermal insulation of supply /return air ducting using factory laminated aluminium foil faced closed cell elastomeric nitrile rubber insulation with class 'O' fire retardant properties as per the specifications and drawings. aluminium foil face shall provide protection from mechanical impact, and Scratches etc. Both insulation & aluminium foil layer should have built in antimicrobial protection. Expose insulation shall be covered with necessary glass cloth & UV protection paint. Adhesive - AC Duct King Eco Fresh
a. | 25mm thick insulation - For AC Duct in Kitchen | SqM | 135 |  | 0
TOTAL (AIR DISTRIBUTION) Rs. | TOTAL ITEM NO. 4 (INSULATION) |  |  | Rs. | 0
4 | ELECTRICAL WORKS
4.1 | Panels
Supply,Installation,Testing and Commissioning of the following cubical type panels made out of 14 guage CRCA structure, base channel, complete with, moulded case circuit breakers, meters, indicating lamps, current transformer etc. Complete in all respects, insulated bus bars with heat shrinkable PVC sleeve in suitable bus chambers , interconnection, small wiring, name plate, danger plate, earth bus etc. & comprising of compartments with hinged door for each feeder & its accessories, cable alley with hinged doors, bus chamber with bolted door etc. The panel being of dust & vermin proof construction with rubber gasket attractively powder coating etc. The panel shall be free standing type / wall mounted type as per relavant drawing and comprising with the following:
Notes :
1. All MCCBs shall be with operating handle.
2. CTs burden shall be 15VA & accuracy class 1.0
3. CTs shall be cast resin type .
4. All MCCBs shall be with thermal magnetic
release.
5. All indication lights shall be LED type.
6. All meter shall be digital type.
7. The outgoing starter feeders for pumps,AHUS
& ventilation fans shall be provided
with push buttons & indicating lamps for
status indication.
8. Proper isolation switches to be
provided near air handling units and
ventilation fans in weather proof enclosure.
9. Bimetal overload relay for all the
starters shall have built-in single
phasing prevention feature.
10. Electrical interlocking wiring shall be
provided as per system requirement.
11. Power cabling/wiring with necessary
earthing from source to each panel
and each exhaust fan shall be
provided by other agencies.
12. All HVAC equipment shall be compatible with
BMS and necessary provisions to be made
in each panel.
4.1.1 | KVF PANEL -1 (Location : Kitchen ) - 13.8KW
| For 9700Cfm Air Washers & Pump, 12100Cfm SISW Fan & ESP | No | 1 |  | 0
Incoming :
63 Amps ,TP MCCB with electronic release &
earth fault relay, door interlock and front drive
rotor kit-- 1set
(0-500) V digital Voltmeter with built in Selector
switch -- 1set
Digital Ammeter with built in selector
switch- 1set
Current Transformers - 1set
LED type RYB phase indication lights- 1set
Busbar
100 Amps TPN aluminium busbar having
suitable fault level, with PVC heat shrunk
sleeves on SMC/DMC supports.
Outgoings :
a. | For Air Washers - (1x11.0KW)
40 Amps ,TP MCCB -- 1 set
Digital Ammeter with built in selector
switch- 1 set
Current Transformers -- 1 set
LED type ON & OFF indication lights -- 1 set
START-STOP Push Buttons -- 1 set
15.0HP Star Delta starter with built-in single phasing
preventor & overload relay & adjustable timer-- 1 set
Auto-Manual type selector switch
to facilitate auto start of unit
after restoration of power -- 1 set
Control wiring and safety circuit as required
with start-stop push buttons stay put or
lockable type -1 set
b. | For Air Scrubber - (1x15KW)
40 Amps ,TP MCCB -- 1 set
Digital Ammeter with built in selector
switch- 1 set
Current Transformers -- 1 set
LED type ON & OFF indication lights -- 1 set
START-STOP Push Buttons -- 1 set
20HP Star Delta starter with built-in single phasing
preventor & overload relay & adjustable timer-- 1 set
Auto-Manual type selector switch
to facilitate auto start of unit
after restoration of power -- 1 set
Contactors, Potential Free Contacts, Control wiring and
safety circuit as requiredwith start-stop push buttons stay
put or lockable type - 1 set
c. | For Pump of Air washer (1x1.0HP) -single phase
20 Amps ,TP MCB -- 1 set
LED type ON & OFF indication lights -- 1 set
START-STOP Push Buttons -- 1 set
Auto-Manual type selector switch-- 1 set
Contactors, Potential Free Contacts, Control wiring and
safety circuit as requiredwith start-stop push buttons stay
put or lockable type - 1 set
d. | For Pump of Air Scrubber (1x1.0HP) -single phase
20 Amps ,TP MCB -- 1 set
LED type ON & OFF indication lights -- 1 set
START-STOP Push Buttons -- 1 set
Auto-Manual type selector switch-- 1 set
Contactors, Potential Free Contacts, Control wiring and
safety circuit as requiredwith start-stop push buttons stay
put or lockable type - 1 set
4.2 | CABLING
4.2.1 | Supply, laying, affecting connections and
Testing of the following sizes of 1.1 KV
armoured PVC insulated aluminium/ copper
conductor cables. Cables shall be inclusive of
all clamps, saddles, screws, cable identification
tags, cable terminal joints including terminal
lugs, insulating tapes, affecting terminal
connections to the equipment as per the
specifications and as required. Quoted price
shall be inclusive of perforated duly painted
2mm thick MS trays to be installed inside and
GI trays to be installed outside exposed and
8SWG copper earth wire for all equipment.
All power cables shall be FRLS type.
a. | 3 C x 16 Sqmm cable (Copper) | RM | -- |  |  | Rate Only
b. | 3 C x 10 Sqmm cable (Copper) | RM | 10 |  | 0
c. | 3 C x 6 Sqmm cable (Copper) | RM | 20 |  | 0
d. | 3 C x 4 Sqmm cable (Copper) | RM | -- |  |  | Rate Only
e. | 3 C x 2.5 Sqmm cable (Copper) | RM | 5 |  | 0
f. | 3 C x 2.5 Sqmm cable( Copper Control cabling) | RM | 5 |  | 0
g. | 3 C x 1.5 Sqmm cable(Copper Control cabling) | RM | 10 |  | 0
h. | 4 C x 1.5 Sqmm cable( Copper Control cabling) | RM | - |  |  | Rate Only
4.3 | Supply and fixing of 1.1 KV grade rubber
mat 914.4 mm wide 6mm thick to withstand
1.1 KV dielectric strength in front of
| each panel. | RM | 2 |  | 0
4.4 | Supply, Installation & Testing of TPN
isolator in weather proof enclosure near
| Fans. | No | 2 |  | 0
| TOTAL ITEM NO. 4 (ELECTRICAL) |  |  | Rs. | 0
|  |  |  | TOTAL | 0

## Plumbing
TFS DWARKA BASE KITCHEN MATIYALA
SUB HEAD A: SANITARY FIXTURES & FITTINGS
S.NO. | DESCRIPTION | QTY | UNIT | RATE | AMOUNT
NOTE: In case of owner supplied items
follwing items will be supplied by the client:
a) All Sanitary fixtures like water closets, wash basins,
urinals etc. brackets for fixing sanitary fixtures,all CP fittings like taps,
mixers,health faucets etc.cement,sand ,aggregate,Reinforcement bars
(if required),bricks.
1.1 | Providing & fixing glazed vitreous china single trap syphonic pattern having back inlet ,supporting chair ,wall hung water closet with cistern complete with all internal fittings/accessories and CP brass flush bend (European type) water closet with seat and lid, with C.P. brass hinges and rubber buffers, adapter, rubber joints fixed to W.C., C.P. brass screwed washers including cutting and making good the walls and floors wherever required and HDPE wc pan connector including jointing with white cement coomplete in all respects.
Wall hung W.C. pan (White colour)with white plastic seat & lid "Thermoset moulded ( bakelite ) IS 2548 Part I
| For supply, installation, testing & commissioning of sanitary fixtures as per above details | 3 | Each |  | 0
0
1.2 | Providing & fixing glazed vitreous china wash basin with R.S. or C.I. brackets painted white, 32mm C.P. brass waste of standard pattern, 32 mm dia. C.P. brass bottle trap(Jaquar model no ALD 769L) and union 32 mm dia C.P. pipes to wall flange. complete including cutting and making good the walls wherever required. |  |  |  | 0
| Undercounter wash basin (White colour)of size: 585x430 mm. |  |  |  | 0
| For supply, installation, testing & commissioning of sanitary fixtures as per above details | 3 | Each |  | 0
1.3 | Providing & fixing 15mm C.P. brass single hole basin mixer without popup waste system with 450mm long copper pipes and brass nuts. |  |  |  | 0
| For supply, installation, testing & commissioning of sanitary fixtures as per above details | QR | Each
0
1.4 | Providing & fixing vitreous chinaware urinal comprising |  |  |  | 0
| Large flat back wall hung urinal in glazed vitreous China new magnum urinal. |  |  |  | 0
| 15 mm electrically operated solenoid valve with infra red sensor mounted in a box with SS Cover. |  |  |  | 0
| CP brass chromium plated flush piping from valve to urinal terminated with a 15 mm screwed spreader |  |  |  | 0
| 32 mm nominal bore CP cast brass waste |  |  |  | 0
| 32 mm nominal bore CP cast bottle trap with extension pipe rubber adopter for waste connection |  |  |  | 0
| For supply, installation, testing & commissioning of sanitary fixtures as per above details | QR | Each
1.5 | Providing & fixing Sink Mixer with Swinging Casted Spout (Table/Wall Mounted) with 450mm long Copper Pipes & Brass Nuts. |  |  |  | 0
| For supply, installation, testing & commissioning of sanitary fixtures as per above details | 16 | Each |  | 0
0
1.6 | Providing & fixing 15 mm dia C.P. brass angle valves with 450mm long C.P. Copper connecting pipe union nut C.P. cast brass wall flange. |  |  |  | 0
| For supply, installation, testing & commissioning of sanitary fixtures as per above details | 40 | Each |  | 0
0
1.7 | Providing & fixing toilet paper holder including cutting and making good the walls. |  |  |  | 0
| For supply, installation, testing & commissioning of sanitary fixtures as per above details | 3 | Each |  | 0
1.8 | Providing & fixing C.P. brass twin coat hooks fixed on toilet door with C.P. brass screws. |  |  |  | 0
| For supply, installation, testing & commissioning of sanitary fixtures as per above details | 3 | Each |  | 0
0
1.9 | Providing & fixing 15mm C.P. brass sink spout(single) complete with all accessories.
| For supply, installation, testing & commissioning of sanitary fixtures as per above details | QR | Each
1.1 | Providing & fixing beveled edge mirror 5.5mm thick of superior quality plate glass complete with 6mm thick marine ply sheet ground fixed to wooden cleats with CP brass screws and washerswith 40 mm wide teak wood frame as per design including polishing. |  |  |  | 0
| For supply, installation, testing & commissioning of sanitary fixtures as per above details | 3 | Sqm |  | 0
0
1.11 | Providing & fixing Health Faucet with 8mm dia, 1M long PVC tube and wall hook. |  |  |  | 0
| For supply, installation, testing & commissioning of sanitary fixtures as per above details | 3 | Each |  | 0
1.12 | Providing & fixing, testing and commissioning of storage type electric water heater with automatic thermostatic control electric element, pressure release valve, brackets fixed to expansion fasteners with M.S. nuts and bolts all complete including cutting and making good the walls wherever required. |  |  |  | 0
1.12.1 | 50 litres capacity |  |  |  | 0
| For supply, installation, testing & commissioning of sanitary fixtures as per above details | 6 | Each |  | 0
1.12.2 | 100 litres capacity |  |  |  | 0
| For supply, installation, testing & commissioning of sanitary fixtures as per above details | 1 | Each |  | 0
0
1.13 | Providing & fixing 15 mm dia C.P. brass bib cock with Hose union of approved quality. |  |  |  | 0
| For installation, testing & commissioning of sanitary fixtures as per above details. | 5 | Each |  | 0
0
1.14 | Providing & fixing 15 mm dia C.P. brass bib cock with C.P. wall flange of approved quality. |  |  |  | 0
| For supply, installation, testing & commissioning of sanitary fixtures as per above details | 5 | Each |  | 0
0
1.15 | Providing & fixing 15mm C.P. brass push tap for basin with 450mm long copper pipes and brass nuts.
| For supply, installation, testing & commissioning of sanitary fixtures as per above details | 3 | Each |  | 0
| NOTE:- |  |  |  | 0
i. | Detail of Sanitary fixture are for the information of the Contractor,however model/makes of all sanitary fixtures shall be selected by Architect/Interior designer/Project manager and the same shall be binding for execution. |  |  |  | 0
0
ii. | No additional fixing cost shall be paid for change in type of sanitary fixtures. |  |  |  | 0
0
iii. | Contractor to receive all the above mentioned items & store at place as directed at site in case supply is by Client . |  |  |  | 0
SUB HEAD B: WATER SUPPLY
1 | Providing and fixing Chlorinated polyvinyl Chloride (CPVC) pipes-SDR-11,havings thermal stability for hot & cold water supply including all CPVC plain & brass threaded fittings including fixing the pipe with clamps at 1.00 m spacing.This includes jointing of pipes & fittings with CPVC solvent cement and the cost of cutting chases and making good the same including testing of joints complete as per direction of Engineer in charge,fixing at wall/ceiling level supported by clamps, hangers, structural steel supports, etc.Cost shall include making connections with Sanitary fixtures & CP fittings.
| a) 15 mm outer dia | QR | RM
| b) 20 mm outer dia | 450 | RM |  | 0
| c) 25 mm outer dia | 100 | RM |  | 0
| d) 32 mm outer dia | 80 | RM |  | 0
| e) 40 mm outer dia | 180 | RM |  | 0
| f) 50 mm outer dia | 25 | RM |  | 0
| g) 65mm inner dia-sch 40 with sch 80 fittings | 20 | RM |  | 0
2 | Providing & fixing gun metal lever operated ball valve. Tested to a pressure of 15 Kg / Sqcm. Including flanges/union, nuts, bolts, washer etc. Complete as required.
| a) 15 mm dia | 4 | NOS |  | 0
| b) 20 mm dia | 8 | NOS |  | 0
| c) 25 mm dia | 4 | NOS |  | 0
| d) 32 mm dia | 4 | NOS |  | 0
| e) 40 mm dia | 8 | NOS |  | 0
| f) 50 mm dia | 8 | NOS |  | 0
3 | Providing & fixing gunmetal non return valve including all accessories suitable for working pressure of 15 Kg/sqcm of the following sizes:
| a) 20mm dia | QR | NOS
| b) 32mm dia | QR | NOS
| c) 40mm dia | 2 | NOS |  | 0
| d) 50 mm dia | QR | NOS
4 | Supplying, installing, testing and commissioning of triple layer HDPE water storage tank including holes for inlet, outlet, overflow level indicator drain and vent points, manhole cover suitable supporting structure complete.Bottom of tank shall be atleast 450mm above finish floor level of terrace.
| a) Capacity 5000 Lts. | 6 | SET |  | 0
5 | Providing and fixing electronic type level indicator for water tank mounted in panel with level display, alarm when water level is low or high, full range from one level to four level display and manual reset for alarm etc. with electrical wiring conduit supports from wall & ceiling probs and all other accessories complete as required. | 3 | NOS. |  | 0
6 | Providing & fixing 6mm thick nitryl rubber insulation
| on hot water pipes-15 to 25 mm dia pipes burried | 200 | RM |  | 0
inside walls.
7 | Providing and fixing 24 SWG Al. sheet metal cladding over pipe insulation, 50mm overlapped and hold the same with self-tapping screws and all joints to be sealed with sealent (tarfelt strip) complete as required.
| a) 15 mm dia pipe --- SP insulation 25 mm thick | 20 | RM |  | 0
| b) 20 mm dia pipe --- SP insulation 25 mm thick | 100 | RM |  | 0
| c) 25 mm dia pipe --- SP insulation 25 mm thick | 10 | RM |  | 0
| d) 32 mm dia pipe --- SP insulation 25 mm thick | 10 | RM |  | 0
| e) 40 mm dia pipe --- SP insulation 25 mm thick | 40 | RM |  | 0
| f) 50 mm dia pipe --- SP insulation 25 mm thick | 10 | RM |  | 0
8 | Providing & fixing of CI butterfly valve suitable for pressure 15 Kg/Sqcm. with flanges, nut bolts & gaskets complete required.
| a) 65 mm dia | 2 | NOS |  | 0
9 | Providing & fixing electricaly operated Motorized Butterfly Valves with by pass piping & all fittings , by pass valves (3nos) for filling of overhead tanks complete with High & Low level control switches to control the valves. The level controllers shall be installed in overhead tanks.The system should be complete in all respect with accessories ,220 volt V AC/24 volt DC , IP67 electrical water level control unit , copper control wiring in wheather proof casing etc. from butterfly valves to control unit .
| a) 32 mm dia | 1 | NO |  | 0
| b) 40 mm dia | 1 | NO |  | 0
| c) 50 mm dia | QR | NOS
10 | Providing & fixing digital water flow meter on pipes of following diameter.
| a) 25 mm dia | 1 | NO |  | 0
| b) 32 mm dia | 1 | NO |  | 0
| c) 40 mm dia | 1 | NO |  | 0
11 | Providing and fixing in position G.I. vent with brass mosquito proof coupling and air filter including return bend, complete as required. The entire fitting shall be hot dipped galvanised.
0
| a) 50 mm dia | 6 | NOS |  | 0
SUB HEAD C:INTERNAL DRAINAGE (SOIL, WASTE & VENT PIPES)
1 | Providing, fixing, jointing and testing in position of ISI marked UV stabilized UPVC pipes for soil, waste and vent, Type-B as per IS : 13592 suitable for rubber ring joints, including all neccessary specials and fittings (confirming to IS:14735) i.e. bends, tees, junctions (with or without doors), reducers, WC connectors, couplers, cowls, clamps, rubber rings, clean outs ,access pieces at ends of main pipes (for roding) etc. fixing at wall/ ceiling/ floor level supported by clamp, hangers & structural steel supports etc. in concealed / inside duct / under floor & basement ceiling / external work etc. including chase cutting as required, excavation and back filling in all kind of soils, suspended from floor under false ceiling or embedding the pipes laid under floors / building in 75 mm. alround 1:2:4 cement concrete (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size) including cost of shuttering for proper completion of the work, breaking and making good the walls and floors etc. after pipes have been duly laid and tested. The rubber ring shall confirm to IS:5382.
The Pipes will be supported with threaded G I rods & clamps on 50x50x5 mm slotted angle. The cost will include all support arrangements. The work includes commissioning of all pipes lines as per drawings and specifications and as directed by engg-in-charge at site.
| a) 75 mm outer dia | 5 | RM |  | 0
| b) 110 mm outer dia | 130 | RM |  | 0
| c) 160 mm outer dia | 70 | RM |  | 0
2 | Providing and laying 1:2:4 cement conc. 100 mm thick all round the pipe including 100mm thick bed concrete for the following M.S./C.I./C.I. class L.A./UPVC pipes and specials below floor including necessary shuttering etc. complete as required.
| a) 75 mm dia pipe | 5 | RM |  | 0
| b) 100 mm dia pipe | 100 | RM |  | 0
| c) 160 mm outer dia | 70 | RM |  | 0
3 | Providing, fixing, jointing and testing in position ISI marked (IS:4985) UPVC pipes of min 6 Kg/ Sqcm rating with fitting for waste pipe from fixtures to floor trap including reduces, enlarger, socket, couplers, bends, tees etc including fixing at wall/ ceiling level supported by clamp & hangers etc. cutting holes in wall/ floors/ slabs and making good the same with cement concrete 1:2:4 complete as required.
| a) 40 mm outer dia | 20 | RM |  | 0
| b) 50 mm outer dia | 90 | RM |  | 0
| c) 63 mm outer dia | 20 | RM |  | 0
4 | Providing & fixing UPVC Floor trap of self cleansing design with CP Jali complete in all respects. (Make : Supreme / Finolex / Prince).Multi trap connection to be provided with each floor trap.
| a) 100 mm inlet and 100 mm outlet. | 36 | NOS |  | 0
| b) 100 mm inlet and 75 mm outlet. | 2 | NO |  | 0
5 | Providing & fixing 100m x 50mm PVC waste including cutting chases, the floor / slab complete as required. | 46 | NOS |  | 0
7 | Providing and fixing PVC clean out plug with suitable inlet key for opening male threaded joint with pipe & socket complete as required.
| a) 100 mm dia | 2 | NOS |  | 0
SUBHEAD D :EXTERNAL SEWAGE
1 | Providing fixing, jointing and testing in position the following DWC SN8 pipes conforming to IS: 16098-Part II for drainage cut to required lengths including all necessary fittings and specials such as bends, junctions, offsets, making proper connections. Pipe to be laid below ground level in trenches upto required depth including excavation in all kind of soil, dewatering, refilling, watering, ramming & removing the surplus excavated material and making good the same complete as required. For external sewer.
| a) 110 mm dia pipe | QR | RM
| b) 160 mm dia pipe | 6 | RM |  | 0
| c) 200 mm dia pipe | 30 | RM |  | 0
| d) 250 mm dia pipe | QR | RM
2 | Providing and laying 150 mm thick cement concrete 1:4:8 (1 cement:4 fine sand:8 graded stone aggregate 40mm nominal size) alround pipes including 150 mm thick bed concrete as per standard design.For external sewer.
| a) 100 mm dia pipe | QR | RM
| b) 150 mm dia pipe | 6 | RM |  | 0
| c) 200 mm dia pipe | 30 | RM |  | 0
3 | Providing and fixing stoneware gully trap grade 'A' of the following sizes with C.I. grating embedded in brick masonary chamber of required size and trap to be set in cement concrete 1:2:4, both side 12mm thick plastering with floating cast of neatcement,rough plaster on outer surface. Making necessary connections & providing water tight C.I. cover with frame. Including necessary excavation Including necessary excavation, dewatering, refilling, watering, ramming and removing the surplus excavated material and making good the same complete as required.
| a) 180X150 mm outlet -chamber size 450x450mm | 1 | NO |  | 0
| b) 150X100 mm outlet -chamber size 300x300mm | QR | NO
0
4 | Constructing brick masonry inspection chamber of the following sizes in brick work of class 75 in cement mortar 1:5 work in cement mortar 1:5 (1 cement:5 fine sand), R.C.C. top slab with 1:2:4 mix (1 cement : 2 coarse sand : 4 graded stone aggregate 20mm. nominal size) foundation concrete 1:4:8 mix(1 cement:4 coarse sand:8 size).Inside plastering 12 mm thick with cement motor 1:3 ( 1 cement : 3 coarse sand) and rough plastering on outside with a floating coat of neat foot rests at 300 mm spacing, banching and making channels with 1:2:4 cement concrete neatly finished, including excavation, in all kind of soil (hard rock), dewatering, refilling, watering, ramming and removing the surplus excavated cement providing MS material making good the same complete as required. |  |  |  | 0
0
| a) Inside size 60x45 cm ( upto 60 cm maximum depth). | QR | NOS
| b) Inside size 90x80 cm ( upto 90 cm maximum depth). | 3 | NOS |  | 0
0
| c) Extra over 'b'above for depth exceeding 60 cm & upto 90 cm. | 1 | RM |  | 0
0
5 | Providing orange colour safety foot rest of minimum 6 mm thick plastic encapsulated as per IS : 10910 on 12 mm dia steel bar conforming to IS : 1786 having minimum cross section as 23 mm X 25 mm and over all minimum length 263 mm and width as 165 mm with minimum 112 mm space between protruded legs having 2 mm tread on top surface by ribbing or chequering besides necessary and adequate anchoring projections on tail length on 138 mm as per standard drawing and suitable to with stand the bend test and chemical resistance test as per specifications and having manufacture's permanent identification mark to be visible even after fixing, including fixing in manholes with 30 X 20 X 15 cm cement concrete block 1:3:6 (1 cement : 3 coarse sand : 6 graded stone aggregate 20 mm nominal size) complete as per design. | 10 | NOS |  | 0
0
6 | Providing & fixing in positon precast R.C.C. manhole cover and frame of required shape and approved quality. |  |  |  | 0
| a) Circular shape 500mm internal diameter Medium Duty . | QR | NOS
0
7 | Providing & fixing cast iron manhole cover with frame. |  |  |  | 0
0
| a) Medium duty double seal of size 500mm internal diameter.Total weight of cover & frame to be not less than 116 Kg. | 3 | NOS |  | 0
0
| b) Heavy duty double seal of size 560mm internal diameter. Total weight of cover & frame to be not less than 208 Kg. | QR | NOS
0
8 | Constructing Oil & Grease Chamber size 2500x 1000mm internal size of 1000mm depth in First class brick work with cement mortar (1:5) Inside 12mm thick with cement mortar 1:3 with floating coat of neat cement and rough plaster on outside, RCC top slab with 500mm dia medium duty manhole cover with frame (weight of cover 58 kg. & weight of frame 58 kg.), 150mm thick foundation concrete (1 :4 : 8), necessary excavation, dewatering, refilling, watering, ramming and removing the surplus excavated material and making good the same complete as required. | 2 | NOS |  | 0
9 | Providing & fixing SS 304 chamber with SS 304 manhole cover with frame,inlet & outlet connections as per drawing including all associated civil works. | 13 | NOS |  | 0
SUB-HEAD E : PUMPS & EQUIPMENTS
1 | Supplying, installing, testing & commissioning Horizontal centrifugal pump set with C.I. casing, Bronze Impeller, SS shaft suitable for operation on 400/440 volts, 3 phase 2900 RPM electric motor,100 mm dia pressure guage, G.M. isolation cock complete as required. Cyclic operations shall be provided for each set of two pumps.Cost shall included electrical control panel with wiring/cabelling/control cabelling.
a) | Raw Water Pumps
Location - Plant room at terrace level
Number of Pumps = 2 Nos
Capacity 2 LPS each
Head 25 Mts
| RPM 2900 | 1 | SET |  | 0
NOTES FOR ALL PUMPS :-
a) Level Controller with sufficient nos. of low / high level alarms, contacts with electrodes and control wiring for the automatic operation of all water supply pumps to achieve the functional requirement shall be provided. Control wiring between these pumps and water tanks shall be provided. Raw water pumps must start at low level of water in domestic water tank & stop at high water level in that tank. Dry running protection shall be provided for the pumps.
2 | Supplying, installing, testing & commissioning vertical inline pumps with S.S. casing, S.S. impeller. mechanical seal, S.S. Shaft directly coupled to motor suitable for operation on 400/440 volts, 3 phase 2900 RPM. TEFC electronic motor mounted on a common channel baseplate 150mm dia pressure gauge, G.M. gauge, G.M. isolation cock.Location Plant Room at terrace level.
i) | Control panel with pressure switch, electrical wiring, cabling from panel to pumps, level controller complete with all accessories.
ii) | CPVC-SDR-11 suction and discharge header with valves & vibration isolator at suction side of header & discharge side of header.
iii) | Set of accessories such as Pressure Switches, Connecting Power & Control Cabling etc.
Hydropneumatic system for Domestic water supply system with 1 No. Precharged vessel of minimum capacity of 100 Lts(minimum) with interchangeable butyl rubber membrane connected to outlet header with necessary flanges, gaskets, isolation valves, nuts, bolts etc. complete.-For feeding Domestic water. Variable Speed.
Capacity 2 LPS (each pump)
Head 20 Mts.
RPM 2900
No. of pumps 2
| Hydropneumatic system as described above | QR | SET
3 | Providing, fixing, testing & commissioning of vertical FRP pressure filter complete with initial charge of filter media frontal piping with valves including testing kit, complete as required.(Location plant room at terrace level).
a) Filter for Domestic Water.
Tested pressure 6Kg/Sq.cm
| Capacity 2 LPS. | 1 | SET |  | 0
4 | Supply, installation, testing & commissioning of chlorine dosing system consisting of one FRP/ HDPE tank of 100 liters capacity with a positive displacement diaphragm Dosing pump with a variable flow rate of 0-12 LPH. The motor shall be suitable for operation at 240 V /one phase/ 50 Hertz supply. The pump shall be supplied complete with necessary poly propylene piping, valves, strainers & injection fittings for system to dose solution to the feed line. The pump shall be Asia LMI make. (Location plant room at terrace level). | 1 | SET |  | 0
5 | Providing, fixing, testing & commissioning of FRP body water softener with frontal piping valves complete with Resin, Hydraulic Brine Injector, HDPE Brine tank of capacity one generation,Remi make mixing motor and all other accessories complete as required.
a) Softner for domestic water. Location -Plant Room at terrace level.
Input water Hardness(appx) =700 Mg/L ( Max )-Exact hardness will be after receiving water analysys report.
Output water Hardness 70 ppm
Regeneration Period After 1.0 lac lts
Operating Pressure 3.5 Kg. per sq.cm
Test Pressure 6 Kg. Sq.cm.
| Capacity 2 LPS | 1 | SET |  | 0
6 | Providing & fixing packaged Reverse Osmosis System skid mounted complete with pre and post water treatment plant, RO plant feed pumps(2nos.)CIP system, pipes ( SS -High pressure, PVC- low Pressure ) , dosing units,TDS meter, valves, control wiring, electrical panel, instrumentation input/output water quality monitoring meters/indicators, fully automated. -Location-Plant room at terrace level.
TDS of Input(raw) water as per water test report= 600 ppm.
Permeate flow rate 1000 LPH (TDS at output after blending will be below 70ppm).
Water Test Report-to be obtained from site before finalising technical details of RO plant.
| RO Plant as mentioned above | 1 | NO |  | 0
|  |  |  | Total | 0

## MAKES
PLUMBING
S No. | Item | Make
1 | Vitreous China Sanitaryware | As Approved
2 | C.P. Brass fittings | Jaquar/Hindware/ as approved
3 | Cast iron pipes & fittings, Manhole covers and frames. | NECO/RIF
4 | G.I. pipes. | Tata/Jindal Hissar/Prakash Surya
5 | G.I. pipes fittings. | K.S. / Unik / `R’ Brand
6 | R.C.C pipe | K.K. / App. Equivalent ISI marked
7 | Stoneware pipes, Gully traps | Perfect potteries, Jabalpur / Approved equivalent ISI marked
8 | Valves | Zoloto / Leader/ C & R / Advance
9 | Paints | Asian Paints / Shalimar Paints /Berger
10 | Pressure Gauge | H Guru/Fiebig
11 | Pumps | Grundfoss/ITT/Kirloskar/KSB
12 | Level Controller & Indicator (Water) | Advance Auto/Technika / Minilec
13 | PVC Pipes | Supreme / Prince/Astral
14 | Urinal Sensor | UTEC System/Jaquar/Hindware
15 | Geyser | Venus/Racold/AO Smith
16 | Sink | Neelkanth/Kobra/Hindware
17 | Water purifier | Eureka Forbes/Kent
18 | HDPE Water tanks | Sintex/Frontier
19 | CPVC Pipes | Aashirwad/Finolex/Astral
20 | Gratings,Cleanouts,Funnels | GMGR/Neer/Jayna
ELECTRICAL
S No. | Item | Make
1 | Conduits | Precision/ AKG/ BEC
2 | FRLS Wires | Finolex / Havells/ KEI/ Polycab
3 | Cables | Polycab/ Havells/ Finolex
4 | Switches | Legrand /Roma / Clipsal/ Opale/ Crabtree/ Northwest
5 | Distribution Boards | Siemens/ MDS/ legrand / L&T
6 | MCB’s /ELCB’s | Siemens/ MDS/ legrand / L&T
7 | Telephone/Speaker Wires | Finolex/ Polycab/ Falcon
8 | T.V.Wires | Comscop/ Finolex
11 | Switch Fuse Units/ Starters | L&T/ Siemens
12 | Fire Alarm System | Apollo/ System Sensor/ Agni/ Honeywell/ Ravel
13 | Data Cable / IO | Amp (TE)/ D Link
14 | Light Fittings | Havells/Wipro/Philips
Notes:-
[1] The Contractor should quote the tender rates considering First make of materials given in above list.
[2] Wherever contractor proposes to use `equivalent' makes (i.e. other than specified) he shall obtain Client's prior approval. Client may consult Consultants before giving approval to the same. Any additional cost and time lost due to this will be on Contractor's account and no claims will be entertained.
[3] The contractor should take approval for make & manufacturer from the TFS before using any material, which does not appear in the list of approved manufacturers.
FIRE FIGHTING
S No. | Item | Make
1 | G.I./M.S pipes. | Tata/Jindal Hissar/Prakash Surya
2 | MS Forged fittings. | VS/KS
3 | Valves | Zoloto / Leader/ C & R / Advance
4 | `Y' strainer | Emerald Enterprises / Zoloto/Kartar
5 | Level Controller & Indicator (Water) | Advance Auto/Technika / Minilec
6 | Paints | Asian Paints / Shalimar Paints /Berger
7 | Pressure Gauge | H Guru/Fiebig
8 | Flexible Rubber Expansion Joint | Kanwal Easyflex/Resistoflex
9 | Pumps | Kirloskar/Mather & Platt /KSB
10 | Fire Fighting Equipments | Minimax/Safeguard/Getech
11 | Sprinklers | Tyco/Grinnel/Best/HD
12 | Welding Rods | Advani/Victor
13 | GI Hangers | Chilly/GMGR