## HVAC BOQ
IDLI.COM & IRISH HOUSE AT LUCKNOW AIRPORT
SUMMARY TO SCHEDULE OF PRICES - HVAC WORKS R0
A | Part A: HVAC Equipments |  |  |  | #REF!
B | Part B: Low Side Works |  |  |  | #REF!
C | Part C: Electrical Works |  |  |  | #REF!
GRAND TOTAL |  |  |  |  | #REF!
IDLI.COM & IRISH HOUSE AT LUCKNOW AIRPORT
SCHEDULE OF PRICES - HVAC WORKS R0
The prices are to be quoted in the below mentioned form and shall include the supply, installation, Testing and Commissioning at site of all the equipments, ancillary materials except where specified otherwise and all such items whatsoever which may be required to fulfill the intent and purpose as laid down in the drawings and specifications shall include all taxes and duties on a basis works contract.
S.No. | Description | Unit | Qty. | Rate(Rs.) | Amount(Rs.)
Part A | HVAC Equipments
1 | Air Handling Units (Indoor Type)
Supply , Installation , testing & commissioning Of Double skin Ceiling Suspended Type air handling units of extruded aluminium section with 0.6 mm preplasticized/precoated GI sheet outside and 0.6 mm plain Galvanized sheet inside, minimum of 25 mm thick PUF insulation of 38KG/m3 , DIDW Blower with TEFC motors, copper cooling coils as mentioned below , with aluminium fins, MERV-8 and MERV 13 Filters. The drain pan shall be constructed out of 18G stainless steel duly insulated. All the AHU's installed under this tender shall have IE3 motor. All the cooling coils shall be AHRI / Eurovent Certified . The AHU Coil shall be selected at 9 deg C Chilled water Inlet Temp Temperature. Approval of AHU Technical Data by consultant prior to fabrication is required. kinldy note it include fixing with proper MS support/vibration pads, electrical connections/installation & commisisoning in all aspects with CFM report to be handover with proper sign off from airport engg team.
Design Parameters- 25 deg C -R.A.Temp, 55% RH, 9 deg C- CHW IN
Water Flow Rate- 2.0 GPM/ TR
1.1 | Ceiling Suspended Type
1.1.1 | 3910 CMH(2500 CFM) at 15 mm External Static Pressure, 6 RD Cooling Coil, Approx 6.0 TR, 1 x 1.1 KW Motor | Nos | 1 |  | 0
1.2 | Digital Cooling Thermostat for Air Handling Units with all accessories including gauges for checking in and out temperature etc. | Nos. | 1 |  | 0
2 | Kitchen Scrubber (Dry Type)
2.1 | Supply , Installation, Testing and Commissioning of Dry Type Scrubber each comprising of extract air intake section, electrostatic precipitation technology, dry type air cleaner to remove oil, smoke and fumes from exhaust air, as per the Specifications. Electrostatic section shall be made of 16 gauge galvanised sheet, high bake epoxy powder coated, washable type aluminium mesh filters, stainless steel spiked ionizers to create high voltage DC field, aluminum collector plates which should be alternatively charged positive and negative with large collecting area with 14" deep cell, to work as magnet for charged smoke and oil particles. Average efficiency of 90-95% in single pass as per ASHRAE test method. Electrostatic Precipitator should be able to charge particles from 0.01 micron to 10 microns through solid state power supply. Collector cell should be of permanent type and incorporate slide out facility for easy removal for cleaning. Power supplies shall be 100% solid state UL Listed, Module of capacity above 3000 CFM shall be equipped with Pulse width modulating (PWM). kinldy note it include fixing with proper MS support/vibration pads, electrical connections/installation & commisisoning in all aspects with CFM report to be handover with proper sign off from airport engg team.
The system should be fitted with interlock switch for safety . The system should allow connection to a fan section to achieve 500 FPM velocity across the air
Operating Voltage : 220V, 50 Hz
Ionizing Voltage : 12.5 to 13 KVDC
Collector Cell Voltage : 6 to 6.5 KVDC
Power Consumption : Not more than 50W per cell.
2.1.1 | 2300 CFM | Nos | 2 |  | 0