## SUMMARY
NANDO'S @ T3 DELHI
HVAC BOQ SUMMARY
Sr.No | Description | Total Amount
1 | VRF SYSTEMS | 0
2 | INDIGENOUS WORK: | 0
3 | VENTILATION SYSTEM | 0
4 | SHEET METAL WORKS: | 0
5 | THERMAL & ACOUSTIC INSULATION: | 0
6 | ELECTRICAL WORKS: | 0
SUB - TOTAL WITHOUT TAX
CGST @ 9%
SGST @ 9%
Other taxes if applicable
TOTAL WITH TAX

## HVAC
NANDO'S @ T3 DELHI
HVAC BOQ
Sr. No. | Description Items | Unit | Qty | Supply Rate | Installation Rate | Total Amount
Sr.No. | Item Description
Note: | Prices shall be based on supply, installation, testing & commissioning (SITC) at site including all taxes, duties, transportation & insurance etc.
1 | VRF SYSTEMS
1.1 | VRF OUTDOOR UNITS
Supply of air cooled variable refrigerant flow modular type condensing units, each comprising of multiple scroll compressors all inverter driven, full charge of refrigerant gas (R-410a), lubricating oil and all accessories as per the specifications. The condensing units shall be suitable to work on heating/ cooling mode. The minimum Energy Efficiency Ratio shall be as per ASHRAE STANDARDS 90.1 -2001 table 6.2.1B . The COP of the system shall be greater than 4 under ARI conditions for 100% load . The condensing units shall be suitable for operation on 415 ± 10% volts, 50Hz, 3 phase AC power supply. VRF unit shall be supplied with operating panel for operation & control. ODU to have standard factory coated treatment for heat & rust corrosion for Condenser coil, panels, motor, electricals & heat exchanger, Power Cabling etc. The condensing units shall be of following capacities:
Refrigeration Capacities indicated below are actual capacity. Selection to be done considering referigerant piping length and derating at @ 40°C. Vendor has to submit/highlight if capacity of the unit exceed diversity factor after derating for 40°C ambient conditions. Any alteration in capacity after bidding will not be entertain. Vendor has to provide unit to meet the refrigeration requirement.
Make : Daikin, Toshiba, Mitsubishi
a | Refrigeration Capacity - 14 HP | Nos. | 1
1.2 | VRF INDOOR UNITS
Supply,Installation,Testing and Commissioning of variable refrigerant flow modular type indoor units Corded / Cordless remote suitable for R410a refrigerant comprising of all accessories as per the specifications. The indoor units shall be suitable to work on cooling as well as heating mode. The minimum Energy Efficiency Ratio shall be as per ASHRAE STANDARDS 90.1 -2001 table 6.2.1B. The indoor units shall be suitable for operation on 220 ±6% volts, 50Hz, 1 phase AC power supply. Ductable indoor units shall be suitable to handle extent of ductwork as shown in the design drawings and dehumidified air quantity as mentioned below. The indoor unit shall be complete with pre filter & remote as per requirement. Unit shall be quoted with T-Tube flange connection kit for for higher fresh air intake. Except Hi-wall unit, all other units shall have port for fresh air intake and inbuilt drain pump. The indoor units shall be of following capacities:.
a | HIGH STATIC DUCTABLE TYPE INDOOR UNIT with CORDED REMOTE CONTROLLER
Indoor Temperature: NMT 22°C
| 2542 CFM / 6.4 TR | Nos. | 2
b | CEILING MOUNTED TYPE COMPACT CASSETTE UNIT with CORDLESS REMOTE CONTROLLER
Indoor Temperature: NMT 22°C
| 318 CFM / 0.6 TR | Nos. | 1
1.3 | CENTRALISED REMOTE CONTROLLER
Supply of the Graphic central remote Controller (Touch Screen Type) . It must act as an advanced air conditioning management system to facilitate complete control of VRF air conditioning equipment. It should be user friendly through its touch screen, icon display and color LCD display. Integratable upto 64 remote controller groups (including AHUs & TFAs) and BMS compatible with ethernet / Wi-Fi communication protocol for remote monitoring. In addition to basic controls such as settings for on/stop, the operation mode & temperature, the air quantity and auto louver can be set. If a problem occurs, an alarm code immediately shows the details of the problem. An external input terminal is provided as standard. External signals enable the following function: central operation / stop, demand control, emergency stop, central operation output, & central alarm output. Controller shall however be suitable for future connectivity of indoor & outdoor units also.
a | Central Remote Controller | Nos. | 1
GENERAL NOTES:
a | The cost shall be included liftting & shifting of each equipment / material with all necesaary arrnagement. Also, it shall be included the cost of scaffloding required for Installation of such material / equipment.
SUB-TOTAL
2 | INDIGENOUS WORK:
2.1 | INSTALLATION OF VRF OUT-DOOR UNITS |  |  |  |  | 0
| Installation, Charging, Testing and commissioning of VRF system with Environment friendly refrigerant gas for the below mentioned system. This shall include lifting, shifting and positioning of outdoor units, nitrogen leak testing, oil charging, vaccumisation etc., |  |  |  |  | 0
a | Refrigeration Capacity - 14 HP | Nos. | 1
2.2 | INSTALLATION OF VRF INDOOR UNITS
| Installation, Charging, Testing and commissioning of units complete with centrifugal blower, cooling coil with suitable rows, electronic expansion valves, high efficiency pre filter sections, drain pump etc as per specifications. |  |  |  |  | 0
a | HIGH STATIC DUCTABLE TYPE INDOOR UNIT with CORDED REMOTE CONTROLLER | 0 |  |  |  | 0
0 | Indoor Temperature: NMT 22°C | 0
0 | 2542 CFM / 6.4 TR | Nos. | 2
0 | 0 | 0 | 0
b | CEILING MOUNTED TYPE COMPACT CASSETTE UNIT with CORDLESS REMOTE CONTROLLER | 0 | 0
0 | Indoor Temperature: NMT 22°C | 0 | 0
0 | 318 CFM / 0.6 TR | Nos. | 1
2.3 | INSTALLATION OF CENTRALISED REMOTE CONTROLLER
| Installation, Charging, Testing and commissioning of of the Graphic central remote Controller (Touch Screen Type) . It must act as an advanced air conditioning management system to facilitate complete control of VRF air conditioning equipment. It should be user friendly through its touch screen, icon display and color LCD display. Integratable upto 64 remote controller groups (including AHUs & TFAs) and BMS compatible with ethernet / Wi-Fi communication protocol for remote monitoring. In addition to basic controls such as settings for on/stop, the operation mode & temperature, the air quantity and auto louver can be set. If a problem occurs, an alarm code immediately shows the details of the problem. An external input terminal is provided as standard. External signals enable the following function: central operation / stop, demand control, emergency stop, central operation output, & central alarm output. Controller shall however be suitable for future connectivity of indoor & outdoor units also. |  |  |  |  | 0
a | Central Remote Controller | Nos. | 1
2.4 | VRF REFRIGERANT PIPING & FITTING WITH INSULATION
| Supply, Installation, Testing and Commissioning of the refrigerant piping with nitrile rubber insulation in sleeve form.It should be selected for maximum working pressure of 624 psi for R – 410a refrigerant circuit and for maximum working pressure of 500psi in case of R407C refrigerant. The Ref. Piping shall be pressure tested at 1.5 times the working pressure. Copper pipes shall be made of phosphorus deoxidized seamless copper. Minimum thickness to be used for refrigerant piping shall be as follows: The insulation( Nitrile rubber, class-O, self extinguishing, CFC free, thermal conductivity of not more than .035w/Wm˚K shall be 19 mm thick for suction piping & liquid line. All Exposed Piping on the floor shall be enclosed in openable GI trays & insulation should be with UV protection with mil cloth.The Ref. Piping shall be properly supported at every 1.5 m distance with stands and support linked with rubber as per specifications. | Rmt | 75
| Make: Maxflow/ Mandev/ Heling |  |  |  |  | 0
| Note: Referiferant piping shall include liquid + gas pipe with all necessory fittings. Also, the size of the same shall be as per manufactured standard. |  |  |  |  | 0
2.5 | GAS CHARGING
| Additional gas charging - Over and above standard Gas charging quantity | Kg | 15
2.6 | REFNET JOINTS
| SITC of Special Refrigerant T & Y-joints for VRF units | Nos | 2
2.7 | POWER CABLING |  |  |  |  | 0
Supply, handling, laying effecting proper connections testing and commissioning of following sizes of 1.1 KV grade XLPE insulated FRLS Aluminium /Copper conductor cables laid over MS supports cable racks or fixing on walls including clamping the cable to supports in an approved manner as required complete with Copper earthing as specified for continuous earthing along with cable. (Earthing will be measured separately and need not be quoted under this item). All complete as required and as per final instruction as given by Owners/ Consultants. (MCCB,s provided 5m from Outdoor unit).
Make: Polycab, KEI & Finolex
b | Suitable copper Armoured cable - from MCB / Isolator to VRF ODU. | Rmt | 5
d | 8 SWG Copper Wire | Rmt | 10
2.8 | COMMUNICATION CABLE
SITC of the control cabling from Indoor to outdoor unit & Outdoor unit to CRC / BACnet for all the units with the necessary fittings. The cabling shall be of weather proof type as most of the cabling will have open exposure to atmosphere. The cabling shall be bundled properly and shall be neatly aligned with the Refrigerant piping. The cabling shall be well supported with G.I cable tray throughout the piping length.
Make: Polycab, KEI & Finolex
a | 1.5 sqmm 2 core | Rmt | 135
2.9 | PERFORATED GI CABLE TRAYS
Supplying & Fixing of following sizes of Perforated GI cable tray duly painted of height 50mm along with necessary bends, reducers etc. anchored along the wall / suspended from the ceiling with necessary MS supports. External & Internal refrigerant piping shall be provided and laid on GI covered cable trays with cover.
a | 150mm wide | Rmt | 25
b | 300mm wide | Rmt | 50
2.1 | FRAMEWORK FOR VRF ODU
| Supply, Fabrication and Installation of MS frame using channels / angle iron sections as required for mounting of air cooled remote condenser in service areas or terrace level. The frame work shall be applied with red oxide primer and thereafter, two coats of enamel paint of approved colour. The general arrangement drawing for frame work shall be got approved from the Architects/ Structural Engineers prior to commencement of fabrication. | Nos. | 1
2.11 | INSULATED CONDENSATE DRAIN PIPE
SITC of UPVC pipes of following sizes for drain with necessary supports and fittings such as elbows, tees & reducers etc. The insulation line to be insulated with nitrile rubber insulation of thickness 9mm and wrapped by weather proof protection tape. The Pipe wherever concealed should also have a parallel line as a standby arrangement in case of block of primary pipe .
Make: Supreme, Prince, Astral
a | 25 mm Dia | Rmt | 30
b | 32 mm Dia | Rmt | 20
c | 40 mm Dia | Rmt | RO
2.12 | Supply, installation of Cowl piece connection with bird screen for VRF Outdoor units | Nos | 1
Note : | Quantities of refrigerant piping and cabling are based on the drawings with Indoor & Outdoor units Locations shown and for the specified configuration. Vendor to confirm refrigerant piping and cabling quantities based on the system configuration being offered by them.
SUB-TOTAL
3 | VENTILATION SYSTEM
3.1 | KITCHEN EXHAUST FAN
SITC of Cabinet type SISW Centrifugal Blower, Belt / Direct Drive, Statically & Dynamically Balanced, Backward Curved Impeller fan, Dunlop Anti- Vibration Pads etc. Motor should be outside stream with TEFC squirrel cage, weather protection shield, IP 55 rating with Class H Insulation, suitable for 3phase, 415volts, 50hz power supply. Sound level should be 65dB @ 3mtr distance. The quote shall include with MS frame, starter panel along with its required cable. Supplied with Dunlop Anti- Vibration Pads & Canvass Connection. Fan shall be BMS compatible. Power will be provided 5 ft away from fan and necessary control wiring with plug will be provided by AC contractor.(Vendor to crosscheck static pressure calculation).
Make : Kruger / Nicotra / Avantec
a | 6600 CFM, 65mm ESP (Class H) | Nos. | 1
3.2 | KITCHEN DRY SCRUBBER
SITC of Dry scrubber – Electrostatic Air cleaner with starter panel as per specifications, suitable for following capacities, including electrical starter panel . The Air filtration efficiency should be between 90 to 95% & units shall be staked one above other or side by side as per site requirement, if vendor will propose multiple units.
Finishing - Power coated, Dark Blue
Operating voltage - 220 Vac+/-10%, 50 Hz (Single phase)
Features - Short circuit, arc protection and auto restore power supply, BMS (Building Management System) terminals provided, Auto power cut-off when door is opened, Indicator LEDs for normal or wash indicator, Set of Terminals for remote LED normal or wash indicator
Efficiency - Upto 95%, meets NIOSH 5026 Oil Mist Test
Particle Size - Collects particles as small as 0.01 microns
Motor - Sealead ball bearings UL, single phase.
Cell - Ionizing voltage - 12 KVdc
Collector voltage - 6 KVdc
One cell comprising of 9 ionizing wires and 25 collection plates
Controls - Auto cut-off when door is opened. Indicator lights for fault, normal or wash function.
Pre-filter - Aluminium mesh, washable Dry contact for BMS.
Make: Rydair / Espair
| CFM - 6600 | Nos. | 1
3.2 | KITCHEN FRESH AIR FAN WITH AIRWASHER TYPE
SITC of CELDEK FILL package type air cooling unit with minimum 90% saturation efficiency. Air cooling unit shall be factory assembled and complete with double skin casing 0.8mm Inner / outer pre-coated GI sheets, DIDW forward curved fans with TEFC, sq. cage, induction motors 1440 RPM (IE-3) with IP-55 Protection. Suitable for operation on 415 ± 10% voltage, 50 Hz 3 phase AC supply, drive package including multi sheave pulleys and belts for fans and motors, 1.2mm thick tank & pad section in SS Construction, vibration isolators, wire mesh pre-filters, 200 mm thick CELDEK FILL, 1HP Water Circulation Pump (1W+1S), internal PVC piping, valves and fittings, 4-bend PVC eliminator. MERV 8 / G4 pleated pre-filters should be made of 100% synthetic media to capture common airborne contaminants as per ASHRAE Standard 52.2. (Vendor to crosscheck static pressure calculation)
Make : Kruger / Nicotra / Avantec
a | 5600 CFM, 50mm ESP (Class F) | Nos. | 1
3.3 | FRAMEWORK FOR FANS
| Supply, Fabrication and Installation of MS frame using channels/angle iron sections as required for mounting of ventilation fans & scrubber in areas shown in the layout. The frame work shall be applied with red oxide primer and thereafter, two coats of enamel paint of approved colour. The general arrangement drawing for frame work shall be got approved from the Architects/ Structural Engineers prior to commencement of fabrication. | Kg | 200
Note:
a. | Fan outlet velocity - 1600 FPM
b. | All cabinet fans should have plenum section.
c. | Fresh air fan if any,should to have 6mm thick synthetic media washable filter with framework.
d. | Contractor shall submit static pressure calculation for all above units to Client/Consultant.
e. | Any change in motor HP or coil selection shall be made at no extra cost to client.
f. | Fan efficiency shall be minimum 75%
g. | The cost shall be included liftting & shifting of each equipment / material with all necesaary arrnagement. Also, it shall be included the cost of scaffloding required for Installation of such material / equipment.
SUB-TOTAL
4 | SHEET METAL WORKS:
4.1 | FACTORY FABRICATED G.I RECTANGULAR DUCT
Supply, Fabrication, Testing, and Commissioning of Factory Fabricated GI Sheet Metal 120GSM Rectangular boxed ducting, Plenums, Cowls, Elbows with turning vanes, Splitters, Reducers, Flanges, Collars etc as per IS and Installaton as per SMACNA standards, The complete ducting shall be provided with MS Supports, Rods, Angles, Flanges, Bracing, Rubber Gaskets, Wooden frames, Canvas Connections, etc. as per drawings and specifications.
GI Sheet Makes : Tata, Jindal, SAIL, Ispat
Make: Rola Star, Zeco & Ductofab
a | 18 Gauge GI Sheet Metal Duct (Above 2251mm & Plenum) | Sq.mtr | 10
b | 20 Gauge GI Sheet Metal Duct (1501-2250mm) & For Kitchen Exhaust Works | Sq.mtr | 150
c | 22 Gauge GI Sheet Metal Duct (751-1500mm) | Sq.mtr | 100
d | 24 Gauge GI Sheet Metal Duct (0-750mm) | Sq.mtr | 120 |  |  | 0
0
4.2 | EXTRUDED ALUMINIUM CEILING GRILLES
Supply, Installation, Testing and Balancing of Powder coated aluminium supply air grilles complete with removable inner core as per approved shop drawing and specifications. The area of grille can be of any geometrical shape (Square/rectangular/Linear). The grilles shall be with 15/30/45° deflections as per requirement. The Colour shall be decided and approved by client and architect.
Make: Cosmos, Air Master & System Air
| Linear / Square / Rectangular Grille | Sq.mtr | 6
0
4.3 | SS EXHAUST AND FRESH AIR GRILLES
SITC of 18G S.S 304 Grills adjustable Double Deflector With S.S Volume Control Dampers. Grills to be of Double Deflection Type for ease of deflection on all sides and to have necessary built in Dampers for adjustable nature.
Make: Carryaire / System Air / Dynacraft / Air Master
a | Linear / Square / Rectangular Grille | Sq.mtr | 0.5
0
4.4 | DOOR TRANSFER GRILLE
SITC of Aluminium extruded powder coated Door transfer grills.
| Door transfer grille (Back to Back) | Sq.mtr | 1
Make: Cosmos, Air Master & System Air
4.5 | MULTI LEAF VOLUME CONTROL DAMPER
| SITC of opposed blade aerofoil type 1.2 mm thick Anodized Aluminium volume control dampers for ducts shall be provided with concealed gears, plastic operator and quadrants for manual control of volume of air flow and for proper balancing of the air distribution system as per the approved shop drawings and specifications. | Sq.mtr | 2.5
Make: Cosmos, Air Master & System Air
4.6 | OPPOSED BLADE DAMPER
| SITC of Aluminium Opposed blade dampers black powder coated vertical blades type for supply air collar. The damper should be gear operated type. | Sq.mtr | 2
0
4.7 | CANVAS CONNECTION
SITC of Flexible connections between mouth piece of Fan and initial piece of ducting with inspection zip. Flexible connections shall be double thickness non-flammable material (Fire retardant type).
a | For VRF Ductable Unit | Nos. | 3
c | For Kitchen EX & FA Fan | Nos. | 4 |  |  | 0
4.8 | CURTAIN TYPE FIRE DAMPER
SITC of fire dampers consist of 16G GI frame, 20G GI interlocking blades secured with SS springs, blades outside airstream clamped with fusible link UL-555 listed with melting point 165 / 225°F, etc; as per the approved shop drawings and specifications.
Make: Carryaire / System Air / Dynacraft / Air Master
a | Bare fire dampers | Sq.mtr | 1
b | Fusible link as per specification UL 555 | No | 1
NOTES:
The ducting support should be as per tender specification and additional supports are to be provided by Contractor as decided by Consultant.
Muslin cloth cover for all air outlets during construction.
Pressure testing of complete duct work as per DW/ SMACNA standard.
Silicon sealant for longitudinal & transverse joints as per specification.
Diffusers & grilles shall be powder coated as per color approved by Architect.
SUB-TOTAL
5 | THERMAL & ACOUSTIC INSULATION:
5.1 | THERMAL INSULATION
| Supply & fixing of Thermal insulation for supply air duct using 19mm thick class " O " Closed cell nitrile rubber with anti-microbial coating on it. Insulation shall have Thermal conductivity of 0.033 W/(m.K) and water vapor permeance of 0.10. Joints should be sealed with 50 mm wide 3 mm thick self adhesive tape. The duct shall be stick with recommended adhesive. | Sq.mtr | 100
Make: Armaflex / K-flex / Aerofoam / ALP Aeroflex
5.2 | ACOUSTIC INSULATION
| Supply & fixing acoustic insulation for ducting using Class "1" closed cell elastomeric insulation of 10mm thick Nitrile rubber insulation adhesive, longitudinal & transverse joints sealed with adhesive in neat & clean manner. Material shall be processed Nitrile Rubber foam with anti-microbial protection. Insulation shall have thermal conductivity of 0.047 W/(m.K) and density of 140 - 180 kg/m³. | Sq.mtr | 25
Make: Armaflex / K-flex / Aerofoam / ALP Aeroflex
5.3 | THERMAL INSULATION FOR KITCHEN EXHAUST DUCTS
| SITC of 80mm thick Glass Fibre Blanket Insulation material bonded with Thrmosetting Resin, with factory applied laminated aluminium foil of 22 micrns with fibre glass backing. Further, wire mesh along with 7 mil cloth shall be applied on above the insulation with proper adhersive. Nominal density : 32 Kg/CuM. Thermal conductivity, < 0.033 W/m.K at 24 degreeC. All Insuation material and adhesives shall be as per Class I for surface spread and in accordance with BS 476, & Class O for non-combustible grade. | Sq.mtr | 150
Make: Rockwool / UP Twiga
Note:
a. | Insulation work to be coordinated with other agencies and repair to be included by contractor as per site requirement.
b. | Vendors to take care of the installation, if any damages takes place the vendor to repair or replace and hand over to clients in good and acceptable condition.
c. | Thermal insulation shall be internal for Elliptical / Expossed ducting.
SUB-TOTAL
6 | ELECTRICAL WORKS:
6.1 | STARTER PANEL FOR FAN WITH VFD
SITC of indoor / outdoor, wall mounting type 3PH, 415VAC MOTOR STARTERS IN CRCA SHEET STEEL ENCLOSURE with necssary supporting brackets and required accessories, etc., The Enclosure shall be provided with knockouts suitable for cable termination at TOP & BOTTOM for incoming and outgoing power cables of A2XFY type and size specified. The starters shall be complete with suitable MPCB/MCCB, Contactor, Bi-metal O/L relay with SPP, ON/OFF Push buttons, on / off / trip indication Lamp, on off push button, & phase indication Lamp. Selection of relay, contractor, MPCB/MCCB etc. as per Type-2 Coordination. Panel shall have provision to connect with BMS. Variable frequency drives shall be provided with necessary sensors and controllers complete with control wiring in all respect as required. VFDs shall be provided with necessary bypass arrangement inside electrical starter panels with IP-55 enclosure.
b | Suitable for 6600 CFM Kitchen Exhaust Fan, Star Delta Panel with VFD | Nos. | RO
c | Suitable for 5600 CFM Kitchen Air-washer, Star Delta Panel with VFD | Nos. | RO
6.2 | POWER CABLING
Supply, handling, laying effecting proper connections testing and commissioning of following sizes of 1.1 KV grade XLPE insulated FRLS Aluminium /Copper conductor cables laid over MS supports cable racks or fixing on walls including clamping the cable to supports in an approved manner as required complete with Copper earthing as specified for continuous earthing along with cable. All complete as required and as per final instruction as given by Owners/ Consultants and as per Technical specifications. Earthing shall be measured separately and shall be connected in two runs. Power to ELCB to be provided near each ODU by electrical contractor.
a | Suitable Power Cable:
| Suitable for 6600 CFM Kitchen Exhaust Fan, Star Delta Panel with VFD | Rmt | 10 |  |  | 0
| Suitable for 5600 CFM Kitchen Air-washer, Star Delta Panel with VFD | Rmt | 10 |  |  | 0
b | Earthing:
| 8 SWG | Rmt | 40 |  |  | 0
6.3 | CABLE TERMINATION :
Supply & Making of Cable termination of armoured / unarmoured cables 1.1 KV grade including installation of cable glands, cable lugs (Aluminium for A2XFY & copper for 2XFY & YY Double compression type), heat shrinkable sleeves on long ends, crimping paste etc. The work includes testing & commissioning of cables, meggaring values & submitting reports of tests. (One set includes termination of all cores of one end only). All crimping tools & dies shall be arranged by contractor.
a | Suitable for 6600 CFM Kitchen Exhaust Fan, Star Delta Panel with VFD | Nos. | 2 |  |  | 0
b | Suitable for 5600 CFM Kitchen Air-washer, Star Delta Panel with VFD | Nos. | 2
6.4 | CABLE TRAYS
Supplying & Fixing of following sizes of GI cable tray duly painted perforated type of height 50mm along with necessary bends, reducers etc. anchored along the wall / suspended from the ceiling with necessary MS supports.
a | 50mm wide x 50mm ht x 1.6mm thick | Rmt | 20 |  |  | 0
SUB-TOTAL
GRAND TOTAL