## SUMMERY
NANDO @ DELHI
SUMMARY FOR ELECTRICAL LOAD
REVISION: R1, DATE: 10.10.2024
Sr.No. | DESCRIPTION | WATTAGE (W) | No of Units | CONNECTED LOAD | MAX. DMD LOAD | DIVERSITY | UPS LOAD
1 | LIGHTING LOAD
a | 600mm X 600mm DROP IN LED CEILING LIGHT | 12 | 7 | 84 | 67.2 | 80%
b | BOH 600mm LONG SURFACE MOUNTED EMERGENCY LIGHT | 18 | 3 | 54 | 43.2 | 80%
c | 4 FT (2 TUBE) KB53 LIGHT | 32 | 4 | 128 | 102.4 | 80%
d | FOH EMERGENCY DOWNLIGHT | 18 | 0 | 0 | 0 | 80%
e | HEAT LAMPS | 300 | 4 | 1200 | 960 | 80%
f | WARM WHITE DOWNLIGHT -L2 | 20 | 16 | 320 | 256 | 80%
h | WARM WHITE DOWNLIGHT -L3 | 35 | 7 | 245 | 196 | 80%
i | WARM WHITE DOWNLIGHT -L4 | 30 | 4 | 120 | 96 | 80%
j | WARM WHITE DOWNLIGHT -L5 | 30 | 6 | 180 | 144 | 80%
k | WARM WHITE DOWNLIGHT -L6 | 30 | 1 | 30 | 24 | 80%
l | WARM WHITE WALL LIGHT -L7 & L8 | 30 | 7 | 210 | 168 | 80%
| Total Lighting KW load |  |  | 2.571 | 2.0568
2 | RAW POWER LOAD
a | 6A Switch sockets Raw power | 100 | 12 | 1200 | 600 | 50%
b | 6A Switch sockets UPS power | 100 | 2 | 200 | 200 | 100% | 200
c | 6/16A Switch sockets RAW power | 100 | 2 | 200 | 100 | 50%
d | POS counters | 150 | 3 | 450 | 315 | 70% | 450
e | KOT | 75 | 1 | 75 | 75 | 100% | 75
f | KDS | 75 | 6 | 450 | 360 | 80% | 450
f | Signage | 15 | 1 | 15 | 12 | 80% | 15
g | External Signage | 75 | 2 | 150 | 150 | 100%
h | Digital Screen | 250 | 2 | 500 | 400 | 80%
| Total Power KW load |  |  | 3.24 | 2.212
3 | ELV LOAD |  |  | 3 | 3 | 100% | 2000
4 | HVAC LOAD
a | 5.5 TR DX DUCTABLE UNIT | 6500 | 2 | 13 | 10.4 | 80%
b | FRESH AIR | 5500 | 1 | 5.5 | 4.4 | 80%
c | EXHAUST AIR FAN | 7500 | 1 | 7.5 | 6 | 80%
5 | KITCHEN EQUIPMENTS |  |  | 63.7 | 47.775 | 75%
9 | MISCELLANEOUS |  |  | 3 | 1.5 | 50%
| TOTAL LOAD IN KW |  |  | 101.511 | 77.3438 |  | 3190
UPS CALCULATIONS
| Total C & S Load | [5 empty] | 3190
| TOTAL EMERGENCY LOAD 15% of total lighting load | [5 empty] | 0.38565
| TOTAL UPS LOAD | [5 empty] | 3190.3857
| Load Factor 85% - UPS Load shall be (WATTAGE) | [5 empty] | 2711.8278
| After considering 0.85 power factor - VA Rating | [5 empty] | 3190.3857
| Efficiency 85% - UPS Rating shall be (VA) | [5 empty] | 3753.3949
| Recommended UPS rating (KVA) -3PH. I/C & 1PH. O/G .(with Plus Minus 5%) | [5 empty] | 3.7534
| Nearest size available- (1#6KVA) | [5 empty] | 6

## Kitchen BOQ
Sr.No | Equipment Name | Qty | KW | TOTAL KW | Ph | R | Y | B |  | R | Y | B
1 | BUN TOASTER | 1 | 3 | 3 | I |  | 3
2 | 15L WATER BOILER | 1 | 3 | 3 | I |  |  |  |  | 3
3 | COKE MACHINE | 1 | 0.5 | 0.5 | I | 0.5
4 | SINGLE PAN BAIN MARIE - TABLE MODEL | 1 | 0.3 | 0.3 | I | 0.3
5 | PANINI TOASTING GRILL | 1 | 3 | 3 | I | 3
6 | FRONT LOADER GLASS WASHER | 1 | 2.1 | 2.1 | I | [5 empty] | 2.1
7 | BLENDER | 2 | 0.6 | 1.2 | I |  | 0.6 | 0.6
8 | MICROWAVE OVEN | 1 | 1.5 | 1.5 | I |  |  | 1.5
9 | 2 DOOR ALTO-SHAAM WARMER1 | 2 | 0.9 | 1.8 | I | 0.9 | 0.9
10 | ADDITIONAL POINT FOR INDUCTION OR MIXER | 1 | 0.5 | 0.5 | I | [6 empty] | 0.5
11 | 2 DOOR SALADTTE UNDER BAR FRIDGE | 1 | 0.75 | 0.75 | I |  |  | 0.75
12 | POST MIX TBC WITH COKE AGENT | 0 | 0.7 | 0 | I
13 | 2 DOOR UNDER BAR FRIDGE - CUPBOARD | 1 | 1.5 | 1.5 | I |  | 1.5
14 | 3L INSTANT GEYSER | 2 | 3 | 6 | I | [5 empty] | 3 | 3
15 | UNDER COUNTER ICE MACHINE | 1 | 2 | 2 | I |  |  |  |  | 2
16 | CHIP DUMP WITH TOP HEAT | 1 | 1.8 | 1.8 | I |  |  | 1.8
17 | CHEST FREEZER | 1 | 1.5 | 1.5 | I | 1.5
19 | BAR UNIT | 1 | 0.75 | 0.75 | I |  |  | 0.75
20 | DRAUGHT MACHINE | 1 | 0.1 | 0.1 | I |  | 0.1
21 | DOUBLE DOOR UC COOLER | 0 | 0.56 | 0 | I
22 | BEVERAGE | 0 | 1.5 | 0 | I
22 | HAND DRYER | 1 | 0.5 | 0.5 | I | [6 empty] | 0.5
22 | FLYCATHER | 4 | 0.1 | 0.4 | I |  |  | 0.2 |  |  |  | 0.2
| OFFICE ACCESSORIES | 2 | 0.3 | 0.6 | I | [6 empty] | 0.6
23 | AIR CURTAIN | 1 | 0.3 | 0.3 | I |  |  | 0.5 | EXTRA POWER |  | 0.3
24 | CHARGING POINT | 12 | 0.05 | 0.6 | I |  |  |  |  | 0.3 |  | 0.3
25 | DISHWASHER | 1 | 11 | 11 | III
26 | OVEN | 1 | 19 | 19 | III
27 | COLD ROOM | 0 | 8 | 0 | III
TOTAL LOAD |  |  |  | 63.7 |  | 6.2 | 6.1 | 6.1 |  | 5.3 | 5.4 | 5.1
[7 empty] | 18.4 |  |  |  | 15.8