## Price Comparison
|  | RFQ No: R0062 COST COMPARISON REPORT | RFQ No: R0062 COST COMPARISON REPORT | RFQ No: R0062 COST COMPARISON REPORT | Comp. Date : 15/01/2024 | Comp. Date : 15/01/2024 | Comp. Date : 15/01/2024 | Vendor Name : PIONEER PROJECT SOLUTION (RV232414136) | [5 empty] | Vendor Name : ANJLE MEP PROJECTS PVT LTD (RV232413533) | [5 empty] | Vendor Name : Pikture Perfect Design Studio Pvt. Ltd (RV232413816) | [5 empty] | Vendor Name : Mahamaya Engineering (T051945)
|  | RFQ No: R0062 COST COMPARISON REPORT | RFQ No: R0062 COST COMPARISON REPORT | RFQ No: R0062 COST COMPARISON REPORT | RFQ #: R0062 | RFQ #: R0062 | RFQ #: R0062 | Contact Name : Mohd Ashraf | [5 empty] | Contact Name : Priyanka/Premkant Rajpoot | [5 empty] | Contact Name : Gangadhar Sharma | [5 empty] | Contact Name : Yash Katoch
|  | RFQ No: R0062 COST COMPARISON REPORT | RFQ No: R0062 COST COMPARISON REPORT | RFQ No: R0062 COST COMPARISON REPORT | RFQ Date : 15/01/2024 20:21:52 | RFQ Date : 15/01/2024 20:21:52 | RFQ Date : 15/01/2024 20:21:52 | Vendor City : | [5 empty] | Vendor City : | [5 empty] | Vendor City : | [5 empty] | Vendor City : Delhi
|  | RFQ No: R0062 COST COMPARISON REPORT | RFQ No: R0062 COST COMPARISON REPORT | RFQ No: R0062 COST COMPARISON REPORT | BCD Date : 15/01/2024 20:48:00 | BCD Date : 15/01/2024 20:48:00 | BCD Date : 15/01/2024 20:48:00 | Telephone # : | [5 empty] | Telephone # : | [5 empty] | Telephone # : | [5 empty] | Telephone # :
|  | RFQ No: R0062 COST COMPARISON REPORT | RFQ No: R0062 COST COMPARISON REPORT | RFQ No: R0062 COST COMPARISON REPORT |  |  |  | Mobile # : | [5 empty] | Mobile # : | [5 empty] | Mobile # : | [5 empty] | Mobile # : 9205300857
PR Number : TFSPL-2324-00122 | PR Number : TFSPL-2324-00122 | PR Number : TFSPL-2324-00122 | PR Number : TFSPL-2324-00122 | PR Number : TFSPL-2324-00122 | PR Number : TFSPL-2324-00122 | PR Number : TFSPL-2324-00122 | PR Number : TFSPL-2324-00122 | Email : projectspioneer@gmail.com | [5 empty] | Email : anjlemepprojects@gmail.com | [5 empty] | Email : piktureperfectdesignstudio@gmail.com | [5 empty] | Email : mahamaya.engineering1@gmail.com
Package / RFQ Name : BOQ for HVAC for Delhi T1-Subway Outlet | Package / RFQ Name : BOQ for HVAC for Delhi T1-Subway Outlet | Package / RFQ Name : BOQ for HVAC for Delhi T1-Subway Outlet | Package / RFQ Name : BOQ for HVAC for Delhi T1-Subway Outlet | Package / RFQ Name : BOQ for HVAC for Delhi T1-Subway Outlet | Package / RFQ Name : BOQ for HVAC for Delhi T1-Subway Outlet | Package / RFQ Name : BOQ for HVAC for Delhi T1-Subway Outlet | Package / RFQ Name : BOQ for HVAC for Delhi T1-Subway Outlet | Round # : 3 (RFQ) | [5 empty] | Round # : 3 (RFQ) | [5 empty] | Round # : 3 (RFQ) | [5 empty] | Round # : 3 (RFQ)
Buyer : Sarvesh Patil / Technical : / Approver : | Buyer : Sarvesh Patil / Technical : / Approver : | Buyer : Sarvesh Patil / Technical : / Approver : | Buyer : Sarvesh Patil / Technical : / Approver : | Buyer : Sarvesh Patil / Technical : / Approver : | Buyer : Sarvesh Patil / Technical : / Approver : | Buyer : Sarvesh Patil / Technical : / Approver : | Buyer : Sarvesh Patil / Technical : / Approver : | Quotation Date : |  |  | Quotation Validity Date : |  |  | Quotation Date : |  |  | Quotation Validity Date : |  |  | Quotation Date : |  |  | Quotation Validity Date : |  |  | Quotation Date : |  |  | Quotation Validity Date :
Comp. # : 3 | Comp. # : 3 | Comp. # : 3 | Comp. # : 3 | Comp. # : 3 | Currency :INR | Currency :INR | Currency :INR | Buyer Remark : | [5 empty] | Buyer Remark : | [5 empty] | Buyer Remark : | [5 empty] | Buyer Remark :
Comp. # : 3 | Comp. # : 3 | Comp. # : 3 | Comp. # : 3 | Comp. # : 3 | BUDGET PRICE : | .00 |  | Quote Currency : INR | [5 empty] | Quote Currency : INR | [5 empty] | Quote Currency : INR | [5 empty] | Quote Currency : INR
# | Item Code | Item Description | Unit | Qty | Last PO Details | Lowest Unit Rate | Lowest Vendor | First Bid | Disc % | GST % | Technical | Unit Price | Total | First Bid | Disc % | GST % | Technical | Unit Price | Total | First Bid | Disc % | GST % | Technical | Unit Price | Total | First Bid | Disc % | GST % | Technical | Unit Price | Total
1 |  | BOQ for HVAC for Delhi T1-Subway Outlet | NOS | 1.00 |  | 603590.00 | ANJLE MEP PROJECTS PVT LTD | 673360.00 | 0.00 | 18.00 |  | 673,360.00 | 673,360.00 | 860650.00 | 0.00 | 18.00 |  | 603,590.00 | 603,590.00 | 897125.00 | 0.00 | 18.00 |  | 897,125.00 | 897,125.00 | 1243550.00 | 0.00 | 28.00 |  | 1,243,550.00 | 1,243,550.00
Item Total | [8 empty] | .00 | 121,204.80 |  |  | 673,360.00 |  | .00 | 108,646.20 |  |  | 603,590.00 |  | .00 | 161,482.50 |  |  | 897,125.00 |  | .00 | 348,194.00 |  |  | 1,243,550.00
Discount Total Value | [7 empty] | Grand Dis. Amt | .00 |  |  |  | .00 | Grand Dis. Amt | .00 |  |  |  | .00 | Grand Dis. Amt | .00 |  |  |  | .00 | Grand Dis. Amt | .00 |  |  |  | .00
GST Total Amount | [12 empty] | 121,204.80 | [5 empty] | 108,646.20 | [5 empty] | 161,482.50 | [5 empty] | 348,194.00
Net Landed Cost | [11 empty] | INR | 794,564.80 |  |  |  |  | INR | 712,236.20 |  |  |  |  | INR | 1,058,607.50 |  |  |  |  | INR | 1,591,744.00
Vendor Status | [7 empty] | Round # : 3 (RFQ) | Round # : 3 (RFQ)
Sr No. | Vendor Code | Vendor Name | [5 empty] | Status | Remarks
1 | T051601 | Vart Infra | [5 empty] | Not Participate
2 | T051606 | SM Infra | [5 empty] | Participate
3 | RV232414136 | PIONEER PROJECT SOLUTION | [5 empty] | Participate
4 | RV232413816 | Pikture Perfect Design Studio Pvt. Ltd | [5 empty] | Participate
5 | RV232413533 | ANJLE MEP PROJECTS PVT LTD | [5 empty] | Participate
6 | T051945 | Mahamaya Engineering | [5 empty] | Participate
7 | T051881 | ACEPL | [5 empty] | Not Participate

## BOQ Price Bid
|  | RFQ No: R0062 COST COMPARISON REPORT | RFQ No: R0062 COST COMPARISON REPORT | Comp. Date : 15/01/2024 | Comp. Date : 15/01/2024 | Comp. Date : 15/01/2024 | Vendor Name : PIONEER PROJECT SOLUTION | Vendor Name : PIONEER PROJECT SOLUTION | Vendor Name : ANJLE MEP PROJECTS PVT LTD | Vendor Name : ANJLE MEP PROJECTS PVT LTD | Vendor Name : Pikture Perfect Design Studio Pvt. Ltd | Vendor Name : Pikture Perfect Design Studio Pvt. Ltd | Vendor Name : Mahamaya Engineering | Vendor Name : Mahamaya Engineering
|  | RFQ No: R0062 COST COMPARISON REPORT | RFQ No: R0062 COST COMPARISON REPORT | RFQ #: R0062 | RFQ #: R0062 | RFQ #: R0062 | Contact Name : Mohd Ashraf | Contact Name : Mohd Ashraf | Contact Name : Priyanka/Premkant Rajpoot | Contact Name : Priyanka/Premkant Rajpoot | Contact Name : Gangadhar Sharma | Contact Name : Gangadhar Sharma | Contact Name : Yash Katoch | Contact Name : Yash Katoch
|  | RFQ No: R0062 COST COMPARISON REPORT | RFQ No: R0062 COST COMPARISON REPORT | RFQ Date : 15/01/2024 20:21:52 | RFQ Date : 15/01/2024 20:21:52 | RFQ Date : 15/01/2024 20:21:52 | Vendor City : | Vendor City : | Vendor City : | Vendor City : | Vendor City : | Vendor City : | Vendor City : Delhi | Vendor City : Delhi
|  | RFQ No: R0062 COST COMPARISON REPORT | RFQ No: R0062 COST COMPARISON REPORT | BCD Date : 15/01/2024 20:48:00 | BCD Date : 15/01/2024 20:48:00 | BCD Date : 15/01/2024 20:48:00 | Telephone # : | Telephone # : | Telephone # : | Telephone # : | Telephone # : | Telephone # : | Telephone # : | Telephone # :
|  | RFQ No: R0062 COST COMPARISON REPORT | RFQ No: R0062 COST COMPARISON REPORT |  |  |  | Mobile # : | Mobile # : | Mobile # : | Mobile # : | Mobile # : | Mobile # : | Mobile # : 9205300857 | Mobile # : 9205300857
PR Number : TFSPL-2324-00122 | PR Number : TFSPL-2324-00122 | PR Number : TFSPL-2324-00122 | PR Number : TFSPL-2324-00122 | PR Number : TFSPL-2324-00122 | PR Number : TFSPL-2324-00122 | PR Number : TFSPL-2324-00122 | Email : projectspioneer@gmail.com | Email : projectspioneer@gmail.com | Email : anjlemepprojects@gmail.com | Email : anjlemepprojects@gmail.com | Email : piktureperfectdesignstudio@gmail.com | Email : piktureperfectdesignstudio@gmail.com | Email : mahamaya.engineering1@gmail.com | Email : mahamaya.engineering1@gmail.com
Package / RFQ Name : BOQ for HVAC for Delhi T1-Subway Outlet | Package / RFQ Name : BOQ for HVAC for Delhi T1-Subway Outlet | Package / RFQ Name : BOQ for HVAC for Delhi T1-Subway Outlet | Package / RFQ Name : BOQ for HVAC for Delhi T1-Subway Outlet | Package / RFQ Name : BOQ for HVAC for Delhi T1-Subway Outlet | Package / RFQ Name : BOQ for HVAC for Delhi T1-Subway Outlet | Package / RFQ Name : BOQ for HVAC for Delhi T1-Subway Outlet | Round # : 3 (RFQ) | Round # : 3 (RFQ) | Round # : 3 (RFQ) | Round # : 3 (RFQ) | Round # : 3 (RFQ) | Round # : 3 (RFQ) | Round # : 3 (RFQ) | Round # : 3 (RFQ)
Buyer : Sarvesh Patil | Buyer : Sarvesh Patil | Buyer : Sarvesh Patil | Buyer : Sarvesh Patil | Buyer : Sarvesh Patil | Buyer : Sarvesh Patil | Buyer : Sarvesh Patil | Techanical Score : | Techanical Score : | Techanical Score : | Techanical Score : | Techanical Score : | Techanical Score : | Techanical Score : | Techanical Score :
Comp. # : 3 | Comp. # : 3 | Comp. # : 3 | Comp. # : 3 | Currency :INR | Currency :INR | Currency :INR | Quotation Date : | Quotation Date : | Quotation Date : | Quotation Date : | Quotation Date : | Quotation Date : | Quotation Date : | Quotation Date :
Comp. # : 3 | Comp. # : 3 | Comp. # : 3 | Comp. # : 3 | BUDGET PRICE :.00 | BUDGET PRICE :.00 | BUDGET PRICE :.00 | Quotation Validity Date : | Quotation Validity Date : | Quotation Validity Date : | Quotation Validity Date : | Quotation Validity Date : | Quotation Validity Date : | Quotation Validity Date : | Quotation Validity Date :
Sr No. | Item Code | Item Name | Item Description | UOM | Qty | Minimum Amount | Unit Price | Amount | Unit Price | Amount | Unit Price | Amount | Unit Price | Amount
1 |  | BOQ for HVAC for Delhi T1-Subway Outlet | BOQ for HVAC for Delhi T1-Subway Outlet | NOS | 1 | 390510 |  | 493360 |  | 439690 |  | 843125 |  | 728550
1 |  | Note | Note
2 |  | Prices shall be based on supply, installation, testing commissioning (SITC) at site including all taxes, duties, transportation insurance etc. | Prices shall be based on supply, installation, testing commissioning (SITC) at site including all taxes, duties, transportation insurance etc.
30 | 2 | CHILLED WATER PIPING WITH INSULATION | CHILLED WATER PIPING WITH INSULATION
31 | 2.1 | CHW PIPE | CHW PIPE
32 |  | SITC of MS Heavy duty class C ERW Chilled Water pipe conforming to IS 1239 - 2004 primer painted including bends, tees, MS supports, PUFF saddles, anchor fasteners, steel angles and any other material required to complete the work. The piping flange connection bolts, washers and nuts should be hot dipped galvanised. Flourscent Plastic Sticker paint shall be applied to indicate Water flow directions. Only End flanges to be used for capping of pipes. Table E of BS code for flange thickness to be adhered. | SITC of MS Heavy duty class C ERW Chilled Water pipe conforming to IS 1239 - 2004 primer painted including bends, tees, MS supports, PUFF saddles, anchor fasteners, steel angles and any other material required to complete the work. The piping flange connection bolts, washers and nuts should be hot dipped galvanised. Flourscent Plastic Sticker paint shall be applied to indicate Water flow directions. Only End flanges to be used for capping of pipes. Table E of BS code for flange thickness to be adhered.
33 |  | Make Jindal Hissar TATA | Make Jindal Hissar TATA
34 |  | F 32 mm | F 32 mm | Rmt | 20 | 19000 | 950 | 19000 | 950 | 19000 | 2150 | 43000 | 1170 | 23400
35 | 2.2 | CHILLED WATER PIPING INSULATION - INTERNAL USE | CHILLED WATER PIPING INSULATION - INTERNAL USE
36 |  | SITC of insulation for chilled water. piping. For internal pipe - Stick 25mm thick Nitrile rubber class O Closed cell nitrile rubber with anti-microbial coating on it. Insulation shall have Thermal conductivity of 0.033 W (m.K) and water vapor permeance of 0.10. Joints should be sealed with 50 mm wide 3 mm thick self adhesive tape and putting PVC bands at all supports. | SITC of insulation for chilled water. piping. For internal pipe - Stick 25mm thick Nitrile rubber class O Closed cell nitrile rubber with anti-microbial coating on it. Insulation shall have Thermal conductivity of 0.033 W (m.K) and water vapor permeance of 0.10. Joints should be sealed with 50 mm wide 3 mm thick self adhesive tape and putting PVC bands at all supports.
37 |  | Make Armaflex K-flex | Make Armaflex K-flex
38 |  | F 32 mm | F 32 mm | Rmt | 20 | 8600 | 450 | 9000 | 430 | 8600 | 550 | 11000 | 1000 | 20000
39 | 2.3 | BALL VALVE | BALL VALVE
40 |  | SITC of following sizes of Ball Valve consist of Cap, Brass Body, Rated for 150 psi SWP, 600 psi WOG Pressure Two-piece construction; with brass body, regular port, B-16 chrome-plated ball and stem, replaceable “Teflon” or “TFE” seats and seals, blowout-proof stem, vinyl covered steel handle, threaded or soldered ends and extended stem for insulated piping. Same valve shall be used as a Drain valve. | SITC of following sizes of Ball Valve consist of Cap, Brass Body, Rated for 150 psi SWP, 600 psi WOG Pressure Two-piece construction; with brass body, regular port, B-16 chrome-plated ball and stem, replaceable “Teflon” or “TFE” seats and seals, blowout-proof stem, vinyl covered steel handle, threaded or soldered ends and extended stem for insulated piping. Same valve shall be used as a Drain valve.
41 |  | Make Zoloto Audco Kitz | Make Zoloto Audco Kitz
42 |  | F 32 mm | F 32 mm | Nos. | 3 | 6900 | 3850 | 11550 | 3250 | 9750 | 2300 | 6900 | 6000 | 18000
43 | 2.4 | BALL VALVE WITH Y-STRAINER | BALL VALVE WITH Y-STRAINER
44 |  | SITC of following sizes of Brass Ball Valve with Y-Strainer consist of Cap, Brass Body, Rated for 150 psi SWP, 600 psi WOG Pressure Two-piece construction; with brass body, regular port, B-16 chrome-plated ball and stem, replaceable “Teflon” or “TFE” seats and seals, blowout-proof stem, vinyl covered steel handle, threaded or soldered ends and extended stem for insulated piping. Filter element shall be of non magnetic SS sheet with perforation. | SITC of following sizes of Brass Ball Valve with Y-Strainer consist of Cap, Brass Body, Rated for 150 psi SWP, 600 psi WOG Pressure Two-piece construction; with brass body, regular port, B-16 chrome-plated ball and stem, replaceable “Teflon” or “TFE” seats and seals, blowout-proof stem, vinyl covered steel handle, threaded or soldered ends and extended stem for insulated piping. Filter element shall be of non magnetic SS sheet with perforation.
45 |  | Make Zoloto Audco Kitz | Make Zoloto Audco Kitz
46 |  | F 32 mm | F 32 mm | No. | 1 | 2850 | 4500 | 4500 | 2850 | 2850 | 5500 | 5500 | 10500 | 10500
47 | 2.5 | PIBCV VALVES | PIBCV VALVES
48 |  | SITC of Pressure Independent Balancing cum Control Valves (PIBCV) including integrated motorised control valve and balancing device for combined flow and water balancing requirement. Valve body to be rated for PN 16. The valve design flow rate should be factory calibrated with + - 5% flow accuracy. Valve shall have necessary measuring ports, drain port, flanges etc., Valve shall also provide temperature sensor with necessary cabling (min 2mtr length to be considered with each valve). The balancing to be done through microprocessor based hand held terminal POT and the same results shall be furnished in the water balancing report as part of commissioning report and handing over manual. | SITC of Pressure Independent Balancing cum Control Valves (PIBCV) including integrated motorised control valve and balancing device for combined flow and water balancing requirement. Valve body to be rated for PN 16. The valve design flow rate should be factory calibrated with + - 5% flow accuracy. Valve shall have necessary measuring ports, drain port, flanges etc., Valve shall also provide temperature sensor with necessary cabling (min 2mtr length to be considered with each valve). The balancing to be done through microprocessor based hand held terminal POT and the same results shall be furnished in the water balancing report as part of commissioning report and handing over manual.
49 |  | Make Oventrop Siemens Danfoss | Make Oventrop Siemens Danfoss
50 |  | F 32 mm | F 32 mm | No. | 1 | 30500 | 30500 | 30500 | 36500 | 36500 | 48500 | 48500 | 37000 | 37000
51 | 2.6 | Auto Air Vent Valves | Auto Air Vent Valves
52 |  | Make Anergy Flamco | Make Anergy Flamco
53 |  | Providing and fitting Auto Vent Valves. | Providing and fitting Auto Vent Valves.
54 |  | SITC of Auto air vent in each risers common headers AHU. 3 4 auto vent valves at each coil riser header. | SITC of Auto air vent in each risers common headers AHU. 3 4 auto vent valves at each coil riser header. | Nos. | 2 | 3700 | 2000 | 4000 | 1850 | 3700 | 3500 | 7000 | 3800 | 7600
55 | 2.7 | SITC of Pressure gauges Thermometers | SITC of Pressure gauges Thermometers
56 |  | Make H Guru Waree | Make H Guru Waree
57 |  | Necessary pressure gauges and thermometers 4 Dial type. | Necessary pressure gauges and thermometers 4 Dial type.
58 |  | Water Pressure gauges 150mm dial complete with gauge valves, mounting, fittings and copper tubing extension wherever required. Pressure gauges Range 0-10 Kg CM2 | Water Pressure gauges 150mm dial complete with gauge valves, mounting, fittings and copper tubing extension wherever required. Pressure gauges Range 0-10 Kg CM2 | Nos. | 2 | 2900 | 1800 | 3600 | 1450 | 2900 | 3950 | 7900 | 5000 | 10000
59 |  | Thermometers of the mercury in glass stem type and copper separable well complete with guard etc., of industrial grade mounting on water lines. Length 9 12 inches, Thermometer, Range 0-50 deg C | Thermometers of the mercury in glass stem type and copper separable well complete with guard etc., of industrial grade mounting on water lines. Length 9 12 inches, Thermometer, Range 0-50 deg C | Nos. | 2 | 2300 | 1150 | 2300 | 2050 | 4100 | 2850 | 5700 | 3500 | 7000
60 |  | Thermowells | Thermowells | Nos. | 4 | 2200 | 550 | 2200 | 950 | 3800 | 5500 | 22000 | 3000 | 12000
61 |  | SITC of Brass Test Plug of industrial grade mounting on water | SITC of Brass Test Plug of industrial grade mounting on water | Nos. | 1 | 1650 | 1650 | 1650 | 1950 | 1950 | 1850 | 1850 | 2500 | 2500
62 | 2.8 | INSULATED CONDENSATE DRAIN PIPE | INSULATED CONDENSATE DRAIN PIPE
63 |  | SITC of UPVC pipes of following sizes for drain with necessary supports and fittings such as elbows, tees reducers etc. The insulation line to be insulated with nitrile rubber insulation of thickness 9mm and wrapped by weather proof protection tape. The Pipe wherever concealed should also have a parallel line as a standby arrangement in case of block of primary pipe . | SITC of UPVC pipes of following sizes for drain with necessary supports and fittings such as elbows, tees reducers etc. The insulation line to be insulated with nitrile rubber insulation of thickness 9mm and wrapped by weather proof protection tape. The Pipe wherever concealed should also have a parallel line as a standby arrangement in case of block of primary pipe .
64 |  | Make Supreme, Prince, Astral | Make Supreme, Prince, Astral
65 |  | F 25 mm | F 25 mm | Rmt | 10 | 1600 | 160 | 1600 | 210 | 2100 | 650 | 6500 | 600 | 6000
66 |  | F 32 mm | F 32 mm | Rmt | 2 | 360 | 180 | 360 | 270 | 540 | 750 | 1500 | 800 | 1600
67 |  | NOTES FOR PIPING | NOTES FOR PIPING
68 |  | Cover all open pipe ends with muslin cloth during construction | Cover all open pipe ends with muslin cloth during construction
69 |  | Pipe cleaning chemical treatment as per specs shall be included in the piping cost. | Pipe cleaning chemical treatment as per specs shall be included in the piping cost.
70 |  | Unit rates for all indicated sizes of pipes valves shall be furnished. | Unit rates for all indicated sizes of pipes valves shall be furnished.
71 |  | Cleaning Painting of pipe before insulation shall be included in piping cost. | Cleaning Painting of pipe before insulation shall be included in piping cost.
72 |  | The piping support should be as per tender specification and additional supports are to be provided Contractor as decided by Consultant. | The piping support should be as per tender specification and additional supports are to be provided Contractor as decided by Consultant.
73 |  | All the valves shall be insulated with the same material as that of Chilled water pipng and cost of insulation for valves shall be considered. | All the valves shall be insulated with the same material as that of Chilled water pipng and cost of insulation for valves shall be considered.
74 |  | SUB-TOTAL | SUB-TOTAL
92 | 4 | SHEET METAL WORKS | SHEET METAL WORKS
93 | 4.1 | GI SHEET METAL DUCTING | GI SHEET METAL DUCTING
94 |  | Supply, Fabrication, Testing, and Commissioning of Factory Fabricated GI Sheet Metal 120GSM Rectangular boxed ducting, Plenums, Cowls, Elbows with turning vanes, Splitters, Reducers, Flanges, Collars etc as per IS 655 and installation as per SMACNA standards, The complete ducting shall be provided with MS Supports, Rods, Angles, Flanges, Bracing, Rubber Gaskets, Wooden frames, Canvas Connections, etc. as per drawings and specifications. | Supply, Fabrication, Testing, and Commissioning of Factory Fabricated GI Sheet Metal 120GSM Rectangular boxed ducting, Plenums, Cowls, Elbows with turning vanes, Splitters, Reducers, Flanges, Collars etc as per IS 655 and installation as per SMACNA standards, The complete ducting shall be provided with MS Supports, Rods, Angles, Flanges, Bracing, Rubber Gaskets, Wooden frames, Canvas Connections, etc. as per drawings and specifications.
95 |  | GI Sheet Makes Tata, Jindal, SAIL, Ispat | GI Sheet Makes Tata, Jindal, SAIL, Ispat
96 |  | Make Rola Star, Zeco Ductofab | Make Rola Star, Zeco Ductofab
97 |  | 22 Gauge GI Sheet Metal Duct (751-1500mm) | 22 Gauge GI Sheet Metal Duct (751-1500mm) | Sq.mtr | 10 | 13400 | 1450 | 14500 | 1340 | 13400 | 1750 | 17500 | 1700 | 17000
98 |  | 24 Gauge GI Sheet Metal Duct (0-750mm) | 24 Gauge GI Sheet Metal Duct (0-750mm) | Sq.mtr | 75 | 93000 | 1250 | 93750 | 1240 | 93000 | 1450 | 108750 | 1550 | 116250
99 | 4.2 | EXTRUDED ALUMINIUM CEILING GRILLES | EXTRUDED ALUMINIUM CEILING GRILLES
100 |  | Supply, Installation, Testing and Balancing of Powder coated aluminium grilles complete with removable inner core as per approved shop drawing and specifications. The area of grille can be of any geometrical shape (Square rectangular Linear). The grilles shall be with 15 30 45° deflections as per requirement. The Colour shall be decided and approved by client and architect. | Supply, Installation, Testing and Balancing of Powder coated aluminium grilles complete with removable inner core as per approved shop drawing and specifications. The area of grille can be of any geometrical shape (Square rectangular Linear). The grilles shall be with 15 30 45° deflections as per requirement. The Colour shall be decided and approved by client and architect.
101 |  | Make Cosmos, Air Master System Air | Make Cosmos, Air Master System Air
102 |  | Square Rectangular Linear | Square Rectangular Linear | Sq.mtr | 4 | 15200 | 8500 | 34000 | 7850 | 31400 | 3800 | 15200 | 11700 | 46800
103 | 4.3 | OPPOSED BLADE DAMPER | OPPOSED BLADE DAMPER
104 |  | SITC of Aluminium Opposed blade dampers black powder coated vertical blades type for supply air collar. The damper should be gear operated type. | SITC of Aluminium Opposed blade dampers black powder coated vertical blades type for supply air collar. The damper should be gear operated type. | Sq.mtr | 12 | 43800 | 5500 | 66000 | 3650 | 43800 | 9500 | 114000 | 8200 | 98400
105 |  | Make Cosmos, Air Master System Air | Make Cosmos, Air Master System Air
106 | 4.6 | MULTI LEAF VOLUME CONTROL DAMPER | MULTI LEAF VOLUME CONTROL DAMPER
107 |  | SITC of multiblade box type galvanised steel sheet volume control dampers for ducts to be provided with suitable links, levers and quadrants for manual control of volume of air flow and for proper balancing of the air distribution system as per the approved shop drawings and specifications. | SITC of multiblade box type galvanised steel sheet volume control dampers for ducts to be provided with suitable links, levers and quadrants for manual control of volume of air flow and for proper balancing of the air distribution system as per the approved shop drawings and specifications. | Sq.mtr | 5 | 31250 | 9500 | 47500 | 6250 | 31250 | 12500 | 62500 | 9200 | 46000
108 |  | Make Carryaire System Air Dynacraft Air Master | Make Carryaire System Air Dynacraft Air Master
109 | 4.7 | EXTRUDED ALUMINIUM SQUARE AIR DIFFUSER | EXTRUDED ALUMINIUM SQUARE AIR DIFFUSER
110 |  | Supply, Installation, Testing and Balancing of Powder coated aluminium supply air square diffuser complete with removable inner core as per approved shop drawing and specifications. The diffuser shall also be provided with Black painted GI opposed blade damper (OBD) of required sizes. Each diffuser shall have double inlet rings to connect flexible ducts. The diffuser shall be suitable for gypsum grid ceiling. The Colour shall be decided and approved by client and architect. | Supply, Installation, Testing and Balancing of Powder coated aluminium supply air square diffuser complete with removable inner core as per approved shop drawing and specifications. The diffuser shall also be provided with Black painted GI opposed blade damper (OBD) of required sizes. Each diffuser shall have double inlet rings to connect flexible ducts. The diffuser shall be suitable for gypsum grid ceiling. The Colour shall be decided and approved by client and architect.
111 |  | Make Cosmos Ruskin Titus Air Master | Make Cosmos Ruskin Titus Air Master
112 |  | SQUARE DIFFUSER FOR GRID CEILING | SQUARE DIFFUSER FOR GRID CEILING
113 |  | Supply Air Diffuser with OBD - Neck Size 250x250mm | Supply Air Diffuser with OBD - Neck Size 250x250mm | Nos. | 4 | 10600 | 3000 | 12000 | 2650 | 10600 | 9500 | 38000 | 7800 | 31200
114 |  | Return Air Diffuser without OBD | Return Air Diffuser without OBD | Nos. | 4 | 8000 | 2000 | 8000 | 2450 | 9800 | 7500 | 30000 | 5700 | 22800
115 |  | SQUARE DIFFUSER FOR GYPSUM CEILING | SQUARE DIFFUSER FOR GYPSUM CEILING
116 |  | Supply Air Diffuser with OBD - Neck Size 250x250mm | Supply Air Diffuser with OBD - Neck Size 250x250mm | Nos. | 4 | 8200 | 3000 | 12000 | 2050 | 8200 | 11500 | 46000 | 7800 | 31200
117 |  | Return Air Diffuser without OBD | Return Air Diffuser without OBD | Nos. | 4 | 7400 | 2000 | 8000 | 1850 | 7400 | 10500 | 42000 | 5700 | 22800
118 | 4.8 | CANVAS CONNECTION | CANVAS CONNECTION
119 |  | Supply fixing of flexible Canvas connections between mouth piece and initial piece of ducting. Flexible connections shall be fire resistant made of closely woven, double layer canvass neoprene coated fibre glass. | Supply fixing of flexible Canvas connections between mouth piece and initial piece of ducting. Flexible connections shall be fire resistant made of closely woven, double layer canvass neoprene coated fibre glass.
120 |  | CHW AHU | CHW AHU | No. | 1 | 2000 | 2500 | 2500 | 2000 | 2000 | 4500 | 4500 | 4500 | 4500
121 |  | Cabinet Exhaust Fan | Cabinet Exhaust Fan | No. | 1 | 2250 | 2500 | 2500 | 2250 | 2250 | 4500 | 4500 | 4500 | 4500
122 |  | Cabinet Fresh Air Fan | Cabinet Fresh Air Fan | No. | 1 | 2250 | 2500 | 2500 | 2250 | 2250 | 4500 | 4500 | 4500 | 4500
123 |  | NOTES | NOTES
124 |  | The ducting support should be as per tender specification and additional supports are to be provided by Contractor as decided by Consultant. | The ducting support should be as per tender specification and additional supports are to be provided by Contractor as decided by Consultant.
125 |  | Muslin cloth cover for all air outlets during construction. | Muslin cloth cover for all air outlets during construction.
126 |  | Pressure testing of complete duct work as per DW SMACNA standard. | Pressure testing of complete duct work as per DW SMACNA standard.
127 |  | Silicon sealant for longitudinal transverse joints as per specification. | Silicon sealant for longitudinal transverse joints as per specification.
128 |  | Diffusers grilles shall be powder coated as per color approved by Architect. | Diffusers grilles shall be powder coated as per color approved by Architect.
129 |  | SUB-TOTAL | SUB-TOTAL
130 | 5 | THERMAL INSULATION | THERMAL INSULATION
131 | 5.1 | THERMAL INSULATION | THERMAL INSULATION
132 |  | Supply fixing of Thermal insulation for supply air duct using 19mm thick class O Closed cell nitrile rubber with anti-microbial coating on it. Insulation shall have Thermal conductivity of 0.033 W (m.K) and water vapor permeance of 0.10. Joints should be sealed with 50 mm wide 3 mm thick self adhesive tape. The duct shall be stick with recommended adhesive. | Supply fixing of Thermal insulation for supply air duct using 19mm thick class O Closed cell nitrile rubber with anti-microbial coating on it. Insulation shall have Thermal conductivity of 0.033 W (m.K) and water vapor permeance of 0.10. Joints should be sealed with 50 mm wide 3 mm thick self adhesive tape. The duct shall be stick with recommended adhesive. | Sq.mtr | 10 | 7500 | 750 | 7500 | 920 | 9200 | 1750 | 17500 | 900 | 9000
133 |  | Make Armaflex K-flex | Make Armaflex K-flex
134 | 5.2 | ACOUSTIC INSULATION | ACOUSTIC INSULATION
135 |  | Supply fixing acoustic insulation for ducting using Class 1 closed cell elastomeric insulation of 10mm thick Nitrile rubber insulation adhesive, longitudinal transverse joints sealed with adhesive in neat clean manner. Material shall be processed Nitrile Rubber foam with anti-microbial protection. Insulation shall have thermal conductivity of 0.047 W (m.K) and density of 140 - 180 kg m³. | Supply fixing acoustic insulation for ducting using Class 1 closed cell elastomeric insulation of 10mm thick Nitrile rubber insulation adhesive, longitudinal transverse joints sealed with adhesive in neat clean manner. Material shall be processed Nitrile Rubber foam with anti-microbial protection. Insulation shall have thermal conductivity of 0.047 W (m.K) and density of 140 - 180 kg m³. | Sq.mtr | 40 | 41200 | 1050 | 42000 | 1030 | 41200 | 1850 | 74000 | 1900 | 76000
136 |  | Make Armaflex K-flex | Make Armaflex K-flex
137 | 5.3 | THERMAL INSULATION FOR KITCHEN DUCTS | THERMAL INSULATION FOR KITCHEN DUCTS
138 |  | SITC of Glass Fibre Blanket Insulation material bonded with Thrmosetting Resin, with factory applied laminated aluminium foil of 22 micrns with fibre glass backing. Further, wire mesh along with 7 mil cloth shall be applied on above the insulation with proper adhersive. Nominal density 48 Kg CuM. Thermal conductivity, < 0.033 W m.K at 24 degC. All Insuation material and adhesives shall be as per Class I for surface spread and in accordance with BS 476, Class O for non-combustible grade. | SITC of Glass Fibre Blanket Insulation material bonded with Thrmosetting Resin, with factory applied laminated aluminium foil of 22 micrns with fibre glass backing. Further, wire mesh along with 7 mil cloth shall be applied on above the insulation with proper adhersive. Nominal density 48 Kg CuM. Thermal conductivity, < 0.033 W m.K at 24 degC. All Insuation material and adhesives shall be as per Class I for surface spread and in accordance with BS 476, Class O for non-combustible grade.
139 |  | Makes UP Twiga, Owens Corning, Supreme | Makes UP Twiga, Owens Corning, Supreme
140 |  | 25 mm Thick | 25 mm Thick | Sq.mtr | 30 | 21900 | 1050 | 31500 | 730 | 21900 | 2150 | 64500 | 1400 | 42000
141 |  | SUB-TOTAL | SUB-TOTAL
142 | 6 | ELECTRICAL WORKS | ELECTRICAL WORKS
143 | 6.1 | Power Cable | Power Cable
144 |  | Supply, handling, laying effecting proper connections testing and commissioning of following sizes of 1.1 KV grade XLPE insulated FRLS Aluminium Copper conductor cables laid over MS supports cable racks or fixing on walls including clamping the cable to supports in an approved manner as required complete with Copper earthing as specified for continuous earthing along with cable. All complete as required and as per final instruction as given by Owners Consultants and as per Technical specifications. Earthing shall be measured separately and shall be connected in two runs. Power to ELCB to be provided near each ODU by electrical contractor. | Supply, handling, laying effecting proper connections testing and commissioning of following sizes of 1.1 KV grade XLPE insulated FRLS Aluminium Copper conductor cables laid over MS supports cable racks or fixing on walls including clamping the cable to supports in an approved manner as required complete with Copper earthing as specified for continuous earthing along with cable. All complete as required and as per final instruction as given by Owners Consultants and as per Technical specifications. Earthing shall be measured separately and shall be connected in two runs. Power to ELCB to be provided near each ODU by electrical contractor.
145 |  | CU Armoured Cable for Suitable 2000 CFM AHU Fan, 3PH Fan | CU Armoured Cable for Suitable 2000 CFM AHU Fan, 3PH Fan | Rmt | 5 | 0 | 550 | 2750 | 250 | 1250 | 575 | 2875 | 0 | 0
146 |  | CU XLPE Cable for EX Fan, 1PH Fan with Industrial Top Plug | CU XLPE Cable for EX Fan, 1PH Fan with Industrial Top Plug | Rmt | 5 | 0 | 350 | 1750 | 350 | 1750 | 350 | 1750 | 0 | 0
147 |  | CU XLPE Cable for FA Fan, 1PH Fan with Industrial Top Plug | CU XLPE Cable for FA Fan, 1PH Fan with Industrial Top Plug | Rmt | 5 | 0 | 350 | 1750 | 350 | 1750 | 350 | 1750 | 0 | 0
148 |  | 8 SWG GI Earthing | 8 SWG GI Earthing | Rmt | 10 | 0 | 150 | 1500 | 100 | 1000 | 75 | 750 | 0 | 0
149 | 6.2 | CABLE TERMINATION | CABLE TERMINATION
150 |  | Supply Making of Cable termination of armoured unarmoured cables 1.1 KV grade including installation of cable glands, cable lugs (Aluminium for A2XFY copper for 2XFY YY Double compression type), heat shrinkable sleeves on long ends, crimping paste etc. The work includes testing commissioning of cables, meggaring values submitting reports of tests. (One set includes termination of all cores of one end only). All crimping tools dies shall be arranged by contractor. | Supply Making of Cable termination of armoured unarmoured cables 1.1 KV grade including installation of cable glands, cable lugs (Aluminium for A2XFY copper for 2XFY YY Double compression type), heat shrinkable sleeves on long ends, crimping paste etc. The work includes testing commissioning of cables, meggaring values submitting reports of tests. (One set includes termination of all cores of one end only). All crimping tools dies shall be arranged by contractor.
151 |  | CU Armoured Cable for Suitable 2000 CFM AHU Fan, 3PH Fan | CU Armoured Cable for Suitable 2000 CFM AHU Fan, 3PH Fan | Nos. | 2 | 0 | 550 | 1100 | 1500 | 3000 | 850 | 1700 | 0 | 0
152 | 6.3 | CABLE TRAYS | CABLE TRAYS
153 |  | Supplying Fixing of following sizes of GI cable tray duly painted perforated type of height 50mm along with necessary bends, reducers etc. anchored along the wall suspended from the ceiling with necessary MS supports. | Supplying Fixing of following sizes of GI cable tray duly painted perforated type of height 50mm along with necessary bends, reducers etc. anchored along the wall suspended from the ceiling with necessary MS supports.
154 |  | 50mm x 50mm x 1.6mm Thick | 50mm x 50mm x 1.6mm Thick | Rmt | 15 | 0 | 450 | 6750 | 350 | 5250 | 1050 | 15750 | 0 | 0
155 |  | 100mm wide x 50mm x 1.6mm Thick | 100mm wide x 50mm x 1.6mm Thick | Rmt | 5 | 0 | 650 | 3250 | 450 | 2250 | 1550 | 7750 | 0 | 0

## Technical Score Detail
|  | RFQ No: R0062 COST COMPARISON REPORT | RFQ No: R0062 COST COMPARISON REPORT | RFQ No: R0062 COST COMPARISON REPORT | Comp. Date : 15/01/2024 | Comp. Date : 15/01/2024 | Comp. Date : 15/01/2024 | Vendor Name : PIONEER PROJECT SOLUTION |  | Vendor Name : ANJLE MEP PROJECTS PVT LTD |  | Vendor Name : Pikture Perfect Design Studio Pvt. Ltd |  | Vendor Name : Mahamaya Engineering
|  | RFQ No: R0062 COST COMPARISON REPORT | RFQ No: R0062 COST COMPARISON REPORT | RFQ No: R0062 COST COMPARISON REPORT | RFQ #: R0062 | RFQ #: R0062 | RFQ #: R0062 | Contact Name : Mohd Ashraf |  | Contact Name : Priyanka/Premkant Rajpoot |  | Contact Name : Gangadhar Sharma |  | Contact Name : Yash Katoch
|  | RFQ No: R0062 COST COMPARISON REPORT | RFQ No: R0062 COST COMPARISON REPORT | RFQ No: R0062 COST COMPARISON REPORT | RFQ Date : 15/01/2024 20:21:52 | RFQ Date : 15/01/2024 20:21:52 | RFQ Date : 15/01/2024 20:21:52 | Vendor City : |  | Vendor City : |  | Vendor City : |  | Vendor City : Delhi
|  | RFQ No: R0062 COST COMPARISON REPORT | RFQ No: R0062 COST COMPARISON REPORT | RFQ No: R0062 COST COMPARISON REPORT | BCD Date : 15/01/2024 20:48:00 | BCD Date : 15/01/2024 20:48:00 | BCD Date : 15/01/2024 20:48:00 | Telephone # : |  | Telephone # : |  | Telephone # : |  | Telephone # :
|  | RFQ No: R0062 COST COMPARISON REPORT | RFQ No: R0062 COST COMPARISON REPORT | RFQ No: R0062 COST COMPARISON REPORT |  |  |  | Mobile # : |  | Mobile # : |  | Mobile # : |  | Mobile # : 9205300857
PR Number : TFSPL-2324-00122 | PR Number : TFSPL-2324-00122 | PR Number : TFSPL-2324-00122 | PR Number : TFSPL-2324-00122 | PR Number : TFSPL-2324-00122 | PR Number : TFSPL-2324-00122 | PR Number : TFSPL-2324-00122 | PR Number : TFSPL-2324-00122 | Email : projectspioneer@gmail.com |  | Email : anjlemepprojects@gmail.com |  | Email : piktureperfectdesignstudio@gmail.com |  | Email : mahamaya.engineering1@gmail.com
Package / RFQ Name : BOQ for HVAC for Delhi T1-Subway Outlet | Package / RFQ Name : BOQ for HVAC for Delhi T1-Subway Outlet | Package / RFQ Name : BOQ for HVAC for Delhi T1-Subway Outlet | Package / RFQ Name : BOQ for HVAC for Delhi T1-Subway Outlet | Package / RFQ Name : BOQ for HVAC for Delhi T1-Subway Outlet | Package / RFQ Name : BOQ for HVAC for Delhi T1-Subway Outlet | Package / RFQ Name : BOQ for HVAC for Delhi T1-Subway Outlet | Package / RFQ Name : BOQ for HVAC for Delhi T1-Subway Outlet | Round # : 3 (RFQ) |  | Round # : 3 (RFQ) |  | Round # : 3 (RFQ) |  | Round # : 3 (RFQ)
Buyer : Sarvesh Patil | Buyer : Sarvesh Patil | Buyer : Sarvesh Patil | Buyer : Sarvesh Patil | Buyer : Sarvesh Patil | Buyer : Sarvesh Patil | Buyer : Sarvesh Patil | Buyer : Sarvesh Patil | Quotation Date : |  | Quotation Date : |  | Quotation Date : |  | Quotation Date :
Comp. # : 3 | Comp. # : 3 | Comp. # : 3 | Comp. # : 3 | Comp. # : 3 | Currency :INR | Currency :INR | Currency :INR | Quotation Validity Date : |  | Quotation Validity Date : |  | Quotation Validity Date : |  | Quotation Validity Date :
Comp. # : 3 | Comp. # : 3 | Comp. # : 3 | Comp. # : 3 | Comp. # : 3 | BUDGET PRICE : | .00 |  | Quote Currency : |  | Quote Currency : |  | Quote Currency : |  | Quote Currency :
# | Item Code | Item Description | Last PO Details | Unit | Qty | Last PO Unit Rate | Last PO Total Value | Score | Justification | Score | Justification | Score | Justification | Score | Justification
1 |  | BOQ for HVAC for Delhi T1-Subway Outlet |  | NOS | 1.000 | 0.00 | 0.00
2 |  | Note |  |  | 0.000 | 0.00 | 0.00
3 |  | Prices shall be based on supply, installation, testing commissioning (SITC) at site including all taxes, duties, transportation insurance etc. |  |  | 0.000 | 0.00 | 0.00
4 | 1 | CHILLED WATER TYPE CEILING SUSPENDED AHU (AIR HANDLING UNIT) |  |  | 0.000 | 0.00 | 0.00
5 | 1.1 | CEILING SUSPENDED AHU |  |  | 0.000 | 0.00 | 0.00
6 |  | Supply and assembly of Ceiling Suspended Double skin cabinet type AHU Integrated (Air handling units) of following specifications |  |  | 0.000 | 0.00 | 0.00
7 |  | Frame Structure It shall consist of 48mm Extruded Aluminium with thermal break profile. |  |  | 0.000 | 0.00 | 0.00
8 |  | Panel 45mm + - 2mm thick double skin sandwich panels with rockwool insulation of density 64 kg m3 or PUF insulation of 48 kg m3 , The sheet thickness shall be minimum 0.6 mm for the outer skin precoated and 0.8 mm thickness for the inner skin of plain GI. |  |  | 0.000 | 0.00 | 0.00
9 |  | Mixing Box shall be provided wherever specified in the drawing. |  |  | 0.000 | 0.00 | 0.00
10 |  | Filtration Section It shall be provided with single stage washable type of prefilter MERV 8 first stage which shall be placed before coil section. |  |  | 0.000 | 0.00 | 0.00
11 |  | Coil Section Chilled water coil Multi row deep constructed with Aluminium fins of min 0.11mm thick 12 Fins per inch, and copper tubes of min 27 Guage thickness HYRDOPHYLLIC coated fins. Copper tube shall be min 12.5mm diameter. AHRI certified coil.The coil face area velocity shall not exceed 2.5m sec (500 fpm). |  |  | 0.000 | 0.00 | 0.00
12 |  | Drain Pan Condensate drain pan shall be fabricated from 18G SS 304 powder coated, insulated with 13 mm thick closed cell elastomeric(nitrile rubber) insulation. |  |  | 0.000 | 0.00 | 0.00
13 |  | Fan Section SISW DIDW Direct drive backward curved fan. The fan section shall be provided with limt switch for safety to shut off fan during Opening of access door. Fan outlet velocity not to exceed 1600 FPM. The sound level shall not be exceed more than 60dB @ 1m from the source. Vibration isolators, Door Limit switch, UV Lamp as per Technical Specifications, AHU Summary Sheet and drawings. Total static pressue has to calculated by Contractor as per the configuration. |  |  | 0.000 | 0.00 | 0.00
14 |  | Other Details AHU to house control box terminal box with Auto-Manual switch and incomer power terminal, with SPP, Over Undervoltage protection, shortcircuit protection and with no-nc contacts (potential free contact) to be provided for tripping on signal from Fire Dampers Fire Alarm Panel. Power cable from Terminal box to motor control cabling of required size upto the thermostat sensor etc. to be provided. Internal electrical and control wiring of AHU to be provided as factory fitted from AHU supplier. The cost shall include all necessary supports accessories required for installation. |  |  | 0.000 | 0.00 | 0.00
15 |  | Contractor shall design the chilled water coil according to the following conditions |  |  | 0.000 | 0.00 | 0.00
16 |  | a. Coil air entering temperature - 75.4°F DB |  |  | 0.000 | 0.00 | 0.00
17 |  | b. Coil air leaving temperature - 54 deg. F DB 52.99 deg. F WB |  |  | 0.000 | 0.00 | 0.00
18 |  | c. Chilled water temperature entering - 7.0 deg. C 44.6 deg. F |  |  | 0.000 | 0.00 | 0.00
19 |  | d. Chilled water temperature leaving - 12 deg. C 53.6 deg. F |  |  | 0.000 | 0.00 | 0.00
20 |  | Make VTS Zeco Citizen |  |  | 0.000 | 0.00 | 0.00
21 |  | Type Capacity Tonnage ESP No. of |  |  | 0.000 | 0.00 | 0.00
22 |  | (Cfm) TR (mm WG) Rows |  |  | 0.000 | 0.00 | 0.00
23 |  | CS AHU 2000 4.2 25 4 6 |  |  | 0.000 | 0.00 | 0.00
24 |  | GENERAL NOTES |  |  | 0.000 | 0.00 | 0.00
25 |  | LHS RHS VALVE station location to be confirmed. |  |  | 0.000 | 0.00 | 0.00
26 |  | Fan outlet velocity - 1600 FPM |  |  | 0.000 | 0.00 | 0.00
27 |  | Contractor shall submit static pressure calculation for all above units to Client Consultant. |  |  | 0.000 | 0.00 | 0.00
28 |  | Any change in motor HP shall be made at no extra cost to client. |  |  | 0.000 | 0.00 | 0.00
29 |  | Fan efficiency shall be minimum 75% |  |  | 0.000 | 0.00 | 0.00
30 |  | The cost shall be included liftting shifting of each equipment material with all necesaary arrnagement. Also, it shall be included the cost of scaffloding required for Installation of such material equipment. |  |  | 0.000 | 0.00 | 0.00
31 | 2 | CHILLED WATER PIPING WITH INSULATION |  |  | 0.000 | 0.00 | 0.00
32 | 2.1 | CHW PIPE |  |  | 0.000 | 0.00 | 0.00
33 |  | SITC of MS Heavy duty class C ERW Chilled Water pipe conforming to IS 1239 - 2004 primer painted including bends, tees, MS supports, PUFF saddles, anchor fasteners, steel angles and any other material required to complete the work. The piping flange connection bolts, washers and nuts should be hot dipped galvanised. Flourscent Plastic Sticker paint shall be applied to indicate Water flow directions. Only End flanges to be used for capping of pipes. Table E of BS code for flange thickness to be adhered. |  |  | 0.000 | 0.00 | 0.00
34 |  | Make Jindal Hissar TATA |  |  | 0.000 | 0.00 | 0.00
35 |  | F 32 mm |  | Rmt | 20.000 | 0.00 | 0.00
36 | 2.2 | CHILLED WATER PIPING INSULATION - INTERNAL USE |  |  | 0.000 | 0.00 | 0.00
37 |  | SITC of insulation for chilled water. piping. For internal pipe - Stick 25mm thick Nitrile rubber class O Closed cell nitrile rubber with anti-microbial coating on it. Insulation shall have Thermal conductivity of 0.033 W (m.K) and water vapor permeance of 0.10. Joints should be sealed with 50 mm wide 3 mm thick self adhesive tape and putting PVC bands at all supports. |  |  | 0.000 | 0.00 | 0.00
38 |  | Make Armaflex K-flex |  |  | 0.000 | 0.00 | 0.00
39 |  | F 32 mm |  | Rmt | 20.000 | 0.00 | 0.00
40 | 2.3 | BALL VALVE |  |  | 0.000 | 0.00 | 0.00
41 |  | SITC of following sizes of Ball Valve consist of Cap, Brass Body, Rated for 150 psi SWP, 600 psi WOG Pressure Two-piece construction; with brass body, regular port, B-16 chrome-plated ball and stem, replaceable “Teflon” or “TFE” seats and seals, blowout-proof stem, vinyl covered steel handle, threaded or soldered ends and extended stem for insulated piping. Same valve shall be used as a Drain valve. |  |  | 0.000 | 0.00 | 0.00
42 |  | Make Zoloto Audco Kitz |  |  | 0.000 | 0.00 | 0.00
43 |  | F 32 mm |  | Nos. | 3.000 | 0.00 | 0.00
44 | 2.4 | BALL VALVE WITH Y-STRAINER |  |  | 0.000 | 0.00 | 0.00
45 |  | SITC of following sizes of Brass Ball Valve with Y-Strainer consist of Cap, Brass Body, Rated for 150 psi SWP, 600 psi WOG Pressure Two-piece construction; with brass body, regular port, B-16 chrome-plated ball and stem, replaceable “Teflon” or “TFE” seats and seals, blowout-proof stem, vinyl covered steel handle, threaded or soldered ends and extended stem for insulated piping. Filter element shall be of non magnetic SS sheet with perforation. |  |  | 0.000 | 0.00 | 0.00
46 |  | Make Zoloto Audco Kitz |  |  | 0.000 | 0.00 | 0.00
47 |  | F 32 mm |  | No. | 1.000 | 0.00 | 0.00
48 | 2.5 | PIBCV VALVES |  |  | 0.000 | 0.00 | 0.00
49 |  | SITC of Pressure Independent Balancing cum Control Valves (PIBCV) including integrated motorised control valve and balancing device for combined flow and water balancing requirement. Valve body to be rated for PN 16. The valve design flow rate should be factory calibrated with + - 5% flow accuracy. Valve shall have necessary measuring ports, drain port, flanges etc., Valve shall also provide temperature sensor with necessary cabling (min 2mtr length to be considered with each valve). The balancing to be done through microprocessor based hand held terminal POT and the same results shall be furnished in the water balancing report as part of commissioning report and handing over manual. |  |  | 0.000 | 0.00 | 0.00
50 |  | Make Oventrop Siemens Danfoss |  |  | 0.000 | 0.00 | 0.00
51 |  | F 32 mm |  | No. | 1.000 | 0.00 | 0.00
52 | 2.6 | Auto Air Vent Valves |  |  | 0.000 | 0.00 | 0.00
53 |  | Make Anergy Flamco |  |  | 0.000 | 0.00 | 0.00
54 |  | Providing and fitting Auto Vent Valves. |  |  | 0.000 | 0.00 | 0.00
55 |  | SITC of Auto air vent in each risers common headers AHU. 3 4 auto vent valves at each coil riser header. |  | Nos. | 2.000 | 0.00 | 0.00
56 | 2.7 | SITC of Pressure gauges Thermometers |  |  | 0.000 | 0.00 | 0.00
57 |  | Make H Guru Waree |  |  | 0.000 | 0.00 | 0.00
58 |  | Necessary pressure gauges and thermometers 4 Dial type. |  |  | 0.000 | 0.00 | 0.00
59 |  | Water Pressure gauges 150mm dial complete with gauge valves, mounting, fittings and copper tubing extension wherever required. Pressure gauges Range 0-10 Kg CM2 |  | Nos. | 2.000 | 0.00 | 0.00
60 |  | Thermometers of the mercury in glass stem type and copper separable well complete with guard etc., of industrial grade mounting on water lines. Length 9 12 inches, Thermometer, Range 0-50 deg C |  | Nos. | 2.000 | 0.00 | 0.00
61 |  | Thermowells |  | Nos. | 4.000 | 0.00 | 0.00
62 |  | SITC of Brass Test Plug of industrial grade mounting on water |  | Nos. | 1.000 | 0.00 | 0.00
63 | 2.8 | INSULATED CONDENSATE DRAIN PIPE |  |  | 0.000 | 0.00 | 0.00
64 |  | SITC of UPVC pipes of following sizes for drain with necessary supports and fittings such as elbows, tees reducers etc. The insulation line to be insulated with nitrile rubber insulation of thickness 9mm and wrapped by weather proof protection tape. The Pipe wherever concealed should also have a parallel line as a standby arrangement in case of block of primary pipe . |  |  | 0.000 | 0.00 | 0.00
65 |  | Make Supreme, Prince, Astral |  |  | 0.000 | 0.00 | 0.00
66 |  | F 25 mm |  | Rmt | 10.000 | 0.00 | 0.00
67 |  | F 32 mm |  | Rmt | 2.000 | 0.00 | 0.00
68 |  | NOTES FOR PIPING |  |  | 0.000 | 0.00 | 0.00
69 |  | Cover all open pipe ends with muslin cloth during construction |  |  | 0.000 | 0.00 | 0.00
70 |  | Pipe cleaning chemical treatment as per specs shall be included in the piping cost. |  |  | 0.000 | 0.00 | 0.00
71 |  | Unit rates for all indicated sizes of pipes valves shall be furnished. |  |  | 0.000 | 0.00 | 0.00
72 |  | Cleaning Painting of pipe before insulation shall be included in piping cost. |  |  | 0.000 | 0.00 | 0.00
73 |  | The piping support should be as per tender specification and additional supports are to be provided Contractor as decided by Consultant. |  |  | 0.000 | 0.00 | 0.00
74 |  | All the valves shall be insulated with the same material as that of Chilled water pipng and cost of insulation for valves shall be considered. |  |  | 0.000 | 0.00 | 0.00
75 |  | SUB-TOTAL |  |  | 0.000 | 0.00 | 0.00
76 | 3 | VENTILATION SYSTEM |  |  | 0.000 | 0.00 | 0.00
77 | 3.1 | KITCHEN EXHAUST AIR FAN WITH WET SCRUBBER |  |  | 0.000 | 0.00 | 0.00
78 |  | SITC of Cabinet type Ventilation fan with Centrifugal Blower, Belt Direct Drive, Statically Dynamically Balanced, Backward Curved Impeller, Speed regulator, Dunlop Anti- Vibration Pads, etc. Motor should be TEFC squirrel cage, IP 55 rating with Class F Insulation, suitable for 3phase, 415volts, 50hz power supply. Sound level should be 65dB @ 3mtr distance. MERV 8 G4 pleated pre-filters should be made of 100% synthetic media to capture common airborne contaminants as per ASHRAE Standard 52.2. Fan shall be BMS compatible. Power will be provided 5 ft away from fan and necessary control wiring with plug will be provided by AC contractor.(Vendor to crosscheck static pressure calculation) |  |  | 0.000 | 0.00 | 0.00
79 |  | Make Kruger Nicotra Systems Air |  |  | 0.000 | 0.00 | 0.00
80 |  | EXHAUST FAN WITH OUT OF STREAM MOTOR |  |  | 0.000 | 0.00 | 0.00
81 |  | 650mm @ 25mm ESP |  | No | 1.000 | 0.00 | 0.00
82 |  | FRESH AIR FAN WITH MERV 8 |  |  | 0.000 | 0.00 | 0.00
83 |  | 500mm @ 25mm ESP |  | No | 1.000 | 0.00 | 0.00
84 |  | Note |  |  | 0.000 | 0.00 | 0.00
85 |  | Fan outlet velocity - 1600 FPM |  |  | 0.000 | 0.00 | 0.00
86 |  | All cabinet fans should have plenum section. |  |  | 0.000 | 0.00 | 0.00
87 |  | Fresh air fan should to have 6mm thick synthetic media washable filter with framework. |  |  | 0.000 | 0.00 | 0.00
88 |  | Contractor shall submit static pressure calculation for all above units to Client Consultant for their approval. Also, the total static drops across the systems shall cover the overall length from suction discharge to grille (inside the outlet). |  |  | 0.000 | 0.00 | 0.00
89 |  | Any change in motor HP or coil selection shall be made at no extra cost to client. |  |  | 0.000 | 0.00 | 0.00
90 |  | Fan efficiency shall be minimum 75% |  |  | 0.000 | 0.00 | 0.00
91 |  | The cost shall be included liftting shifting of each equipment material with all necesaary arrnagement. Also, it shall be included the cost of scaffloding required for Installation of such material equipment. |  |  | 0.000 | 0.00 | 0.00
92 |  | SUB-TOTAL |  |  | 0.000 | 0.00 | 0.00
93 | 4 | SHEET METAL WORKS |  |  | 0.000 | 0.00 | 0.00
94 | 4.1 | GI SHEET METAL DUCTING |  |  | 0.000 | 0.00 | 0.00
95 |  | Supply, Fabrication, Testing, and Commissioning of Factory Fabricated GI Sheet Metal 120GSM Rectangular boxed ducting, Plenums, Cowls, Elbows with turning vanes, Splitters, Reducers, Flanges, Collars etc as per IS 655 and installation as per SMACNA standards, The complete ducting shall be provided with MS Supports, Rods, Angles, Flanges, Bracing, Rubber Gaskets, Wooden frames, Canvas Connections, etc. as per drawings and specifications. |  |  | 0.000 | 0.00 | 0.00
96 |  | GI Sheet Makes Tata, Jindal, SAIL, Ispat |  |  | 0.000 | 0.00 | 0.00
97 |  | Make Rola Star, Zeco Ductofab |  |  | 0.000 | 0.00 | 0.00
98 |  | 22 Gauge GI Sheet Metal Duct (751-1500mm) |  | Sq.mtr | 10.000 | 0.00 | 0.00
99 |  | 24 Gauge GI Sheet Metal Duct (0-750mm) |  | Sq.mtr | 75.000 | 0.00 | 0.00
100 | 4.2 | EXTRUDED ALUMINIUM CEILING GRILLES |  |  | 0.000 | 0.00 | 0.00
101 |  | Supply, Installation, Testing and Balancing of Powder coated aluminium grilles complete with removable inner core as per approved shop drawing and specifications. The area of grille can be of any geometrical shape (Square rectangular Linear). The grilles shall be with 15 30 45° deflections as per requirement. The Colour shall be decided and approved by client and architect. |  |  | 0.000 | 0.00 | 0.00
102 |  | Make Cosmos, Air Master System Air |  |  | 0.000 | 0.00 | 0.00
103 |  | Square Rectangular Linear |  | Sq.mtr | 4.000 | 0.00 | 0.00
104 | 4.3 | OPPOSED BLADE DAMPER |  |  | 0.000 | 0.00 | 0.00
105 |  | SITC of Aluminium Opposed blade dampers black powder coated vertical blades type for supply air collar. The damper should be gear operated type. |  | Sq.mtr | 12.000 | 0.00 | 0.00
106 |  | Make Cosmos, Air Master System Air |  |  | 0.000 | 0.00 | 0.00
107 | 4.6 | MULTI LEAF VOLUME CONTROL DAMPER |  |  | 0.000 | 0.00 | 0.00
108 |  | SITC of multiblade box type galvanised steel sheet volume control dampers for ducts to be provided with suitable links, levers and quadrants for manual control of volume of air flow and for proper balancing of the air distribution system as per the approved shop drawings and specifications. |  | Sq.mtr | 5.000 | 0.00 | 0.00
109 |  | Make Carryaire System Air Dynacraft Air Master |  |  | 0.000 | 0.00 | 0.00
110 | 4.7 | EXTRUDED ALUMINIUM SQUARE AIR DIFFUSER |  |  | 0.000 | 0.00 | 0.00
111 |  | Supply, Installation, Testing and Balancing of Powder coated aluminium supply air square diffuser complete with removable inner core as per approved shop drawing and specifications. The diffuser shall also be provided with Black painted GI opposed blade damper (OBD) of required sizes. Each diffuser shall have double inlet rings to connect flexible ducts. The diffuser shall be suitable for gypsum grid ceiling. The Colour shall be decided and approved by client and architect. |  |  | 0.000 | 0.00 | 0.00
112 |  | Make Cosmos Ruskin Titus Air Master |  |  | 0.000 | 0.00 | 0.00
113 |  | SQUARE DIFFUSER FOR GRID CEILING |  |  | 0.000 | 0.00 | 0.00
114 |  | Supply Air Diffuser with OBD - Neck Size 250x250mm |  | Nos. | 4.000 | 0.00 | 0.00
115 |  | Return Air Diffuser without OBD |  | Nos. | 4.000 | 0.00 | 0.00
116 |  | SQUARE DIFFUSER FOR GYPSUM CEILING |  |  | 0.000 | 0.00 | 0.00
117 |  | Supply Air Diffuser with OBD - Neck Size 250x250mm |  | Nos. | 4.000 | 0.00 | 0.00
118 |  | Return Air Diffuser without OBD |  | Nos. | 4.000 | 0.00 | 0.00
119 | 4.8 | CANVAS CONNECTION |  |  | 0.000 | 0.00 | 0.00
120 |  | Supply fixing of flexible Canvas connections between mouth piece and initial piece of ducting. Flexible connections shall be fire resistant made of closely woven, double layer canvass neoprene coated fibre glass. |  |  | 0.000 | 0.00 | 0.00
121 |  | CHW AHU |  | No. | 1.000 | 0.00 | 0.00
122 |  | Cabinet Exhaust Fan |  | No. | 1.000 | 0.00 | 0.00
123 |  | Cabinet Fresh Air Fan |  | No. | 1.000 | 0.00 | 0.00
124 |  | NOTES |  |  | 0.000 | 0.00 | 0.00
125 |  | The ducting support should be as per tender specification and additional supports are to be provided by Contractor as decided by Consultant. |  |  | 0.000 | 0.00 | 0.00
126 |  | Muslin cloth cover for all air outlets during construction. |  |  | 0.000 | 0.00 | 0.00
127 |  | Pressure testing of complete duct work as per DW SMACNA standard. |  |  | 0.000 | 0.00 | 0.00
128 |  | Silicon sealant for longitudinal transverse joints as per specification. |  |  | 0.000 | 0.00 | 0.00
129 |  | Diffusers grilles shall be powder coated as per color approved by Architect. |  |  | 0.000 | 0.00 | 0.00
130 |  | SUB-TOTAL |  |  | 0.000 | 0.00 | 0.00
131 | 5 | THERMAL INSULATION |  |  | 0.000 | 0.00 | 0.00
132 | 5.1 | THERMAL INSULATION |  |  | 0.000 | 0.00 | 0.00
133 |  | Supply fixing of Thermal insulation for supply air duct using 19mm thick class O Closed cell nitrile rubber with anti-microbial coating on it. Insulation shall have Thermal conductivity of 0.033 W (m.K) and water vapor permeance of 0.10. Joints should be sealed with 50 mm wide 3 mm thick self adhesive tape. The duct shall be stick with recommended adhesive. |  | Sq.mtr | 10.000 | 0.00 | 0.00
134 |  | Make Armaflex K-flex |  |  | 0.000 | 0.00 | 0.00
135 | 5.2 | ACOUSTIC INSULATION |  |  | 0.000 | 0.00 | 0.00
136 |  | Supply fixing acoustic insulation for ducting using Class 1 closed cell elastomeric insulation of 10mm thick Nitrile rubber insulation adhesive, longitudinal transverse joints sealed with adhesive in neat clean manner. Material shall be processed Nitrile Rubber foam with anti-microbial protection. Insulation shall have thermal conductivity of 0.047 W (m.K) and density of 140 - 180 kg m³. |  | Sq.mtr | 40.000 | 0.00 | 0.00
137 |  | Make Armaflex K-flex |  |  | 0.000 | 0.00 | 0.00
138 | 5.3 | THERMAL INSULATION FOR KITCHEN DUCTS |  |  | 0.000 | 0.00 | 0.00
139 |  | SITC of Glass Fibre Blanket Insulation material bonded with Thrmosetting Resin, with factory applied laminated aluminium foil of 22 micrns with fibre glass backing. Further, wire mesh along with 7 mil cloth shall be applied on above the insulation with proper adhersive. Nominal density 48 Kg CuM. Thermal conductivity, < 0.033 W m.K at 24 degC. All Insuation material and adhesives shall be as per Class I for surface spread and in accordance with BS 476, Class O for non-combustible grade. |  |  | 0.000 | 0.00 | 0.00
140 |  | Makes UP Twiga, Owens Corning, Supreme |  |  | 0.000 | 0.00 | 0.00
141 |  | 25 mm Thick |  | Sq.mtr | 30.000 | 0.00 | 0.00
142 |  | SUB-TOTAL |  |  | 0.000 | 0.00 | 0.00
143 | 6 | ELECTRICAL WORKS |  |  | 0.000 | 0.00 | 0.00
144 | 6.1 | Power Cable |  |  | 0.000 | 0.00 | 0.00
145 |  | Supply, handling, laying effecting proper connections testing and commissioning of following sizes of 1.1 KV grade XLPE insulated FRLS Aluminium Copper conductor cables laid over MS supports cable racks or fixing on walls including clamping the cable to supports in an approved manner as required complete with Copper earthing as specified for continuous earthing along with cable. All complete as required and as per final instruction as given by Owners Consultants and as per Technical specifications. Earthing shall be measured separately and shall be connected in two runs. Power to ELCB to be provided near each ODU by electrical contractor. |  |  | 0.000 | 0.00 | 0.00
146 |  | CU Armoured Cable for Suitable 2000 CFM AHU Fan, 3PH Fan |  | Rmt | 5.000 | 0.00 | 0.00
147 |  | CU XLPE Cable for EX Fan, 1PH Fan with Industrial Top Plug |  | Rmt | 5.000 | 0.00 | 0.00
148 |  | CU XLPE Cable for FA Fan, 1PH Fan with Industrial Top Plug |  | Rmt | 5.000 | 0.00 | 0.00
149 |  | 8 SWG GI Earthing |  | Rmt | 10.000 | 0.00 | 0.00
150 | 6.2 | CABLE TERMINATION |  |  | 0.000 | 0.00 | 0.00
151 |  | Supply Making of Cable termination of armoured unarmoured cables 1.1 KV grade including installation of cable glands, cable lugs (Aluminium for A2XFY copper for 2XFY YY Double compression type), heat shrinkable sleeves on long ends, crimping paste etc. The work includes testing commissioning of cables, meggaring values submitting reports of tests. (One set includes termination of all cores of one end only). All crimping tools dies shall be arranged by contractor. |  |  | 0.000 | 0.00 | 0.00
152 |  | CU Armoured Cable for Suitable 2000 CFM AHU Fan, 3PH Fan |  | Nos. | 2.000 | 0.00 | 0.00
153 | 6.3 | CABLE TRAYS |  |  | 0.000 | 0.00 | 0.00
154 |  | Supplying Fixing of following sizes of GI cable tray duly painted perforated type of height 50mm along with necessary bends, reducers etc. anchored along the wall suspended from the ceiling with necessary MS supports. |  |  | 0.000 | 0.00 | 0.00
155 |  | 50mm x 50mm x 1.6mm Thick |  | Rmt | 15.000 | 0.00 | 0.00
156 |  | 100mm wide x 50mm x 1.6mm Thick |  | Rmt | 5.000 | 0.00 | 0.00