## Price Comparison (hidden)
|  | RFQ No: R1471 COST COMPARISON REPORT | RFQ No: R1471 COST COMPARISON REPORT | RFQ No: R1471 COST COMPARISON REPORT | Comp. Date : 12/08/2024 | Comp. Date : 12/08/2024 | Comp. Date : 12/08/2024 | Vendor Name : ARROW ELECTRICALS (RV232418724) | [15 empty] | Vendor Name : Electech Enterprises (RV232422514)
|  | RFQ No: R1471 COST COMPARISON REPORT | RFQ No: R1471 COST COMPARISON REPORT | RFQ No: R1471 COST COMPARISON REPORT | RFQ #: R1471 | RFQ #: R1471 | RFQ #: R1471 | Contact Name : SANTOSH KHAKE | [15 empty] | Contact Name : Alam
|  | RFQ No: R1471 COST COMPARISON REPORT | RFQ No: R1471 COST COMPARISON REPORT | RFQ No: R1471 COST COMPARISON REPORT | RFQ Date : 12/08/2024 12:31:59 | RFQ Date : 12/08/2024 12:31:59 | RFQ Date : 12/08/2024 12:31:59 | Vendor City : | [15 empty] | Vendor City :
|  | RFQ No: R1471 COST COMPARISON REPORT | RFQ No: R1471 COST COMPARISON REPORT | RFQ No: R1471 COST COMPARISON REPORT | BCD Date : | BCD Date : | BCD Date : | Telephone # : | [15 empty] | Telephone # :
|  | RFQ No: R1471 COST COMPARISON REPORT | RFQ No: R1471 COST COMPARISON REPORT | RFQ No: R1471 COST COMPARISON REPORT |  |  |  | Mobile # : | [15 empty] | Mobile # :
PR Number : BLR-2425-00075 | PR Number : BLR-2425-00075 | PR Number : BLR-2425-00075 | PR Number : BLR-2425-00075 | PR Number : BLR-2425-00075 | PR Number : BLR-2425-00075 | PR Number : BLR-2425-00075 | PR Number : BLR-2425-00075 | Email : project.arrowelectricals@gmail.com | [15 empty] | Email : alam@electechenterprises.net
Package / RFQ Name : TFAS / RFQ / BLR-2425-00075 | Package / RFQ Name : TFAS / RFQ / BLR-2425-00075 | Package / RFQ Name : TFAS / RFQ / BLR-2425-00075 | Package / RFQ Name : TFAS / RFQ / BLR-2425-00075 | Package / RFQ Name : TFAS / RFQ / BLR-2425-00075 | Package / RFQ Name : TFAS / RFQ / BLR-2425-00075 | Package / RFQ Name : TFAS / RFQ / BLR-2425-00075 | Package / RFQ Name : TFAS / RFQ / BLR-2425-00075 | Round # : 1 (RFQ) |  |  |  |  | Round # : 2 (RFQ) |  |  |  |  | Round # : 3 (Auction) | [5 empty] | Round # : 1 (RFQ) |  |  |  |  | Round # : 2 (RFQ) |  |  |  |  | Round # : 3 (Auction)
Buyer : Binu Balachandran / Technical : / Approver : | Buyer : Binu Balachandran / Technical : / Approver : | Buyer : Binu Balachandran / Technical : / Approver : | Buyer : Binu Balachandran / Technical : / Approver : | Buyer : Binu Balachandran / Technical : / Approver : | Buyer : Binu Balachandran / Technical : / Approver : | Buyer : Binu Balachandran / Technical : / Approver : | Buyer : Binu Balachandran / Technical : / Approver : | Quotation Date : |  | Quotation Validity Date : |  |  | Quotation Date : |  | Quotation Validity Date : |  |  | Quotation Date : |  |  | Quotation Validity Date : |  |  | Quotation Date : |  | Quotation Validity Date : |  |  | Quotation Date : |  | Quotation Validity Date : |  |  | Quotation Date : |  |  | Quotation Validity Date :
Comp. # : 3 | Comp. # : 3 | Comp. # : 3 | Comp. # : 3 | Comp. # : 3 | Currency :INR | Currency :INR | Currency :INR | Buyer Remark : |  |  |  |  | Buyer Remark : |  |  |  |  | Buyer Remark : Will be updated on detailed Po terms | [5 empty] | Buyer Remark : |  |  |  |  | Buyer Remark : |  |  |  |  | Buyer Remark :
Comp. # : 3 | Comp. # : 3 | Comp. # : 3 | Comp. # : 3 | Comp. # : 3 | BUDGET PRICE : | .00 |  | Quote Currency : INR |  |  |  |  | Quote Currency : INR |  |  |  |  | Quote Currency : INR | [5 empty] | Quote Currency : INR |  |  |  |  | Quote Currency : INR |  |  |  |  | Quote Currency : INR
# | Item Code | Item Description | Unit | Qty | Last PO Details | Lowest Unit Rate | Lowest Vendor | Price | Disc % | GST % | Unit Price | Total | Price | Disc % | GST % | Unit Price | Total | Price | Disc % | GST % | Technical | Unit Price | Total | Price | Disc % | GST % | Unit Price | Total | Price | Disc % | GST % | Unit Price | Total | Price | Disc % | GST % | Technical | Unit Price | Total
1 |  | Electrical | NOS | 1.00 |  | 7498335.00 | ARROW ELECTRICALS | 7581435.00 | 0.00 | 18.00 | 7,581,435.00 | 7,581,435.00 | 7581435.00 | 0.00 | 18.00 | 7,498,335.00 | 7,498,335.00 | 7581435.00 | 0.00 | 18.00 |  | 7,498,335.00 | 7,498,335.00 | 7982005.00 | 0.00 | 18.00 | 7,982,005.00 | 7,982,005.00 | 7982005.00 | 0.00 | 18.00 | 7,982,005.00 | 7,982,005.00 | 7982005.00 | 0.00 | 18.00 |  | 7,787,005.00 | 7,787,005.00
Item Total | [8 empty] | .00 | 1,364,658.30 |  | 7,581,435.00 |  | .00 | 1,349,700.30 |  | 7,498,335.00 |  | .00 | 1,349,700.30 |  |  | 7,498,335.00 |  | .00 | 1,436,760.90 |  | 7,982,005.00 |  | .00 | 1,436,760.90 |  | 7,982,005.00 |  | .00 | 1,401,660.90 |  |  | 7,787,005.00
Discount Total Value | [7 empty] | Grand Dis. Amt | .00 |  |  | .00 | Grand Dis. Amt | .00 |  |  | .00 | Grand Dis. Amt | .00 |  |  |  | .00 | Grand Dis. Amt | .00 |  |  | .00 | Grand Dis. Amt | .00 |  |  | .00 | Grand Dis. Amt | .00 |  |  |  | .00
GST Total Amount | [11 empty] | 1,364,658.30 |  |  |  |  | 1,349,700.30 | [5 empty] | 1,349,700.30 |  |  |  |  | 1,436,760.90 |  |  |  |  | 1,436,760.90 | [5 empty] | 1,401,660.90
Net Landed Cost | [10 empty] | INR | 8,946,093.30 |  |  |  | INR | 8,848,035.30 |  |  |  |  | INR | 8,848,035.30 |  |  |  | INR | 9,418,765.90 |  |  |  | INR | 9,418,765.90 |  |  |  |  | INR | 9,188,665.90
Vendor Status | [7 empty] | Round # : 1 (RFQ) | Round # : 1 (RFQ) | Round # : 2 (RFQ) | Round # : 2 (RFQ) | Round # : 3 (Auction) | Round # : 3 (Auction)
Sr No. | Vendor Code | Vendor Name | [5 empty] | Status | Remarks | Status | Remarks | Status | Remarks
1 | T054974 | UNITY ELECTRICAL | [5 empty] | Participate |  | Participate |  | Participate
2 | T054973 | EMPIRE FURNITURES | [5 empty] | Participate |  | Participate |  | Participate
3 | RV232422514 | Electech Enterprises | [5 empty] | Participate |  | Participate |  | Participate
4 | T054523 | Gold Fingers | [5 empty] | Participate |  | Participate |  | Participate
5 | T054976 | THE MAKERS | [5 empty] | Not Participate |  | Not Participate |  | Not Participate
6 | T054970 | DESIGNWORX | [5 empty] | Participate |  | Participate |  | Participate
7 | T054962 | HR INTERIORS | [5 empty] | Not Participate |  | Not Participate |  | Not Participate
8 | T054937 | INFINITY INTERIORS | [5 empty] | Not Participate |  | Not Participate |  | Not Participate
9 | T054520 | Bay Interior | [5 empty] | Participate |  | Participate |  | Participate
10 | T054485 | Keystone | [5 empty] | Not Participate |  | Not Participate |  | Not Participate
11 | RV232422609 | Pioneer Infra and Turnkey solutiom | [5 empty] | Participate |  | Participate |  | Participate
12 | T054359 | BGM interiors | [5 empty] | Participate |  | Participate |  | Participate
13 | T052019 | Trident | [5 empty] | Not Participate |  | Not Participate |  | Not Participate
14 | T051927 | Bay Interiors | [5 empty] | Participate |  | Participate |  | Participate
15 | T051926 | Keystone Solutions | [5 empty] | Not Participate |  | Not Participate |  | Not Participate
16 | T051606 | SM Infra | [5 empty] | Not Participate |  | Not Participate |  | Not Participate
17 | RV242523149 | INTER CARE ENTERPRISES | [5 empty] | Participate |  | Participate |  | Participate
18 | T055028 | AKHIL CHIRAG ELECTRICAL | [5 empty] | Participate |  | Participate |  | Participate
19 | T055027 | CRP CONTROL ENGINEERS | [5 empty] | Not Participate |  | Not Participate |  | Not Participate
20 | T054745 | NEO ELECTRICAL | [5 empty] | Not Participate |  | Not Participate |  | Not Participate
21 | RV242523197 | AD ASSOCIATES | [5 empty] | Participate |  | Participate |  | Participate
22 | T055026 | D B ELECTRICALS | [5 empty] | Not Participate |  | Not Participate |  | Not Participate
23 | T055097 | ALEX ELECTRICALS | [5 empty] | Not Participate |  | Not Participate |  | Not Participate
24 | RV232418724 | ARROW ELECTRICALS | [5 empty] | Participate |  | Participate |  | Participate
25 | RV232419010 | SHAH ENTERPRISES | [5 empty] | Participate |  | Participate |  | Participate

## BOQ Price Bid
|  | RFQ No: R1471 COST COMPARISON REPORT | Comp. Date : 12/08/2024 | Comp. Date : 12/08/2024 | Comp. Date : 12/08/2024 | Vendor Name : ARROW ELECTRICALS | Vendor Name : ARROW ELECTRICALS | Vendor Name : Electech Enterprises | Vendor Name : Electech Enterprises
|  | RFQ No: R1471 COST COMPARISON REPORT | RFQ #: R1471 | RFQ #: R1471 | RFQ #: R1471 | Contact Name : SANTOSH KHAKE | Contact Name : SANTOSH KHAKE | Contact Name : Alam | Contact Name : Alam
|  | RFQ No: R1471 COST COMPARISON REPORT | RFQ Date : 12/08/2024 12:31:59 | RFQ Date : 12/08/2024 12:31:59 | RFQ Date : 12/08/2024 12:31:59 | Vendor City : | Vendor City : | Vendor City : | Vendor City :
|  | RFQ No: R1471 COST COMPARISON REPORT | BCD Date : | BCD Date : | BCD Date : | Telephone # : | Telephone # : | Telephone # : | Telephone # :
|  | RFQ No: R1471 COST COMPARISON REPORT |  |  |  | Mobile # : | Mobile # : | Mobile # : | Mobile # :
PR Number : BLR-2425-00075 | PR Number : BLR-2425-00075 | PR Number : BLR-2425-00075 | PR Number : BLR-2425-00075 | PR Number : BLR-2425-00075 | PR Number : BLR-2425-00075 | Email : project.arrowelectricals@gmail.com | Email : project.arrowelectricals@gmail.com | Email : alam@electechenterprises.net | Email : alam@electechenterprises.net
Package / RFQ Name : TFAS / RFQ / BLR-2425-00075 | Package / RFQ Name : TFAS / RFQ / BLR-2425-00075 | Package / RFQ Name : TFAS / RFQ / BLR-2425-00075 | Package / RFQ Name : TFAS / RFQ / BLR-2425-00075 | Package / RFQ Name : TFAS / RFQ / BLR-2425-00075 | Package / RFQ Name : TFAS / RFQ / BLR-2425-00075 | Round # : 3 (Auction) | Round # : 3 (Auction) | Round # : 3 (Auction) | Round # : 3 (Auction)
Buyer : Binu Balachandran | Buyer : Binu Balachandran | Buyer : Binu Balachandran | Buyer : Binu Balachandran | Buyer : Binu Balachandran | Buyer : Binu Balachandran | Techanical Score : | Techanical Score : | Techanical Score : | Techanical Score :
Comp. # : 3 | Comp. # : 3 | Comp. # : 3 | Currency :INR | Currency :INR | Currency :INR | Quotation Date : | Quotation Date : | Quotation Date : | Quotation Date :
Comp. # : 3 | Comp. # : 3 | Comp. # : 3 | BUDGET PRICE :.00 | BUDGET PRICE :.00 | BUDGET PRICE :.00 | Quotation Validity Date : | Quotation Validity Date : | Quotation Validity Date : | Quotation Validity Date :
Sr No. | Item Code | Item Description | UOM | Qty | Minimum Amount | Unit Price | Amount | Unit Price | Amount
1 |  | Electrical | NOS | 1 |  |  | 7498335 |  | 7787005
1 | I | PANEL SWITCHGEAR
2 | 1 | Supply, installation, testing commissioning of free standing, floor mounting compartmentalized panels fabricated out of CRCA sheet steel sections after carrying out 7 tank cleaning process and duly powder coated using Siemens Grey Shade No. RAL 7032. The frame structure, doors and gland plates shall have 2.0 mm thick sheets and partitions shall be with 1.6 mm thick CRCA sheet. Base channel size 75 x 40 x 6 mm of ISMC shall be provided. The panel shall be dust and vermin proof with neoprene gasket. The doors shall be provided with concealed hinges and with brazing wherever required to avoid deformation and shall be earthed. The bus bar shall be of tinned Copper with epoxy supports and shall be insulated with colour coded heat shrink sleeves. The control wiring min. 2.5 Sq.mm shall be FRLS type. The Panel shall be provided with CTs, phase indication lamps, meters, relays and all switchgear, etc. as per the SLD. The panel shall be complete in all aspects as per the final approval of the Consultant.
3 |  | Special Note Both the main panels of zone-1 2 shall be provided with CQRS (Ceasefire Quick Response System with 2 kg FM-200 gas flooding system complete with sensors located in the panels. Make - Ceasefire Kalpex Eqv.
4 | A | Providing installing MAIN PANEL (ZONE-1) as per SLD Spec. | Set | 1 | 620000 | 651800 | 651800 | 620000 | 620000
5 |  | 100 Amps 4 pole, 25kA MCCB as a Incomer with MP based LSIG protection, Conserv make (or eqv.) EM6400 Energy manager with 4A SP MCB with 100 5A-3 Nos., 10VA, CL-1 CT s for metering AE make and indicating lamps for RYB and on-off-trip etc. for detail refer the SLD.
6 |  | Busbar chamber - 1 set, 4 pole 200A Tinned AL. Busbar with necessary
7 |  | OUTGOINGS
8 |  | i) 63A 4P MCCB with electromagnetic LSIG protections– 3 Nos.
9 |  | ii.) 40A 4P MCCB with electromagnetic LSIG protections – 4 Nos.
10 |  | iii.) 32A 4P MCCB with electromagnetic LSIG protections – 1 Nos.
11 |  | iv) 32A 4P ELMCB with 30 mA sensitivity – 1 Nos.
12 |  | v.) 32A 2P MCCB with electromagnetic LSIG protections – 1 Nos.
13 |  | vi.) DOL stsrters, 1.1 kW as indicated in the SLD and with a provision to connect a Start-Stop push button station from remote. - 2 Nos.
14 |  | vii.) DOL stsrters, 5.5 kW as indicated in the SLD and with a provision to connect Start-Stop push button station from remote. - 1 Nos.
15 | B | Providing installing MAIN PANEL (ZONE-2) as per SLD Spec. | Set | 1 | 604700 | 604700 | 604700 | 685000 | 685000
16 |  | 320 Amps 4 pole, 25kA MCCB as a Incomer with MP based LSIG protection, Conserv make (or eqv.) EM6400 Energy manager with 4A SP MCB for control circuit with 320 5A-3 Nos., 10VA, CL-1 CT s for metering AE make and indicating lamps for RYB and on-off-trip etc. for detail refer the SLD.
17 |  | Busbar chamber - 1 set, 4 pole 400A Tinned AL. Busbar with necessary supports etc.
18 |  | OUTGOINGS
19 |  | i) 100A 4P MCCB with electromagnetic LSIG protections– 1 Nos.
20 |  | i) 63A 4P MCCB with electromagnetic LSIG protections– 5 Nos.
21 |  | ii.) 40A 4P MCCB with electromagnetic LSIG protections – 1 Nos.
22 |  | iii.) 32A 4P MCCB with electromagnetic LSIG protections – 1 Nos.
23 |  | iv) 63A 4P ELMCB with 30 mA sensitivity – 1 Nos.
24 |  | iv) 32A 4P ELMCB with 30 mA sensitivity – 1 Nos.
25 |  | vi) 25A 4P ELMCB with 30 mA sensitivity – 1 Nos.
26 |  | vii) 16A 4P ELMCB with 30 mA sensitivity – 1 Nos.
27 |  | viii.) DOL stsrters, 0.75 kW as indicated in the SLD and with a provision to connect a Stsrt-Stop push button station from remote. - 1 Nos.
28 |  | ix.) DOL stsrters, 1.1 kW as indicated in the SLD and with a provision to connect a Stsrt-Stop push button station from remote. - 2 Nos.
29 |  | vii.) DOL stsrters, 5.5 kW as indicated in the SLD and with a provision to connect a Stsrt-Stop push button station from remote. - 1 Nos.
30 | 1 | Supply, installation, testing commissioning of Switchgears. (Standard Product)
31 | a | 100 amps 4P MCCB with thermal magnetic releases in FRP enclosure, IP-65, complete with all mounting accessories – for 34 TR VRF ODU | Nos. | 1 | 22500 | 22500 | 22500 | 25000 | 25000
32 | b | 32 amps 4P MCB C TYPE in FRP enclosure, IP-65, complete with all mounting accessories – for 3.5 TR DX ODU. | Nos. | 1 | 4500 | 12500 | 12500 | 4500 | 4500
33 | d | 63 amps 4P MCB with 63A 5 Pin Industrial Socket complete with all mounting accessories (for induction cook top) | Nos. | 1 | 12000 | 14500 | 14500 | 12000 | 12000
34 | e | 32 amps 4P MCB with 32A 5 Pin Industrial Socket complete with all mounting accessories (for Pasta Cooker Electric Fry Top) | Nos. | 2 | 21000 | 13500 | 27000 | 10500 | 21000
35 | II | UPS BATTERY
36 | 1 | Supply, Installation, testing and commissioning of 4.0 KVA UPS System with 1-Phase I C 1-Phase O G complete with 30 Minutes Battery Back-up and the required accessories as specified in the drawings the specifications. | Set | 1 | 95000 | 105000 | 105000 | 95000 | 95000
37 | III | DISTRIBUTION BOARDS
38 |  | Supply, installation, testing commissioning of Distribution Boards surface flush mounted with Double door containing MCB ELMCB as incomer and SPMCB as outgoing. All MCBs are of 10KA breaking capacity and ELMCBs RCCB should be of 30mA 100 MA sensivity. The DB shall have appropriate no. of top and bottom knock outs for outgoing circuits and shall be complete with necessary busbars, interconnection terminals and earth studs. All terminations in DB shall be complete with ferulling, dressing and all circuits shall be properly labeled with PVC strip (sticker type) having identification as per the final approval of Consultant. For UPS DB MCB shall be D type and other MCBs shall be C category for lighting and raw power DB LEGRAND HAGER SCHNEIDER.
39 | 1 | VTPN DB | Nos. | 0 | 0 | 24500 | 0 | 0 | 0
40 |  | 4 way TPN DB
41 |  | Incomer
42 |  | 63A 4P MCB 10kA – 1no.
43 |  | Outgoings 63 25 SP MCB, C Type – 4 Nos
44 | 2 | Lighting Distribution Board (LDB) | Nos. | 2 | 54000 | 27500 | 55000 | 27000 | 54000
45 |  | 8+2 way TPN PPI DB
46 |  | Incomer
47 |  | 32 40A 4P MCB 10kA – 1no.
48 |  | Subincomer
49 |  | 32A DP ELCB 30mA - 3 nos
50 |  | Outgoings 6 10 SP MCB, B Curve Type – 24 Nos
51 | 2 | Small Power Distribution Board (For small power and SPA) | Nos. | 3 | 78000 | 30500 | 91500 | 26000 | 78000
52 |  | 6+2 way TPN PPI DB
53 |  | Incomer
54 |  | 32 40A 4P MCB 10kA – 1no.
55 |  | Subincomer
56 |  | 40A DP ELCB 30mA - 3 nos
57 |  | Outgoings 10 16 20 SP MCB, C Type – 18 Nos
58 | 3 | Power Distribution Board (For Bar Office Store, Buffet Counter-1 2) | Nos. | 3 | 84000 | 32500 | 97500 | 28000 | 84000
59 |  | 8+2 way TPN PPI DB
60 |  | Incomer
61 |  | 63A 4P MCB 10kA – 1no.
62 |  | Subincomer
63 |  | 63A DP ELCB 30mA - 3 nos
64 |  | Outgoings 10 16 20 SP MCB, C Type – 24 Nos
65 | 4 | Power Distribution Board (For Beaverage Station and Sports Lounge) | Nos. | 1 | 26000 | 31500 | 31500 | 26000 | 26000
66 |  | 6+2 way TPN PPI DB
67 |  | Incomer
68 |  | 63A 4P MCB 10kA – 1no.
69 |  | Subincomer
70 |  | 63A DP ELCB 30mA - 3 nos
71 |  | Outgoings 10 16 20 SP MCB, C Type – 18 Nos
72 | 5 | UPS LDB | Nos. | 1 |  | 11000 | 11000 | 11000 | 11000
73 |  | 12 way SPN DB
74 |  | Incomer 25A DP MCB
75 |  | Outgoings 6 10A SP MCB, C Type – 8 Nos
76 |  | TOTAL FOR DISTRIBUTION BOARDS
77 | IV | CABLES ACCESSORIES
78 |  | Note Make a provision for suspenders as per site ceiling requirement.
79 |  | Supply installation of following armoured LT cables (XLPE insulated, Cu Al conductor, ST-2 rated inner FR PVC sheath and FRLS PVC outer sheath) rated for 1100 volts AC as per IS standard 1554 Part 1 and IS 7098, Part-1. with necessary M.S. clamps. All cables shall be properly clamped or tied when run on cable trays. All such cables shall be provided with temporary labelling at every 20 mtrs and ten finally with metal identification tags showing the size and the location from to the specific Panel DB at both ends.
80 | 4 | 4C x 16 Sq. mm CU. Armoured XLPE CABLE (For VRF ODU, PDB for Beverages Sports) | Mtr. | 125 | 124375 | 995 | 124375 | 1150 | 143750
81 | 5 | 4C x 10 Sq. mm CU. Armoured XLPE CABLE (for induction cook top, DBs, Buffet counter KPDB) | Mtr. | 135 | 105975 | 785 | 105975 | 950 | 128250
82 | 6 | 4C x 6 Sq. mm CU. armoured XLPE Cable (For electric fry top, SPA DB, SPA Geyser, LDB, small power DB etc) | Mtr. | 225 | 132750 | 590 | 132750 | 600 | 135000
83 | 7 | 4C x 4 Sq. mm CU. armoured XLPE Cable (For DX ODU, 20 TR CSU, Pasta Cooker, Induction WOK, Floor AHU etc,)) | Mtr. | 275 | 115500 | 462 | 127050 | 420 | 115500
84 | 8 | 4C x 2.5 Sq. mm CU. armoured XLPE Cable (Exhaust, FA fans, CSUs etc) | Mtr. | 250 | 62500 | 331 | 82750 | 250 | 62500
85 | 10 | 3C x 6 Sq. mm CU. Unarmoured XLPE Cable (For UPS I P and output upto the isolator) | Mtr. | 35 | 16975 | 485 | 16975 | 500 | 17500
86 | 13 | 3Rx1Cx6 Sq.mm YY FRLS Cable (Cu) (For UPS I P, O P from isolator) in flexible metallic conduit. | Mtr. | 35 | 11375 | 325 | 11375 | 400 | 14000
87 | B | Termination of following sizes of cables with Single compression cable gland.
88 | 1 | 3.5C x 185 Sq. mm AL. Armoured XLPE CABLE | Nos. | 2 | 2100 | 1850 | 3700 | 1050 | 2100
89 | 2 | 3.5C x 120 Sq. mm AL. Armoured XLPE CABLE | Nos. | 2 | 1600 | 1450 | 2900 | 800 | 1600
90 | 4 | 4C x 16 Sq. mm CU. Armoured XLPE CABLE (For VRF ODU, PDB for Beverages Sports) | Nos. | 6 | 2400 | 750 | 4500 | 400 | 2400
91 | 5 | 4C x 10 Sq. mm CU. Armoured XLPE CABLE (for induction cook top, DBs, Buffet counter KPDB) | Nos. | 8 | 3200 | 620 | 4960 | 400 | 3200
92 | 6 | 4C x 6 Sq. mm CU. armoured XLPE Cable (For electric fry top, SPA DB, SPA Geyser, LDB, small power DB etc) | Nos. | 8 | 2400 | 510 | 4080 | 300 | 2400
93 | 7 | 4C x 4 Sq. mm CU. armoured XLPE Cable (For DX ODU, 20 TR CSU, Pasta Cooker, Induction WOK, Floor AHU etc,)) | Nos. | 8 | 2400 | 410 | 3280 | 300 | 2400
94 | 8 | 4C x 2.5 Sq. mm CU. armoured XLPE Cable (Exhaust, FA fans, CSUs etc) | Nos. | 8 | 1600 | 250 | 2000 | 200 | 1600
95 | 9 | 3C x 4 Sq. mm CU. armoured XLPE Cable | Nos. | 8 | 1600 | 310 | 2480 | 200 | 1600
96 | 10 | 3C x 6 Sq. mm CU. Unarmoured XLPE Cable (For UPS I P and output upto the isolator) | Nos. | 4 | 1200 | 350 | 1400 | 300 | 1200
97 | 13 | 3Rx1Cx6 Sq.mm YY FRLS Cable (Cu) (For UPS I P, O P from isolator) in flexible metallic conduit. | Nos. | 6 |  | 250 | 1500 | 350 | 2100
98 |  | TOTAL FOR CABLES ACCESSORIES
99 | V | POINT WIRING ACCESSORIES
100 |  | Note Make a provision for suspenders as per site ceiling requirement.
101 | 1 | Wiring of circuit mains from DB to the switchboards or power points.
102 | a | 3RX2.5 sq.mm FR-LSH insulated multistrand copper conductor wires, 1.1 kV grade, in G.I. Conduits of 20 mm dia | Mtrs. | 1750 | 598500 | 342 | 598500 | 345 | 603750
103 | b | 2RX4 sq.mm + 1R X 2.5 sq. mm. FR-LSH insulated multistrand copper conductor wires, 1.1 kV grade in G.I. Conduits of 20 mm dia | Mtrs. | 2750 | 1058750 | 385 | 1058750 | 400 | 1100000
104 | 2 | SWITCH OPERATED LIGHT POINT WIRING
105 |  | Supply, installation, testing commissioning of point wiring for lights plug points bell point etc. in G.I. conduit of suitable diameter, surface or recessed mounted complete with junction box, joints, bends, switch box, cover plate etc. including 1.1kV grade 2 x 2.5+ 1 x 1.5 sq.mm. (Primary Points) Copper multi-stranded PVC insulated FRLS wires and 2 x 1.5 + 1 x 1.5 sq.mm. (Secondary Points) Copper multi-stranded PVC insulated FRLS wires, along with 6A modular surface recessed mounted switch, ceiling rose, connectors switch boxes etc. The work shall be completed with all material, labour, chiselling, making good surface etc. in cordination with civil agency complying with IE rules, regulations, standards local supply authority requirements. All G.I. conduit pipes, FRLS wires shall be considered) Note 1) The cost of Circuit Wiring from DB to switch board and switch board to switch board shall be covered by wiring of circuit mains
106 | a | Primary point | Each | 55 | 192500 | 3950 | 217250 | 3500 | 192500
107 | b | Secondary point | Each | 85 | 127500 | 2050 | 174250 | 1500 | 127500
108 | 3 | MCB OPERATED LIGHT POINT WIRING (DIRECT FROM LDB)
109 |  | Supply, installation, testing commissioning of point wiring for lights plug points bell point etc. in G.I. conduit of suitable diameter, surface or recessed mounted complete with junction box, joints, bends, switch box, cover plate etc. including 1.1kV grade 2 x 2.5+ 1 x 1.5 sq.mm. (Primary Points) Copper multi-stranded PVC insulated FRLS wires and 2 x 1.5 + 1 x 1.5 sq.mm. (Secondary Points) Copper multi-stranded PVC insulated FRLS wires, along with 6A modular surface recessed mounted switch, ceiling rose, connectors switch boxes etc. The work shall be completed with all material, labour, chiselling, making good surface etc. in cordination with civil agency complying with IE rules, regulations, standards local supply authority requirements. All G.I. conduit pipes, FRLS wires shall be considered) Note The first point shall be considered in running meters with 3X2.5 sq. mm wires. The loop poins shall be considered as secondary point shall be with 3X1.5 sq.mm wires with an average length of 10 metres.
110 | a | Primary point | Each | 35 | 136500 | 4250 | 148750 | 3900 | 136500
111 | b | Secondary point | Each | 77 | 138600 | 2400 | 184800 | 1800 | 138600
112 |  | POWER POINT WIRING
113 | 4 | Supplying, erecting , testing commissioning independent surface or recessed mounting modular 5A switch 5 15A sockesocket complete with switch box, internal wiring with required chiseling making good surface etc...in coordination with civil agency complying with IE rules, regulations, standards local supply authority requirements. as per final approval of Architect Consultant. (3X2.5 sq.mm wires for primary shall be multistrand copper conductor, FR-LSH type in G.I. conduit) Excluding of switch socket. (First power point shall be measure as per circuit mains wiring. The secondary is power point shall be about 5Mtr.
114 |  | Secondary point | Nos. | 35 | 64750 | 1850 | 64750 | 2500 | 87500
115 | 5 | Supplying, erecting , testing commissioning independent surface or recessed mounting modular 15A switch socket complete with switch box, internal wiring with required chiseling making good surface etc...in coordination with civil agency complying with IE rules, regulations, standards local supply authority requirements. as per final approval of Architect Consultant. (4sq.mm Wires shall be for primary FRLS type G.I. conduit ) Excluding of switch socket. (First power point shall be measure as per circuit mains wiring. The secondary is power point shall be about 5Mtr.
116 |  | Secondary point | Each | 30 | 65700 | 2190 | 65700 | 2500 | 75000
117 | 6 | Supply and installation of Perforated Cable Tray out of 14 gauge GI sheet complete with necessary fixing arrangement with Anchor Fastener and all other accessories as per the final approval of the Consultant Architect. Note Make a provision for suspenders as per site ceiling requirement.
118 | a | 450 x 50 x 2mm | Mtr. | 30 | 48000 | 1647 | 49410 | 1600 | 48000
119 | 7 | Supply and installation of AL raceway with 2 mm thickness proper ties clamps at appropriate intervals as per the route approved by Architect Consultant. (Cost of cutting the floor for laying of raceways to be included).
120 | a | 2 runs of underfloor AL raceways of size 100 x 40 mm (Type-A) | Mtr. | 47 | 39480 | 1850 | 86950 | 840 | 39480
121 | b | 1 runs of underfloor AL raceways of size 100 x 40 mm | Mtr. | 5 | 2100 | 920 | 4600 | 420 | 2100
122 | c | 1 runs of underfloor AL raceways of size 85 x 38 mm | Mtr. | 18 | 5760 | 790 | 14220 | 320 | 5760
123 | d | 1 runs of underfloor AL raceway of size 65 x 38 mm | Mtr. | 75 | 19500 | 655 | 49125 | 260 | 19500
124 | e | 2 runs of underfloor HMS grade uPVC Conduit Pipes 25 mm dia | Mtr. | 72 | 5040 | 230 | 16560 | 70 | 5040
125 | 8 | Supply installation of GI junction boxes with 2 mm thickness, 2mm thick SS cover with 2” extra on all sides SS cover on top and having screw fixed plates on all four sides with knock out holes for conduits. The plates shall be retained on the sidezs having no conduit or raceway so as to avoid the entry of any unwanted material. Earth stud to be provided for all Junction boxes for earthing. Junction box to be prepared as per the final approval of Architect Consultant. The junction boxes shall be protected from the entry of unwanted material till the completion of the project the SS plates shall be installed after the final polishing of flooring.
126 |  | Note
127 | a | 450 x 450 x 50 mm | Nos. | 5 | 8750 | 1750 | 8750 | 1800 | 9000
128 | b | 50 x 350 x 50 mm | Nos. | 5 | 6000 | 1550 | 7750 | 1200 | 6000
129 | c | 250 x 250 x 50 mm | Nos. | 25 |  | 1250 | 31250 | 1050 | 26250
130 | d | 150 x 150 x 50 mm | Nos. | 38 |  | 950 | 36100 | 900 | 34200
131 | e | Waterproofing of Junction Boxes in the planter box area by applying Sealing compound, NEER of Emerson make (or eqv.) | Nos. | 10 | 15000 | 1500 | 15000 | 5300 | 53000
132 | 9 | Supply, installation of temporary lighting power arrangement for construction purpose of with industrial type switch sockets MCB s ELCB s lighting fittings as required to finish the work for interior contractor necessary electrical protections throughout the site for construction work till the handover of site. Contractor shall maintain the saftey rules regulations as per Airport Security Department. The material shall be taken back by the contractor, also included scaffolded work at site during excution. | Job | 1 | 40000 | 40000 | 40000 | 85000 | 85000
133 | 10 | Supply, installation, testing commissioning of modular type flush mounted plate type switch and switch + sockets with hot dipped GI box complete as per the final approval of Architect Consultant
134 | a | 6A one way plate type switch | Nos. | 55 | 13200 | 240 | 13200 | 320 | 17600
135 | c | 6A 5pin switch socket outlet (Raw UPS power) + USB | Nos. | 36 | 64800 | 2195 | 79020 | 1800 | 64800
136 | c | 6 16A 5pin switch socket outlet (Raw UPS power) + USB | Nos. | 40 | 84000 | 2250 | 90000 | 2100 | 84000
137 | d | 2nos 6 16A 5pin switch socket outlet (Raw power) | Nos. | 18 | 23400 | 1350 | 24300 | 1300 | 23400
138 | e | 3 nos. 6 13A socket controlled by 1no 16A switch + USB | Nos. | 12 | 30000 | 3130 | 37560 | 2500 | 30000
139 | g | 1 nos. 16A socket controlled by 1nos 16A switch | Nos. | 6 | 4500 | 750 | 4500 | 800 | 4800
140 | h | RG6 coaxial TV outlet | Nos. | 12 | 6600 | 550 | 6600 | 600 | 7200
141 | 11 | Supply, installation, testing commissioning of industrial type plug and sockets conforming to IEC-60309 of Make-C S Legrand Havells or eqv.
142 | h | Industrial Socket, panel surface mounting type, IP-67, 63 Amps, 5-Pin, 3P+N+E, 415 V, 3-Ph, with 4-P MCB of 63A (For Induction Cook Top) | No. | 1 | 15000 | 16500 | 16500 | 15000 | 15000
143 | i | Industrial Socket, panel surface mounting type, IP-67, 32 Amps, 5-Pin, 3P+N+E, 415 V, 3-Ph with 4-P MCB of 32A. (For Pasta Cooker, Elect. Fry Top Induction WOK) | Nos. | 3 |  | 15500 | 46500 | 14000 | 42000
144 | j | Industrial Socket, panel surface mounting type, IP-67, 32 Amps, 3-Pin, 2P+E, 230 V, 1-Ph with 2-P MCB of 16 20 32A. (For Kitchen and Buffet Counter as required) | Nos. | 10 | 65000 | 6500 | 65000 | 9000 | 90000
145 | 12 | Supply installation of G.I. conduit with pull box junction box all accessories.
146 | 13 | Providing Television wiring inside 25mm dia GI conduit from each TV outlet to LV Shaft by using coaxial cable of type RG 6. Tinned copper conductor with necessary accessories viz. deep junction boxes, inspection boxes bends, termination etc. | RM | 450 | 99000 | 220 | 99000 | 230 | 103500
147 | 14 | SITC of following Splitter unit in Metal enclosure for Cable TV.
148 | 14.1 | 4 way Splitter | Nos. | 1 | 400 | 950 | 950 | 400 | 400
149 | 14.2 | 6 way Splitter | Nos. | 1 | 600 | 1100 | 1100 | 600 | 600
150 |  | TOTAL FOR WIRING ACCESSORIES
151 |  | EARTHING
152 | 1 | Supply erection of G.I. strip of 25 x 3 mm used for earthing of DBs, AHUs, ODUs etc. by laying on wall, cable trays with necessary clamps fixed on wall painted with bituminous paint in an approved manner. | Mtr. | 350 | 42000 | 205 | 71750 | 120 | 42000
153 | 2 | Supply erection of G.I. strip of 40 x 5 mm used for earthing of Main Panels by laying on wall, cable trays with necessary clamps fixed on wall painted with bituminous paint in an approved manner. | Mtr. | 450 | 112500 | 322 | 144900 | 250 | 112500
154 | 3 | 1 no. 4 sq. mm YY cable in 25mm G.I. conduit for earthing forUPS, networking and other ELV applications.etc | Mtr. | 250 | 13750 | 55 | 13750 | 60 | 15000
155 | 4 | Supplying erecting bare copper conductor of 8 swg for earthing purpose. As required. | Mtr. | 50 | 4000 | 110 | 5500 | 80 | 4000
156 | 5 | Supplying erecting bare GI conductor of 8 swg for earthing purpose | Mtr. | 125 | 4375 | 70 | 8750 | 35 | 4375
157 | 7 | SITC of Earthing terminal Box for distribution with 40X5 mm G.I. strip of 300 mm length. | Nos. | 1 | 3500 | 7500 | 7500 | 3500 | 3500
158 | 8 | SITC of Earthing terminal Box for distribution with 25X6 mm Copper strip of 300 mm length. | Nos. | 1 | 4500 | 9200 | 9200 | 4500 | 4500
159 |  | TOTAL FOR EARTHING
160 |  | MISCELLANEOUS
161 | 1 | Supply, fabrication and erection of M.S. Structural steel such as base mounting frames, brackets supports for installation of panels, cable tray etc.from M.S channel, angle, flats as per the requirement with painting of one coat of red oxide primer and two coats of approved shade of epoxy paint. | kgs. | 1500 | 217500 | 145 | 217500 | 180 | 270000
162 | 1 | Supply fixing of the best quality LT Danger Boards(415V) for of approved shape and size as specified by the local electrical authorities written in English, and local Language | Nos. | 2 | 700 | 350 | 700 | 500 | 1000
163 | 2 | Supply handed over to client of First Aid Box | Set | 2 | 4000 | 2500 | 5000 | 2000 | 4000
164 | 3 | Supply of 2M x 1M Rubber mat as per IS 15652 2006, 2mm thick, suitable upto 3.3 KV, fire retardant, no effect of acids, alkalies and transformer oils, moisture proof, high tensile strength and texture finish cloth impression (Anti slip, marking on top) . Make – DOZZ or equivalent | Nos. | 4 | 9000 | 2250 | 9000 | 3400 | 13600
165 |  | Supply fixing in position approved shock treatment chart written in English, Hindi and Gujarati. These charts shall be put in wooden frame covered with clear glass. | No. | 2 | 2500 | 1250 | 2500 | 2500 | 5000
166 |  | Fire Extinguisher 4.5 Kg (BCE Type). | No. | 2 | 9000 | 7500 | 15000 | 4500 | 9000
167 |  | Liaisoning with electrical inspector for necessary approvals of electrical installations. | LS | 1 | 10000 | 10000 | 10000 | 15000 | 15000
168 | II | PA MUSIC SYSTEM CONTAINMENT (BIAMP - 8600)
169 |  | Note The PA system shall be integrated with Fire Alarm System to activate evacuation message at preset loud volume in case of emergency
170 | 1 | Supply, Installation, Testing Commissioning of 6 Zone Controller (Make - BIAMP), Location - Reception | Nos. | 1 | 12600 | 12600 | 12600 | 30000 | 30000
171 | 2 | Supply, Installation, Testing Commissioning of 6W ceiling mount speaker. (Make - BIAMP) | Nos. | 30 | 39000 | 1850 | 55500 | 1300 | 39000
172 | 3 | Supply, Installation, Testing Commissioning of 12W Wall Mounted Speaker. (Make - BIAMP) | Nos. | 6 | 23100 | 3850 | 23100 | 4000 | 24000
173 | 4 | Supply, Installation, Testing Commissioningof 300W Booster amplifier with zone controller (BIAMP), Location - Reception | Nos. | 1 | 42500 | 42500 | 42500 | 50000 | 50000
174 | 5 | Audio Message Manager | No. | 1 | 5350 | 5350 | 5350 | 23000 | 23000
175 | 6 | Desk Microphone, (6-Zone Call Station), Location - Reception | No. | 1 | 6300 | 6300 | 6300 | 40000 | 40000
176 | 7 | Supply and laying of 2 Core Speaker Cable including 25mm G.I. conduit. | Mtr | 1250 | 290000 | 232 | 290000 | 260 | 325000
177 | 8 | Required connectors, jumper patch cables etc other accessories required. | Lot | 1 | 1800 | 11500 | 11500 | 1800 | 1800
178 | I | DATA, WIFI TELEPHONE SYSTEM
179 | 1 | Supplying,Installation,Testing and Commissioning of CAT 6 cable for Data connectivity pulled in G.I. conduit. | Rmt | 2150 | 473000 | 220 | 473000 | 350 | 752500
180 | 2 | Supplying,Installation,Testing and Commissioning of CAT 6 cable for Telephone Data connectivity pulled in Al raceways laid already. | Rmt | 1880 | 169200 | 90 | 169200 | 90 | 169200
181 | 3 | Supply, Installation of CAT 6 Information Outlet
182 | a | DATA OUTLET | Nos. | 48 | 26400 | 590 | 28320 | 550 | 26400
183 | b | WI-FI | Nos. | 10 | 5500 | 650 | 6500 | 550 | 5500
184 | c | CCTV | Nos. | 33 | 18150 | 650 | 21450 | 550 | 18150
185 | 4 | Supply, installation Configuration of Network Switch EX 4200, 24-port 10 100 1000BaseT (24 ports PoE+) with 1x930W AC PS PART NO. EX4200-24PX. | Nos | 2 | 0 | 0 | 0 | 0 | 0
186 | 5 | Supply, installation Configuration of Network Switch EX 4200, 48-port 10 100 1000BaseT (48 ports PoE+) with 1x930W AC PS PART NO. EX4200-48PX. | Nos. | 1 | 0 | 0 | 0 | 0 | 0
187 | 6 | Supply, installation of 27 U Wall Mount Rack with Std. Accessories required mounting Hardware ( WQ ) Black | Nos | 1 | 0 | 0 | 0 | 0 | 0
188 | 8 | Supply, installation of Dual band (5 GHz and 2.4 GHz concurrent) Mid – Range 802.11n Wireless Access Point + Power Adaptor + PoE Injector + Ceiling Mounting Kit. | Nos | 10 | 0 | 0 | 0 | 0 | 0
189 |  | Distributed Antenna System (DAS)
190 | 10 | SIGNAL MAP ANALYSIS TEST FOR MOBILE NETWORK Carry out tests for signal strength to plan DAS network. | LS | 1 | 0 | 0 | 0 | 0 | 0
191 | 10.1 | Supply, installation, testing and commissioning of Antenna points suitable for 4-Band coverage, low or medium power as shown in the layout. | Nos. | 8 | 0 | 0 | 0 | 0 | 0
192 | 10.2 | Supply, installation and termination of RG-6 coaxial cable in GI conduits of 25 mm dia | Mtrs. | 530 | 118720 | 224 | 118720 | 280 | 148400
193 | 10.3 | Termination and integration at the main existing DAS antenna point | LS | 1 | 0 | 0 | 0 | 0 | 0

## Technical Score Detail (hidden)
|  | RFQ No: R1471 COST COMPARISON REPORT | RFQ No: R1471 COST COMPARISON REPORT | RFQ No: R1471 COST COMPARISON REPORT | Comp. Date : 12/08/2024 | Comp. Date : 12/08/2024 | Comp. Date : 12/08/2024 | Vendor Name : ARROW ELECTRICALS | [5 empty] | Vendor Name : Electech Enterprises
|  | RFQ No: R1471 COST COMPARISON REPORT | RFQ No: R1471 COST COMPARISON REPORT | RFQ No: R1471 COST COMPARISON REPORT | RFQ #: R1471 | RFQ #: R1471 | RFQ #: R1471 | Contact Name : SANTOSH KHAKE | [5 empty] | Contact Name : Alam
|  | RFQ No: R1471 COST COMPARISON REPORT | RFQ No: R1471 COST COMPARISON REPORT | RFQ No: R1471 COST COMPARISON REPORT | RFQ Date : 12/08/2024 12:31:59 | RFQ Date : 12/08/2024 12:31:59 | RFQ Date : 12/08/2024 12:31:59 | Vendor City : | [5 empty] | Vendor City :
|  | RFQ No: R1471 COST COMPARISON REPORT | RFQ No: R1471 COST COMPARISON REPORT | RFQ No: R1471 COST COMPARISON REPORT | BCD Date : | BCD Date : | BCD Date : | Telephone # : | [5 empty] | Telephone # :
|  | RFQ No: R1471 COST COMPARISON REPORT | RFQ No: R1471 COST COMPARISON REPORT | RFQ No: R1471 COST COMPARISON REPORT |  |  |  | Mobile # : | [5 empty] | Mobile # :
PR Number : BLR-2425-00075 | PR Number : BLR-2425-00075 | PR Number : BLR-2425-00075 | PR Number : BLR-2425-00075 | PR Number : BLR-2425-00075 | PR Number : BLR-2425-00075 | PR Number : BLR-2425-00075 | PR Number : BLR-2425-00075 | Email : project.arrowelectricals@gmail.com | [5 empty] | Email : alam@electechenterprises.net
Package / RFQ Name : TFAS / RFQ / BLR-2425-00075 | Package / RFQ Name : TFAS / RFQ / BLR-2425-00075 | Package / RFQ Name : TFAS / RFQ / BLR-2425-00075 | Package / RFQ Name : TFAS / RFQ / BLR-2425-00075 | Package / RFQ Name : TFAS / RFQ / BLR-2425-00075 | Package / RFQ Name : TFAS / RFQ / BLR-2425-00075 | Package / RFQ Name : TFAS / RFQ / BLR-2425-00075 | Package / RFQ Name : TFAS / RFQ / BLR-2425-00075 | Round # : 1 (RFQ) |  | Round # : 2 (RFQ) |  | Round # : 3 (Auction) |  | Round # : 1 (RFQ) |  | Round # : 2 (RFQ) |  | Round # : 3 (Auction)
Buyer : Binu Balachandran | Buyer : Binu Balachandran | Buyer : Binu Balachandran | Buyer : Binu Balachandran | Buyer : Binu Balachandran | Buyer : Binu Balachandran | Buyer : Binu Balachandran | Buyer : Binu Balachandran | Quotation Date : |  | Quotation Date : |  | Quotation Date : |  | Quotation Date : |  | Quotation Date : |  | Quotation Date :
Comp. # : 3 | Comp. # : 3 | Comp. # : 3 | Comp. # : 3 | Comp. # : 3 | Currency :INR | Currency :INR | Currency :INR | Quotation Validity Date : |  | Quotation Validity Date : |  | Quotation Validity Date : |  | Quotation Validity Date : |  | Quotation Validity Date : |  | Quotation Validity Date :
Comp. # : 3 | Comp. # : 3 | Comp. # : 3 | Comp. # : 3 | Comp. # : 3 | BUDGET PRICE : | .00 |  | Quote Currency : |  | Quote Currency : |  | Quote Currency : |  | Quote Currency : |  | Quote Currency : |  | Quote Currency :
# | Item Code | Item Description | Last PO Details | Unit | Qty | Last PO Unit Rate | Last PO Total Value | Score | Justification | Score | Justification | Score | Justification | Score | Justification | Score | Justification | Score | Justification
1 |  | Electrical |  | NOS | 1.000 | 0.00 | 0.00
2 | I | PANEL SWITCHGEAR |  |  | 0.000 | 0.00 | 0.00
3 | 1 | Supply, installation, testing commissioning of free standing, floor mounting compartmentalized panels fabricated out of CRCA sheet steel sections after carrying out 7 tank cleaning process and duly powder coated using Siemens Grey Shade No. RAL 7032. The frame structure, doors and gland plates shall have 2.0 mm thick sheets and partitions shall be with 1.6 mm thick CRCA sheet. Base channel size 75 x 40 x 6 mm of ISMC shall be provided. The panel shall be dust and vermin proof with neoprene gasket. The doors shall be provided with concealed hinges and with brazing wherever required to avoid deformation and shall be earthed. The bus bar shall be of tinned Copper with epoxy supports and shall be insulated with colour coded heat shrink sleeves. The control wiring min. 2.5 Sq.mm shall be FRLS type. The Panel shall be provided with CTs, phase indication lamps, meters, relays and all switchgear, etc. as per the SLD. The panel shall be complete in all aspects as per the final approval of the Consultant. |  |  | 0.000 | 0.00 | 0.00
4 |  | Special Note Both the main panels of zone-1 2 shall be provided with CQRS (Ceasefire Quick Response System with 2 kg FM-200 gas flooding system complete with sensors located in the panels. Make - Ceasefire Kalpex Eqv. |  |  | 0.000 | 0.00 | 0.00
5 | A | Providing installing MAIN PANEL (ZONE-1) as per SLD Spec. |  | Set | 1.000 | 0.00 | 0.00
6 |  | 100 Amps 4 pole, 25kA MCCB as a Incomer with MP based LSIG protection, Conserv make (or eqv.) EM6400 Energy manager with 4A SP MCB with 100 5A-3 Nos., 10VA, CL-1 CT s for metering AE make and indicating lamps for RYB and on-off-trip etc. for detail refer the SLD. |  |  | 0.000 | 0.00 | 0.00
7 |  | Busbar chamber - 1 set, 4 pole 200A Tinned AL. Busbar with necessary |  |  | 0.000 | 0.00 | 0.00
8 |  | OUTGOINGS |  |  | 0.000 | 0.00 | 0.00
9 |  | i) 63A 4P MCCB with electromagnetic LSIG protections– 3 Nos. |  |  | 0.000 | 0.00 | 0.00
10 |  | ii.) 40A 4P MCCB with electromagnetic LSIG protections – 4 Nos. |  |  | 0.000 | 0.00 | 0.00
11 |  | iii.) 32A 4P MCCB with electromagnetic LSIG protections – 1 Nos. |  |  | 0.000 | 0.00 | 0.00
12 |  | iv) 32A 4P ELMCB with 30 mA sensitivity – 1 Nos. |  |  | 0.000 | 0.00 | 0.00
13 |  | v.) 32A 2P MCCB with electromagnetic LSIG protections – 1 Nos. |  |  | 0.000 | 0.00 | 0.00
14 |  | vi.) DOL stsrters, 1.1 kW as indicated in the SLD and with a provision to connect a Start-Stop push button station from remote. - 2 Nos. |  |  | 0.000 | 0.00 | 0.00
15 |  | vii.) DOL stsrters, 5.5 kW as indicated in the SLD and with a provision to connect Start-Stop push button station from remote. - 1 Nos. |  |  | 0.000 | 0.00 | 0.00
16 | B | Providing installing MAIN PANEL (ZONE-2) as per SLD Spec. |  | Set | 1.000 | 0.00 | 0.00
17 |  | 320 Amps 4 pole, 25kA MCCB as a Incomer with MP based LSIG protection, Conserv make (or eqv.) EM6400 Energy manager with 4A SP MCB for control circuit with 320 5A-3 Nos., 10VA, CL-1 CT s for metering AE make and indicating lamps for RYB and on-off-trip etc. for detail refer the SLD. |  |  | 0.000 | 0.00 | 0.00
18 |  | Busbar chamber - 1 set, 4 pole 400A Tinned AL. Busbar with necessary supports etc. |  |  | 0.000 | 0.00 | 0.00
19 |  | OUTGOINGS |  |  | 0.000 | 0.00 | 0.00
20 |  | i) 100A 4P MCCB with electromagnetic LSIG protections– 1 Nos. |  |  | 0.000 | 0.00 | 0.00
21 |  | i) 63A 4P MCCB with electromagnetic LSIG protections– 5 Nos. |  |  | 0.000 | 0.00 | 0.00
22 |  | ii.) 40A 4P MCCB with electromagnetic LSIG protections – 1 Nos. |  |  | 0.000 | 0.00 | 0.00
23 |  | iii.) 32A 4P MCCB with electromagnetic LSIG protections – 1 Nos. |  |  | 0.000 | 0.00 | 0.00
24 |  | iv) 63A 4P ELMCB with 30 mA sensitivity – 1 Nos. |  |  | 0.000 | 0.00 | 0.00
25 |  | iv) 32A 4P ELMCB with 30 mA sensitivity – 1 Nos. |  |  | 0.000 | 0.00 | 0.00
26 |  | vi) 25A 4P ELMCB with 30 mA sensitivity – 1 Nos. |  |  | 0.000 | 0.00 | 0.00
27 |  | vii) 16A 4P ELMCB with 30 mA sensitivity – 1 Nos. |  |  | 0.000 | 0.00 | 0.00
28 |  | viii.) DOL stsrters, 0.75 kW as indicated in the SLD and with a provision to connect a Stsrt-Stop push button station from remote. - 1 Nos. |  |  | 0.000 | 0.00 | 0.00
29 |  | ix.) DOL stsrters, 1.1 kW as indicated in the SLD and with a provision to connect a Stsrt-Stop push button station from remote. - 2 Nos. |  |  | 0.000 | 0.00 | 0.00
30 |  | vii.) DOL stsrters, 5.5 kW as indicated in the SLD and with a provision to connect a Stsrt-Stop push button station from remote. - 1 Nos. |  |  | 0.000 | 0.00 | 0.00
31 | 1 | Supply, installation, testing commissioning of Switchgears. (Standard Product) |  |  | 0.000 | 0.00 | 0.00
32 | a | 100 amps 4P MCCB with thermal magnetic releases in FRP enclosure, IP-65, complete with all mounting accessories – for 34 TR VRF ODU |  | Nos. | 1.000 | 0.00 | 0.00
33 | b | 32 amps 4P MCB C TYPE in FRP enclosure, IP-65, complete with all mounting accessories – for 3.5 TR DX ODU. |  | Nos. | 1.000 | 0.00 | 0.00
34 | d | 63 amps 4P MCB with 63A 5 Pin Industrial Socket complete with all mounting accessories (for induction cook top) |  | Nos. | 1.000 | 0.00 | 0.00
35 | e | 32 amps 4P MCB with 32A 5 Pin Industrial Socket complete with all mounting accessories (for Pasta Cooker Electric Fry Top) |  | Nos. | 2.000 | 0.00 | 0.00
36 | II | UPS BATTERY |  |  | 0.000 | 0.00 | 0.00
37 | 1 | Supply, Installation, testing and commissioning of 4.0 KVA UPS System with 1-Phase I C 1-Phase O G complete with 30 Minutes Battery Back-up and the required accessories as specified in the drawings the specifications. |  | Set | 1.000 | 0.00 | 0.00
38 | III | DISTRIBUTION BOARDS |  |  | 0.000 | 0.00 | 0.00
39 |  | Supply, installation, testing commissioning of Distribution Boards surface flush mounted with Double door containing MCB ELMCB as incomer and SPMCB as outgoing. All MCBs are of 10KA breaking capacity and ELMCBs RCCB should be of 30mA 100 MA sensivity. The DB shall have appropriate no. of top and bottom knock outs for outgoing circuits and shall be complete with necessary busbars, interconnection terminals and earth studs. All terminations in DB shall be complete with ferulling, dressing and all circuits shall be properly labeled with PVC strip (sticker type) having identification as per the final approval of Consultant. For UPS DB MCB shall be D type and other MCBs shall be C category for lighting and raw power DB LEGRAND HAGER SCHNEIDER. |  |  | 0.000 | 0.00 | 0.00
40 | 1 | VTPN DB |  | Nos. | 0.000 | 0.00 | 0.00
41 |  | 4 way TPN DB |  |  | 0.000 | 0.00 | 0.00
42 |  | Incomer |  |  | 0.000 | 0.00 | 0.00
43 |  | 63A 4P MCB 10kA – 1no. |  |  | 0.000 | 0.00 | 0.00
44 |  | Outgoings 63 25 SP MCB, C Type – 4 Nos |  |  | 0.000 | 0.00 | 0.00
45 | 2 | Lighting Distribution Board (LDB) |  | Nos. | 2.000 | 0.00 | 0.00
46 |  | 8+2 way TPN PPI DB |  |  | 0.000 | 0.00 | 0.00
47 |  | Incomer |  |  | 0.000 | 0.00 | 0.00
48 |  | 32 40A 4P MCB 10kA – 1no. |  |  | 0.000 | 0.00 | 0.00
49 |  | Subincomer |  |  | 0.000 | 0.00 | 0.00
50 |  | 32A DP ELCB 30mA - 3 nos |  |  | 0.000 | 0.00 | 0.00
51 |  | Outgoings 6 10 SP MCB, B Curve Type – 24 Nos |  |  | 0.000 | 0.00 | 0.00
52 | 2 | Small Power Distribution Board (For small power and SPA) |  | Nos. | 3.000 | 0.00 | 0.00
53 |  | 6+2 way TPN PPI DB |  |  | 0.000 | 0.00 | 0.00
54 |  | Incomer |  |  | 0.000 | 0.00 | 0.00
55 |  | 32 40A 4P MCB 10kA – 1no. |  |  | 0.000 | 0.00 | 0.00
56 |  | Subincomer |  |  | 0.000 | 0.00 | 0.00
57 |  | 40A DP ELCB 30mA - 3 nos |  |  | 0.000 | 0.00 | 0.00
58 |  | Outgoings 10 16 20 SP MCB, C Type – 18 Nos |  |  | 0.000 | 0.00 | 0.00
59 | 3 | Power Distribution Board (For Bar Office Store, Buffet Counter-1 2) |  | Nos. | 3.000 | 0.00 | 0.00
60 |  | 8+2 way TPN PPI DB |  |  | 0.000 | 0.00 | 0.00
61 |  | Incomer |  |  | 0.000 | 0.00 | 0.00
62 |  | 63A 4P MCB 10kA – 1no. |  |  | 0.000 | 0.00 | 0.00
63 |  | Subincomer |  |  | 0.000 | 0.00 | 0.00
64 |  | 63A DP ELCB 30mA - 3 nos |  |  | 0.000 | 0.00 | 0.00
65 |  | Outgoings 10 16 20 SP MCB, C Type – 24 Nos |  |  | 0.000 | 0.00 | 0.00
66 | 4 | Power Distribution Board (For Beaverage Station and Sports Lounge) |  | Nos. | 1.000 | 0.00 | 0.00
67 |  | 6+2 way TPN PPI DB |  |  | 0.000 | 0.00 | 0.00
68 |  | Incomer |  |  | 0.000 | 0.00 | 0.00
69 |  | 63A 4P MCB 10kA – 1no. |  |  | 0.000 | 0.00 | 0.00
70 |  | Subincomer |  |  | 0.000 | 0.00 | 0.00
71 |  | 63A DP ELCB 30mA - 3 nos |  |  | 0.000 | 0.00 | 0.00
72 |  | Outgoings 10 16 20 SP MCB, C Type – 18 Nos |  |  | 0.000 | 0.00 | 0.00
73 | 5 | UPS LDB |  | Nos. | 1.000 | 0.00 | 0.00
74 |  | 12 way SPN DB |  |  | 0.000 | 0.00 | 0.00
75 |  | Incomer 25A DP MCB |  |  | 0.000 | 0.00 | 0.00
76 |  | Outgoings 6 10A SP MCB, C Type – 8 Nos |  |  | 0.000 | 0.00 | 0.00
77 |  | TOTAL FOR DISTRIBUTION BOARDS |  |  | 0.000 | 0.00 | 0.00
78 | IV | CABLES ACCESSORIES |  |  | 0.000 | 0.00 | 0.00
79 |  | Note Make a provision for suspenders as per site ceiling requirement. |  |  | 0.000 | 0.00 | 0.00
80 |  | Supply installation of following armoured LT cables (XLPE insulated, Cu Al conductor, ST-2 rated inner FR PVC sheath and FRLS PVC outer sheath) rated for 1100 volts AC as per IS standard 1554 Part 1 and IS 7098, Part-1. with necessary M.S. clamps. All cables shall be properly clamped or tied when run on cable trays. All such cables shall be provided with temporary labelling at every 20 mtrs and ten finally with metal identification tags showing the size and the location from to the specific Panel DB at both ends. |  |  | 0.000 | 0.00 | 0.00
81 | 4 | 4C x 16 Sq. mm CU. Armoured XLPE CABLE (For VRF ODU, PDB for Beverages Sports) |  | Mtr. | 125.000 | 0.00 | 0.00
82 | 5 | 4C x 10 Sq. mm CU. Armoured XLPE CABLE (for induction cook top, DBs, Buffet counter KPDB) |  | Mtr. | 135.000 | 0.00 | 0.00
83 | 6 | 4C x 6 Sq. mm CU. armoured XLPE Cable (For electric fry top, SPA DB, SPA Geyser, LDB, small power DB etc) |  | Mtr. | 225.000 | 0.00 | 0.00
84 | 7 | 4C x 4 Sq. mm CU. armoured XLPE Cable (For DX ODU, 20 TR CSU, Pasta Cooker, Induction WOK, Floor AHU etc,)) |  | Mtr. | 275.000 | 0.00 | 0.00
85 | 8 | 4C x 2.5 Sq. mm CU. armoured XLPE Cable (Exhaust, FA fans, CSUs etc) |  | Mtr. | 250.000 | 0.00 | 0.00
86 | 10 | 3C x 6 Sq. mm CU. Unarmoured XLPE Cable (For UPS I P and output upto the isolator) |  | Mtr. | 35.000 | 0.00 | 0.00
87 | 13 | 3Rx1Cx6 Sq.mm YY FRLS Cable (Cu) (For UPS I P, O P from isolator) in flexible metallic conduit. |  | Mtr. | 35.000 | 0.00 | 0.00
88 | B | Termination of following sizes of cables with Single compression cable gland. |  |  | 0.000 | 0.00 | 0.00
89 | 1 | 3.5C x 185 Sq. mm AL. Armoured XLPE CABLE |  | Nos. | 2.000 | 0.00 | 0.00
90 | 2 | 3.5C x 120 Sq. mm AL. Armoured XLPE CABLE |  | Nos. | 2.000 | 0.00 | 0.00
91 | 4 | 4C x 16 Sq. mm CU. Armoured XLPE CABLE (For VRF ODU, PDB for Beverages Sports) |  | Nos. | 6.000 | 0.00 | 0.00
92 | 5 | 4C x 10 Sq. mm CU. Armoured XLPE CABLE (for induction cook top, DBs, Buffet counter KPDB) |  | Nos. | 8.000 | 0.00 | 0.00
93 | 6 | 4C x 6 Sq. mm CU. armoured XLPE Cable (For electric fry top, SPA DB, SPA Geyser, LDB, small power DB etc) |  | Nos. | 8.000 | 0.00 | 0.00
94 | 7 | 4C x 4 Sq. mm CU. armoured XLPE Cable (For DX ODU, 20 TR CSU, Pasta Cooker, Induction WOK, Floor AHU etc,)) |  | Nos. | 8.000 | 0.00 | 0.00
95 | 8 | 4C x 2.5 Sq. mm CU. armoured XLPE Cable (Exhaust, FA fans, CSUs etc) |  | Nos. | 8.000 | 0.00 | 0.00
96 | 9 | 3C x 4 Sq. mm CU. armoured XLPE Cable |  | Nos. | 8.000 | 0.00 | 0.00
97 | 10 | 3C x 6 Sq. mm CU. Unarmoured XLPE Cable (For UPS I P and output upto the isolator) |  | Nos. | 4.000 | 0.00 | 0.00
98 | 13 | 3Rx1Cx6 Sq.mm YY FRLS Cable (Cu) (For UPS I P, O P from isolator) in flexible metallic conduit. |  | Nos. | 6.000 | 0.00 | 0.00
99 |  | TOTAL FOR CABLES ACCESSORIES |  |  | 0.000 | 0.00 | 0.00
100 | V | POINT WIRING ACCESSORIES |  |  | 0.000 | 0.00 | 0.00
101 |  | Note Make a provision for suspenders as per site ceiling requirement. |  |  | 0.000 | 0.00 | 0.00
102 | 1 | Wiring of circuit mains from DB to the switchboards or power points. |  |  | 0.000 | 0.00 | 0.00
103 | a | 3RX2.5 sq.mm FR-LSH insulated multistrand copper conductor wires, 1.1 kV grade, in G.I. Conduits of 20 mm dia |  | Mtrs. | 1750.000 | 0.00 | 0.00
104 | b | 2RX4 sq.mm + 1R X 2.5 sq. mm. FR-LSH insulated multistrand copper conductor wires, 1.1 kV grade in G.I. Conduits of 20 mm dia |  | Mtrs. | 2750.000 | 0.00 | 0.00
105 | 2 | SWITCH OPERATED LIGHT POINT WIRING |  |  | 0.000 | 0.00 | 0.00
106 |  | Supply, installation, testing commissioning of point wiring for lights plug points bell point etc. in G.I. conduit of suitable diameter, surface or recessed mounted complete with junction box, joints, bends, switch box, cover plate etc. including 1.1kV grade 2 x 2.5+ 1 x 1.5 sq.mm. (Primary Points) Copper multi-stranded PVC insulated FRLS wires and 2 x 1.5 + 1 x 1.5 sq.mm. (Secondary Points) Copper multi-stranded PVC insulated FRLS wires, along with 6A modular surface recessed mounted switch, ceiling rose, connectors switch boxes etc. The work shall be completed with all material, labour, chiselling, making good surface etc. in cordination with civil agency complying with IE rules, regulations, standards local supply authority requirements. All G.I. conduit pipes, FRLS wires shall be considered) Note 1) The cost of Circuit Wiring from DB to switch board and switch board to switch board shall be covered by wiring of circuit mains |  |  | 0.000 | 0.00 | 0.00
107 | a | Primary point |  | Each | 55.000 | 0.00 | 0.00
108 | b | Secondary point |  | Each | 85.000 | 0.00 | 0.00
109 | 3 | MCB OPERATED LIGHT POINT WIRING (DIRECT FROM LDB) |  |  | 0.000 | 0.00 | 0.00
110 |  | Supply, installation, testing commissioning of point wiring for lights plug points bell point etc. in G.I. conduit of suitable diameter, surface or recessed mounted complete with junction box, joints, bends, switch box, cover plate etc. including 1.1kV grade 2 x 2.5+ 1 x 1.5 sq.mm. (Primary Points) Copper multi-stranded PVC insulated FRLS wires and 2 x 1.5 + 1 x 1.5 sq.mm. (Secondary Points) Copper multi-stranded PVC insulated FRLS wires, along with 6A modular surface recessed mounted switch, ceiling rose, connectors switch boxes etc. The work shall be completed with all material, labour, chiselling, making good surface etc. in cordination with civil agency complying with IE rules, regulations, standards local supply authority requirements. All G.I. conduit pipes, FRLS wires shall be considered) Note The first point shall be considered in running meters with 3X2.5 sq. mm wires. The loop poins shall be considered as secondary point shall be with 3X1.5 sq.mm wires with an average length of 10 metres. |  |  | 0.000 | 0.00 | 0.00
111 | a | Primary point |  | Each | 35.000 | 0.00 | 0.00
112 | b | Secondary point |  | Each | 77.000 | 0.00 | 0.00
113 |  | POWER POINT WIRING |  |  | 0.000 | 0.00 | 0.00
114 | 4 | Supplying, erecting , testing commissioning independent surface or recessed mounting modular 5A switch 5 15A sockesocket complete with switch box, internal wiring with required chiseling making good surface etc...in coordination with civil agency complying with IE rules, regulations, standards local supply authority requirements. as per final approval of Architect Consultant. (3X2.5 sq.mm wires for primary shall be multistrand copper conductor, FR-LSH type in G.I. conduit) Excluding of switch socket. (First power point shall be measure as per circuit mains wiring. The secondary is power point shall be about 5Mtr. |  |  | 0.000 | 0.00 | 0.00
115 |  | Secondary point |  | Nos. | 35.000 | 0.00 | 0.00
116 | 5 | Supplying, erecting , testing commissioning independent surface or recessed mounting modular 15A switch socket complete with switch box, internal wiring with required chiseling making good surface etc...in coordination with civil agency complying with IE rules, regulations, standards local supply authority requirements. as per final approval of Architect Consultant. (4sq.mm Wires shall be for primary FRLS type G.I. conduit ) Excluding of switch socket. (First power point shall be measure as per circuit mains wiring. The secondary is power point shall be about 5Mtr. |  |  | 0.000 | 0.00 | 0.00
117 |  | Secondary point |  | Each | 30.000 | 0.00 | 0.00
118 | 6 | Supply and installation of Perforated Cable Tray out of 14 gauge GI sheet complete with necessary fixing arrangement with Anchor Fastener and all other accessories as per the final approval of the Consultant Architect. Note Make a provision for suspenders as per site ceiling requirement. |  |  | 0.000 | 0.00 | 0.00
119 | a | 450 x 50 x 2mm |  | Mtr. | 30.000 | 0.00 | 0.00
120 | 7 | Supply and installation of AL raceway with 2 mm thickness proper ties clamps at appropriate intervals as per the route approved by Architect Consultant. (Cost of cutting the floor for laying of raceways to be included). |  |  | 0.000 | 0.00 | 0.00
121 | a | 2 runs of underfloor AL raceways of size 100 x 40 mm (Type-A) |  | Mtr. | 47.000 | 0.00 | 0.00
122 | b | 1 runs of underfloor AL raceways of size 100 x 40 mm |  | Mtr. | 5.000 | 0.00 | 0.00
123 | c | 1 runs of underfloor AL raceways of size 85 x 38 mm |  | Mtr. | 18.000 | 0.00 | 0.00
124 | d | 1 runs of underfloor AL raceway of size 65 x 38 mm |  | Mtr. | 75.000 | 0.00 | 0.00
125 | e | 2 runs of underfloor HMS grade uPVC Conduit Pipes 25 mm dia |  | Mtr. | 72.000 | 0.00 | 0.00
126 | 8 | Supply installation of GI junction boxes with 2 mm thickness, 2mm thick SS cover with 2” extra on all sides SS cover on top and having screw fixed plates on all four sides with knock out holes for conduits. The plates shall be retained on the sidezs having no conduit or raceway so as to avoid the entry of any unwanted material. Earth stud to be provided for all Junction boxes for earthing. Junction box to be prepared as per the final approval of Architect Consultant. The junction boxes shall be protected from the entry of unwanted material till the completion of the project the SS plates shall be installed after the final polishing of flooring. |  |  | 0.000 | 0.00 | 0.00
127 |  | Note |  |  | 0.000 | 0.00 | 0.00
128 | a | 450 x 450 x 50 mm |  | Nos. | 5.000 | 0.00 | 0.00
129 | b | 50 x 350 x 50 mm |  | Nos. | 5.000 | 0.00 | 0.00
130 | c | 250 x 250 x 50 mm |  | Nos. | 25.000 | 0.00 | 0.00
131 | d | 150 x 150 x 50 mm |  | Nos. | 38.000 | 0.00 | 0.00
132 | e | Waterproofing of Junction Boxes in the planter box area by applying Sealing compound, NEER of Emerson make (or eqv.) |  | Nos. | 10.000 | 0.00 | 0.00
133 | 9 | Supply, installation of temporary lighting power arrangement for construction purpose of with industrial type switch sockets MCB s ELCB s lighting fittings as required to finish the work for interior contractor necessary electrical protections throughout the site for construction work till the handover of site. Contractor shall maintain the saftey rules regulations as per Airport Security Department. The material shall be taken back by the contractor, also included scaffolded work at site during excution. |  | Job | 1.000 | 0.00 | 0.00
134 | 10 | Supply, installation, testing commissioning of modular type flush mounted plate type switch and switch + sockets with hot dipped GI box complete as per the final approval of Architect Consultant |  |  | 0.000 | 0.00 | 0.00
135 | a | 6A one way plate type switch |  | Nos. | 55.000 | 0.00 | 0.00
136 | c | 6A 5pin switch socket outlet (Raw UPS power) + USB |  | Nos. | 36.000 | 0.00 | 0.00
137 | c | 6 16A 5pin switch socket outlet (Raw UPS power) + USB |  | Nos. | 40.000 | 0.00 | 0.00
138 | d | 2nos 6 16A 5pin switch socket outlet (Raw power) |  | Nos. | 18.000 | 0.00 | 0.00
139 | e | 3 nos. 6 13A socket controlled by 1no 16A switch + USB |  | Nos. | 12.000 | 0.00 | 0.00
140 | g | 1 nos. 16A socket controlled by 1nos 16A switch |  | Nos. | 6.000 | 0.00 | 0.00
141 | h | RG6 coaxial TV outlet |  | Nos. | 12.000 | 0.00 | 0.00
142 | 11 | Supply, installation, testing commissioning of industrial type plug and sockets conforming to IEC-60309 of Make-C S Legrand Havells or eqv. |  |  | 0.000 | 0.00 | 0.00
143 | h | Industrial Socket, panel surface mounting type, IP-67, 63 Amps, 5-Pin, 3P+N+E, 415 V, 3-Ph, with 4-P MCB of 63A (For Induction Cook Top) |  | No. | 1.000 | 0.00 | 0.00
144 | i | Industrial Socket, panel surface mounting type, IP-67, 32 Amps, 5-Pin, 3P+N+E, 415 V, 3-Ph with 4-P MCB of 32A. (For Pasta Cooker, Elect. Fry Top Induction WOK) |  | Nos. | 3.000 | 0.00 | 0.00
145 | j | Industrial Socket, panel surface mounting type, IP-67, 32 Amps, 3-Pin, 2P+E, 230 V, 1-Ph with 2-P MCB of 16 20 32A. (For Kitchen and Buffet Counter as required) |  | Nos. | 10.000 | 0.00 | 0.00
146 | 12 | Supply installation of G.I. conduit with pull box junction box all accessories. |  |  | 0.000 | 0.00 | 0.00
147 | 13 | Providing Television wiring inside 25mm dia GI conduit from each TV outlet to LV Shaft by using coaxial cable of type RG 6. Tinned copper conductor with necessary accessories viz. deep junction boxes, inspection boxes bends, termination etc. |  | RM | 450.000 | 0.00 | 0.00
148 | 14 | SITC of following Splitter unit in Metal enclosure for Cable TV. |  |  | 0.000 | 0.00 | 0.00
149 | 14.1 | 4 way Splitter |  | Nos. | 1.000 | 0.00 | 0.00
150 | 14.2 | 6 way Splitter |  | Nos. | 1.000 | 0.00 | 0.00
151 |  | TOTAL FOR WIRING ACCESSORIES |  |  | 0.000 | 0.00 | 0.00
152 |  | EARTHING |  |  | 0.000 | 0.00 | 0.00
153 | 1 | Supply erection of G.I. strip of 25 x 3 mm used for earthing of DBs, AHUs, ODUs etc. by laying on wall, cable trays with necessary clamps fixed on wall painted with bituminous paint in an approved manner. |  | Mtr. | 350.000 | 0.00 | 0.00
154 | 2 | Supply erection of G.I. strip of 40 x 5 mm used for earthing of Main Panels by laying on wall, cable trays with necessary clamps fixed on wall painted with bituminous paint in an approved manner. |  | Mtr. | 450.000 | 0.00 | 0.00
155 | 3 | 1 no. 4 sq. mm YY cable in 25mm G.I. conduit for earthing forUPS, networking and other ELV applications.etc |  | Mtr. | 250.000 | 0.00 | 0.00
156 | 4 | Supplying erecting bare copper conductor of 8 swg for earthing purpose. As required. |  | Mtr. | 50.000 | 0.00 | 0.00
157 | 5 | Supplying erecting bare GI conductor of 8 swg for earthing purpose |  | Mtr. | 125.000 | 0.00 | 0.00
158 | 7 | SITC of Earthing terminal Box for distribution with 40X5 mm G.I. strip of 300 mm length. |  | Nos. | 1.000 | 0.00 | 0.00
159 | 8 | SITC of Earthing terminal Box for distribution with 25X6 mm Copper strip of 300 mm length. |  | Nos. | 1.000 | 0.00 | 0.00
160 |  | TOTAL FOR EARTHING |  |  | 0.000 | 0.00 | 0.00
161 |  | MISCELLANEOUS |  |  | 0.000 | 0.00 | 0.00
162 | 1 | Supply, fabrication and erection of M.S. Structural steel such as base mounting frames, brackets supports for installation of panels, cable tray etc.from M.S channel, angle, flats as per the requirement with painting of one coat of red oxide primer and two coats of approved shade of epoxy paint. |  | kgs. | 1500.000 | 0.00 | 0.00
163 | 1 | Supply fixing of the best quality LT Danger Boards(415V) for of approved shape and size as specified by the local electrical authorities written in English, and local Language |  | Nos. | 2.000 | 0.00 | 0.00
164 | 2 | Supply handed over to client of First Aid Box |  | Set | 2.000 | 0.00 | 0.00
165 | 3 | Supply of 2M x 1M Rubber mat as per IS 15652 2006, 2mm thick, suitable upto 3.3 KV, fire retardant, no effect of acids, alkalies and transformer oils, moisture proof, high tensile strength and texture finish cloth impression (Anti slip, marking on top) . Make – DOZZ or equivalent |  | Nos. | 4.000 | 0.00 | 0.00
166 |  | Supply fixing in position approved shock treatment chart written in English, Hindi and Gujarati. These charts shall be put in wooden frame covered with clear glass. |  | No. | 2.000 | 0.00 | 0.00
167 |  | Fire Extinguisher 4.5 Kg (BCE Type). |  | No. | 2.000 | 0.00 | 0.00
168 |  | Liaisoning with electrical inspector for necessary approvals of electrical installations. |  | LS | 1.000 | 0.00 | 0.00
169 | II | PA MUSIC SYSTEM CONTAINMENT (BIAMP - 8600) |  |  | 0.000 | 0.00 | 0.00
170 |  | Note The PA system shall be integrated with Fire Alarm System to activate evacuation message at preset loud volume in case of emergency |  |  | 0.000 | 0.00 | 0.00
171 | 1 | Supply, Installation, Testing Commissioning of 6 Zone Controller (Make - BIAMP), Location - Reception |  | Nos. | 1.000 | 0.00 | 0.00
172 | 2 | Supply, Installation, Testing Commissioning of 6W ceiling mount speaker. (Make - BIAMP) |  | Nos. | 30.000 | 0.00 | 0.00
173 | 3 | Supply, Installation, Testing Commissioning of 12W Wall Mounted Speaker. (Make - BIAMP) |  | Nos. | 6.000 | 0.00 | 0.00
174 | 4 | Supply, Installation, Testing Commissioningof 300W Booster amplifier with zone controller (BIAMP), Location - Reception |  | Nos. | 1.000 | 0.00 | 0.00
175 | 5 | Audio Message Manager |  | No. | 1.000 | 0.00 | 0.00
176 | 6 | Desk Microphone, (6-Zone Call Station), Location - Reception |  | No. | 1.000 | 0.00 | 0.00
177 | 7 | Supply and laying of 2 Core Speaker Cable including 25mm G.I. conduit. |  | Mtr | 1250.000 | 0.00 | 0.00
178 | 8 | Required connectors, jumper patch cables etc other accessories required. |  | Lot | 1.000 | 0.00 | 0.00
179 | I | DATA, WIFI TELEPHONE SYSTEM |  |  | 0.000 | 0.00 | 0.00
180 | 1 | Supplying,Installation,Testing and Commissioning of CAT 6 cable for Data connectivity pulled in G.I. conduit. |  | Rmt | 2150.000 | 0.00 | 0.00
181 | 2 | Supplying,Installation,Testing and Commissioning of CAT 6 cable for Telephone Data connectivity pulled in Al raceways laid already. |  | Rmt | 1880.000 | 0.00 | 0.00
182 | 3 | Supply, Installation of CAT 6 Information Outlet |  |  | 0.000 | 0.00 | 0.00
183 | a | DATA OUTLET |  | Nos. | 48.000 | 0.00 | 0.00
184 | b | WI-FI |  | Nos. | 10.000 | 0.00 | 0.00
185 | c | CCTV |  | Nos. | 33.000 | 0.00 | 0.00
186 | 4 | Supply, installation Configuration of Network Switch EX 4200, 24-port 10 100 1000BaseT (24 ports PoE+) with 1x930W AC PS PART NO. EX4200-24PX. |  | Nos | 2.000 | 0.00 | 0.00
187 | 5 | Supply, installation Configuration of Network Switch EX 4200, 48-port 10 100 1000BaseT (48 ports PoE+) with 1x930W AC PS PART NO. EX4200-48PX. |  | Nos. | 1.000 | 0.00 | 0.00
188 | 6 | Supply, installation of 27 U Wall Mount Rack with Std. Accessories required mounting Hardware ( WQ ) Black |  | Nos | 1.000 | 0.00 | 0.00
189 | 8 | Supply, installation of Dual band (5 GHz and 2.4 GHz concurrent) Mid – Range 802.11n Wireless Access Point + Power Adaptor + PoE Injector + Ceiling Mounting Kit. |  | Nos | 10.000 | 0.00 | 0.00
190 |  | Distributed Antenna System (DAS) |  |  | 0.000 | 0.00 | 0.00
191 | 10 | SIGNAL MAP ANALYSIS TEST FOR MOBILE NETWORK Carry out tests for signal strength to plan DAS network. |  | LS | 1.000 | 0.00 | 0.00
192 | 10.1 | Supply, installation, testing and commissioning of Antenna points suitable for 4-Band coverage, low or medium power as shown in the layout. |  | Nos. | 8.000 | 0.00 | 0.00
193 | 10.2 | Supply, installation and termination of RG-6 coaxial cable in GI conduits of 25 mm dia |  | Mtrs. | 530.000 | 0.00 | 0.00
194 | 10.3 | Termination and integration at the main existing DAS antenna point |  | LS | 1.000 | 0.00 | 0.00