## 080 Lounge (hvac)
| Site Name | Budget | Time Line
| 080 Lounge BLR | 10411376 | 3 months
10
Sr No | Description | Event | Pioneer Project | Crystal Aircool | Anjle MEP |  | Line wise minimum
1 | Hvac , kitchen ventilation work | RFQ 1 | 7050004 | 7322146.72 | 7643985 | 7050004 | 6307186.169
2 |  | RFQ 2 | 7050004 | 6956039.48 | 9309452.3
3 |  | Auction 3&4 | 6649204 | 6825532.139 | 9145162.3
4 |  | Final commercial | 6750000 |  |  | 2395162.3
|  | Rank | L1 | L3 | L2
| Current projects |  | Ulava charu-Hyd KFC-Hyd Carl's Jr-Hyd Dhaba-1986 Hyd Land side -Hyd |  | Jamie's Pizzeria-Hyd Land side kitchen-Hyd MOD-Hyd Tacobell-Hyd Airside Kitchen-Hyd
| Purchase remark |  |  | Did not quote for Kitchen ventilation

## Final summary
|  | RFQ No: R1359 COST COMPARISON REPORT | RFQ No: R1359 COST COMPARISON REPORT | RFQ No: R1359 COST COMPARISON REPORT | Comp. Date : 29/07/2024 | Comp. Date : 29/07/2024 | Comp. Date : 29/07/2024 | Vendor Name : PIONEER PROJECT SOLUTION (T054969) | [30 empty] | Vendor Name : CRYSTAL AIRCOOL (RV242522537) | [30 empty] | Vendor Name : ANJLE MEP PROJECT PVT LTD (RV242523025)
|  | RFQ No: R1359 COST COMPARISON REPORT | RFQ No: R1359 COST COMPARISON REPORT | RFQ No: R1359 COST COMPARISON REPORT | RFQ #: R1359 | RFQ #: R1359 | RFQ #: R1359 | Contact Name : ASHRAF | [30 empty] | Contact Name : JOHN | [30 empty] | Contact Name : PREMKANT
|  | RFQ No: R1359 COST COMPARISON REPORT | RFQ No: R1359 COST COMPARISON REPORT | RFQ No: R1359 COST COMPARISON REPORT | RFQ Date : 24/07/2024 17:16:44 | RFQ Date : 24/07/2024 17:16:44 | RFQ Date : 24/07/2024 17:16:44 | Vendor City : | [30 empty] | Vendor City : | [30 empty] | Vendor City :
|  | RFQ No: R1359 COST COMPARISON REPORT | RFQ No: R1359 COST COMPARISON REPORT | RFQ No: R1359 COST COMPARISON REPORT | BCD Date : 25/07/2024 14:03:00 | BCD Date : 25/07/2024 14:03:00 | BCD Date : 25/07/2024 14:03:00 | Telephone # : | [30 empty] | Telephone # : | [30 empty] | Telephone # :
|  | RFQ No: R1359 COST COMPARISON REPORT | RFQ No: R1359 COST COMPARISON REPORT | RFQ No: R1359 COST COMPARISON REPORT |  |  |  | Mobile # : 98106 34901 | [30 empty] | Mobile # : | [30 empty] | Mobile # :
PR Number : BLR-2425-00064 | PR Number : BLR-2425-00064 | PR Number : BLR-2425-00064 | PR Number : BLR-2425-00064 | PR Number : BLR-2425-00064 | PR Number : BLR-2425-00064 | PR Number : BLR-2425-00064 | PR Number : BLR-2425-00064 | Email : projectspioneer@gmail.com | [30 empty] | Email : crystalhvac002@gmail.com | [30 empty] | Email : anjlemepprojects@gmail.com
Package / RFQ Name : TFAS / RFQ / BLR-2425-00064 | Package / RFQ Name : TFAS / RFQ / BLR-2425-00064 | Package / RFQ Name : TFAS / RFQ / BLR-2425-00064 | Package / RFQ Name : TFAS / RFQ / BLR-2425-00064 | Package / RFQ Name : TFAS / RFQ / BLR-2425-00064 | Package / RFQ Name : TFAS / RFQ / BLR-2425-00064 | Package / RFQ Name : TFAS / RFQ / BLR-2425-00064 | Package / RFQ Name : TFAS / RFQ / BLR-2425-00064 | Round # : 1 (RFQ) |  |  |  |  | Round # : 2 (RFQ) |  |  |  |  | Round # : 3 (Auction) |  |  |  |  | Round # : 3 (Auction) |  |  |  |  | Round # : 4 (Auction) | [10 empty] | Round # : 1 (RFQ) |  |  |  |  | Round # : 2 (RFQ) |  |  |  |  | Round # : 3 (Auction) |  |  |  |  | Round # : 3 (Auction) |  |  |  |  | Round # : 4 (Auction) | [10 empty] | Round # : 1 (RFQ) |  |  |  |  | Round # : 2 (RFQ) |  |  |  |  | Round # : 3 (Auction) |  |  |  |  | Round # : 3 (Auction) |  |  |  |  | Round # : 4 (Auction)
Buyer : Binu Balachandran / Technical : / Approver : | Buyer : Binu Balachandran / Technical : / Approver : | Buyer : Binu Balachandran / Technical : / Approver : | Buyer : Binu Balachandran / Technical : / Approver : | Buyer : Binu Balachandran / Technical : / Approver : | Buyer : Binu Balachandran / Technical : / Approver : | Buyer : Binu Balachandran / Technical : / Approver : | Buyer : Binu Balachandran / Technical : / Approver : | Quotation Date : |  | Quotation Validity Date : |  |  | Quotation Date : |  | Quotation Validity Date : |  |  | Quotation Date : |  | Quotation Validity Date : |  |  | Quotation Date : |  | Quotation Validity Date : |  |  | Quotation Date : |  | Quotation Validity Date : | [5 empty] | Quotation Validity Date : |  |  | Quotation Date : |  | Quotation Validity Date : |  |  | Quotation Date : |  | Quotation Validity Date : |  |  | Quotation Date : |  | Quotation Validity Date : |  |  | Quotation Date : |  | Quotation Validity Date : |  |  | Quotation Date : |  | Quotation Validity Date : | [5 empty] | Quotation Validity Date : |  |  | Quotation Date : |  | Quotation Validity Date : |  |  | Quotation Date : |  | Quotation Validity Date : |  |  | Quotation Date : |  | Quotation Validity Date : |  |  | Quotation Date : |  | Quotation Validity Date : |  |  | Quotation Date : |  | Quotation Validity Date : | [5 empty] | Quotation Validity Date :
Comp. # : 4 | Comp. # : 4 | Comp. # : 4 | Comp. # : 4 | Comp. # : 4 | Currency :INR | Currency :INR | Currency :INR | Buyer Remark : |  |  |  |  | Buyer Remark : |  |  |  |  | Buyer Remark : |  |  |  |  | Buyer Remark : |  |  |  |  | Buyer Remark : | [10 empty] | Buyer Remark : |  |  |  |  | Buyer Remark : |  |  |  |  | Buyer Remark : |  |  |  |  | Buyer Remark : |  |  |  |  | Buyer Remark : | [10 empty] | Buyer Remark : |  |  |  |  | Buyer Remark : |  |  |  |  | Buyer Remark : |  |  |  |  | Buyer Remark : |  |  |  |  | Buyer Remark :
Comp. # : 4 | Comp. # : 4 | Comp. # : 4 | Comp. # : 4 | Comp. # : 4 | BUDGET PRICE : | .00 |  | Quote Currency : INR |  |  |  |  | Quote Currency : INR |  |  |  |  | Quote Currency : INR |  |  |  |  | Quote Currency : INR |  |  |  |  | Quote Currency : INR | [10 empty] | Quote Currency : INR |  |  |  |  | Quote Currency : INR |  |  |  |  | Quote Currency : INR |  |  |  |  | Quote Currency : INR |  |  |  |  | Quote Currency : INR | [10 empty] | Quote Currency : |  |  |  |  | Quote Currency : INR |  |  |  |  | Quote Currency : INR |  |  |  |  | Quote Currency : INR |  |  |  |  | Quote Currency : INR
# | Item Code | Item Description | Unit | Qty | Last PO Details | Lowest Unit Rate | Lowest Vendor | Price | Disc % | GST % | Unit Price | Total | Price | Disc % | GST % | Unit Price | Total | Price | Disc % | GST % | Unit Price | Total | Price | Disc % | GST % | Unit Price | Total | Price | Disc % | GST % | Unit Price | Total | Converted Total (INR) | Disc % | GST % | Technical | Unit Price | Total | Price | Disc % | GST % | Unit Price | Total | Price | Disc % | GST % | Unit Price | Total | Price | Disc % | GST % | Unit Price | Total | Price | Disc % | GST % | Unit Price | Total | Price | Disc % | GST % | Unit Price | Total | Converted Total (INR) | Disc % | GST % | Technical | Unit Price | Total | Price | Disc % | GST % | Unit Price | Total | Price | Disc % | GST % | Unit Price | Total | Price | Disc % | GST % | Unit Price | Total | Price | Disc % | GST % | Unit Price | Total | Price | Disc % | GST % | Unit Price | Total | Converted Total (INR) | Disc % | GST % | Technical | Unit Price | Total
1 |  | HVAC High side Work | NOS | 1 |  | 1765500 | PIONEER PROJECT SOLUTION | 1820500 | 0 | 28 | 1820500 | 1820500 | 1820500 | 0 | 28 | 1820500 | 1820500 | 1820500 | 0 | 0 | 1820500 | 1820500 | 1820500 | 0 | 0 | 1820500 | 1820500 | 1820500 | 0 | 0 | 1820500 | 1820500 | 1820500 | 0 | 0 |  | 1765500 | 1765500 | 1948220 | 0 | 28 | 1948220 | 1948220 | 1948220 | 0 | 28 | 1850809 | 1850809 | 1948220 | 0 | 0 | 1850809 | 1850809 | 1948220 | 0 | 0 | 1850809 | 1850809 | 1948220 | 0 | 0 | 1850809 | 1850809 | 1850809 | 0 | 0 |  | 1850809 | 1850809 | 2225500 | 0 | 0 | 0 | 0 | 2225500 | 0 | 28 | 2225500 | 2225500 | 2225500 | 0 | 0 | 2225500 | 2225500 | 2225500 | 0 | 0 | 2225500 | 2225500 | 2225500 | 0 | 0 | 2225500 | 2225500 | 2225500 | 0 | 0 |  | 2202500 | 2202500 | 2819200
2 |  | HVAC Low side Work | NOS | 1 |  | 2850800 | PIONEER PROJECT SOLUTION | 3062800 | 0 | 18 | 3062800 | 3062800 | 3062800 | 0 | 18 | 3062800 | 3062800 | 3062800 | 0 | 0 | 3062800 | 3062800 | 3062800 | 0 | 0 | 3062800 | 3062800 | 3062800 | 0 | 0 | 3062800 | 3062800 | 3062800 | 0 | 0 |  | 2850800 | 2850800 | 4091884 | 0 | 18 | 4091884 | 4091884 | 4091884 | 0 | 18 | 3887289.8 | 3887289.8 | 4091884 | 0 | 0 | 3887289.8 | 3887289.8 | 4091884 | 0 | 0 | 3887289.8 | 3887289.8 | 4091884 | 0 | 0 | 3887289.8 | 3887289.8 | 3887289.8 | 0 | 0 |  | 3887289.8 | 3887289.8 | 4029985 | 0 | 0 | 0 | 0 | 4029985 | 0 | 18 | 4029985 | 4029985 | 4029985 | 0 | 0 | 4029985 | 4029985 | 4029985 | 0 | 0 | 4029985 | 4029985 | 4029985 | 0 | 0 | 4029985 | 4029985 | 4029985 | 0 | 0 |  | 3979985 | 3979985 | 4696382.3
3 |  | Kitchen Ventilation High side Work | NOS | 1 |  | 318000 | PIONEER PROJECT SOLUTION | 350000 | 0 | 18 | 350000 | 350000 | 350000 | 0 | 18 | 350000 | 350000 | 350000 | 0 | 0 | 350000 | 350000 | 350000 | 0 | 0 | 350000 | 350000 | 350000 | 0 | 0 | 350000 | 350000 | 350000 | 0 | 0 |  | 318000 | 318000 | 1 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 0 | 0 |  | 1 | 1 | 670000 | 0 | 0 | 0 | 0 | 670000 | 0 | 28 | 670000 | 670000 | 670000 | 0 | 0 | 670000 | 670000 | 670000 | 0 | 0 | 670000 | 670000 | 670000 | 0 | 0 | 670000 | 670000 | 670000 | 0 | 0 |  | 670000 | 670000 | 790600
4 |  | Kitchen Ventilation Low side Work | NOS | 1 |  | 551000 | PIONEER PROJECT SOLUTION | 587000 | 0 | 18 | 587000 | 587000 | 587000 | 0 | 18 | 587000 | 587000 | 587000 | 0 | 0 | 587000 | 587000 | 587000 | 0 | 0 | 587000 | 587000 | 587000 | 0 | 0 | 587000 | 587000 | 587000 | 0 | 0 |  | 551000 | 551000 | 1 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 0 | 0 |  | 1 | 1 | 718500 | 0 | 0 | 0 | 0 | 718500 | 0 | 18 | 718500 | 718500 | 718500 | 0 | 0 | 718500 | 718500 | 718500 | 0 | 0 | 718500 | 718500 | 718500 | 0 | 0 | 718500 | 718500 | 718500 | 0 | 0 |  | 711000 | 711000 | 838980
Item Total | [8 empty] | 0 | 1229704 |  | 5820300 |  | 0 | 1229704 |  | 5820300 |  | 0 | 0 |  | 5820300 |  | 0 | 0 |  | 5820300 |  | 0 | 0 |  | 5820300 | 5820300 | 0 | 0 |  |  | 5485300 |  | 0 | 1282040.72 |  | 6040106 |  | 0 | 1217938.68 |  | 5738100.8 |  | 0 | 0 |  | 5738100.8 |  | 0 | 0 |  | 5738100.8 |  | 0 | 0 |  | 5738100.8 | 5738100.8 | 0 | 0 |  |  | 5738100.8 |  | 0 | 0 |  | 0 |  | 0 | 1665467.3 |  | 7643985 |  | 0 | 0 |  | 7643985 |  | 0 | 0 |  | 7643985 |  | 0 | 0 |  | 7643985 | 7643985 | 0 | 0 |  |  | 7563485 | 9145162.3
Discount Total Value | [7 empty] | Grand Dis. Amt | 0 |  |  | 0 | Grand Dis. Amt | 0 |  |  | 0 | Grand Dis. Amt | 0 |  |  | 0 | Grand Dis. Amt | 0 |  |  | 0 | Grand Dis. Amt | 0 |  |  | 0 | 0 | 0 |  |  |  | 0 | Grand Dis. Amt | 0 |  |  | 0 | Grand Dis. Amt | 0 |  |  | 0 | Grand Dis. Amt | 0 |  |  | 0 | Grand Dis. Amt | 0 |  |  | 0 | Grand Dis. Amt | 0 |  |  | 0 | 0 | 0 |  |  |  | 0 | Grand Dis. Amt | 0 |  |  | 0 | Grand Dis. Amt | 0 |  |  | 0 | Grand Dis. Amt | 0 |  |  | 0 | Grand Dis. Amt | 0 |  |  | 0 | Grand Dis. Amt | 0 |  |  | 0 | 0 | 0 |  |  |  | 0
GST Total Amount | [11 empty] | 1229704 |  |  |  |  | 1229704 |  |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 |  |  |  |  | 1282040.72 |  |  |  |  | 1217938.68 |  |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 1665467.3 |  |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0
Net Landed Cost | [10 empty] | INR | 7050004 |  |  |  | INR | 7050004 |  |  |  | INR | 5,820,300.00 |  |  |  | INR | 5,820,300.00 |  |  |  | INR | 5,820,300.00 | 5,820,300.00 |  |  |  | INR | 5485300 |  |  |  | INR | 7322146.72 |  |  |  | INR | 6956039.48 |  |  |  | INR | 5,738,100.80 |  |  |  | INR | 5,738,100.80 |  |  |  | INR | 5,738,100.80 | 5,738,100.80 |  |  |  | INR | 5738100.8 |  |  |  |  | .00 |  |  |  | INR | 9,309,452.30 |  |  |  | INR | 7,643,985.00 |  |  |  | INR | 7,643,985.00 |  |  |  | INR | 7643985 | 7,643,985.00 |  |  |  | INR | 7563485
Vendor Status | [7 empty] | Round # : 1 (RFQ) | Round # : 1 (RFQ) | Round # : 2 (RFQ) | Round # : 2 (RFQ) | Round # : 3 (Auction) | Round # : 3 (Auction) | Round # : 3 (Auction) | Round # : 3 (Auction) | Round # : 4 (Auction) | Round # : 4 (Auction) | Round # : 4 (Auction) | Round # : 4 (Auction)
Sr No. | Vendor Code | Vendor Name | [5 empty] | Status | Remarks | Status | Remarks | Status | Remarks | Status | Remarks | Status | Remarks | Status | Remarks
1 | T054969 | PIONEER PROJECT SOLUTION | [5 empty] | Participate |  | Participate |  | Participate |  | Participate |  | Participate |  | Participate
2 | RV232419193 | ANJLE MEP PROJECTS PVT LTD | [5 empty] | Not Participate |  | Not Participate |  | Not Participate |  | Not Participate |  | Not Participate |  | Not Participate
3 | RV242522852 | HAIER INDIA | [5 empty] | Not Participate |  | Not Participate |  | Not Participate |  | Not Participate |  | Not Participate |  | Not Participate
4 | RV242522537 | CRYSTAL AIRCOOL | [5 empty] | Participate |  | Participate |  | Participate |  | Participate |  | Participate |  | Participate
5 | T054973 | EMPIRE FURNITURES | [5 empty] | Not Participate |  | Participate |  | Participate |  | Participate |  | Participate |  | Participate
6 | RV242523025 | ANJLE MEP PROJECT PVT LTD | [7 empty] | Participate |  | Participate |  | Participate |  | Participate |  | Participate
7 | T054523 | Gold Fingers | [7 empty] | Participate |  | Participate |  | Participate |  | Participate |  | Participate
8 | RV232419136 | NAS Contracts Private Limited | [7 empty] | Not Participate |  | Not Participate |  | Not Participate |  | Not Participate |  | Not Participate

## RFQ comparative
|  | RFQ No: R1359 COST COMPARISON REPORT | Comp. Date : 29/07/2024 | Comp. Date : 29/07/2024 | Comp. Date : 29/07/2024 | Vendor Name : CRYSTAL AIRCOOL | Vendor Name : CRYSTAL AIRCOOL | Vendor Name : PIONEER PROJECT SOLUTION | Vendor Name : PIONEER PROJECT SOLUTION | Vendor Name : ANJLE MEP PROJECT PVT LTD | Vendor Name : ANJLE MEP PROJECT PVT LTD
|  | RFQ No: R1359 COST COMPARISON REPORT | RFQ #: R1359 | RFQ #: R1359 | RFQ #: R1359 | Contact Name : JOHN | Contact Name : JOHN | Contact Name : ASHRAF | Contact Name : ASHRAF | Contact Name : PREMKANT | Contact Name : PREMKANT
|  | RFQ No: R1359 COST COMPARISON REPORT | RFQ Date : 08/07/2024 09:51:08 | RFQ Date : 08/07/2024 09:51:08 | RFQ Date : 08/07/2024 09:51:08 | Vendor City : | Vendor City : | Vendor City : | Vendor City : | Vendor City : | Vendor City :
|  | RFQ No: R1359 COST COMPARISON REPORT | BCD Date : 24/07/2024 10:41:00 | BCD Date : 24/07/2024 10:41:00 | BCD Date : 24/07/2024 10:41:00 | Telephone # : | Telephone # : | Telephone # : | Telephone # : | Telephone # : | Telephone # :
|  | RFQ No: R1359 COST COMPARISON REPORT |  |  |  | Mobile # : | Mobile # : | Mobile # : 98106 34901 | Mobile # : 98106 34901 | Mobile # : | Mobile # :
PR Number : BLR-2425-00064 | PR Number : BLR-2425-00064 | PR Number : BLR-2425-00064 | PR Number : BLR-2425-00064 | PR Number : BLR-2425-00064 | PR Number : BLR-2425-00064 | Email : crystalhvac002@gmail.com | Email : crystalhvac002@gmail.com | Email : projectspioneer@gmail.com | Email : projectspioneer@gmail.com | Email : anjlemepprojects@gmail.com | Email : anjlemepprojects@gmail.com
Package / RFQ Name : TFAS / RFQ / BLR-2425-00064 | Package / RFQ Name : TFAS / RFQ / BLR-2425-00064 | Package / RFQ Name : TFAS / RFQ / BLR-2425-00064 | Package / RFQ Name : TFAS / RFQ / BLR-2425-00064 | Package / RFQ Name : TFAS / RFQ / BLR-2425-00064 | Package / RFQ Name : TFAS / RFQ / BLR-2425-00064 | Round # : 2 (RFQ) | Round # : 2 (RFQ) | Round # : 2 (RFQ) | Round # : 2 (RFQ) | Round # : 2 (RFQ) | Round # : 2 (RFQ)
Buyer : Binu Balachandran | Buyer : Binu Balachandran | Buyer : Binu Balachandran | Buyer : Binu Balachandran | Buyer : Binu Balachandran | Buyer : Binu Balachandran | Techanical Score : | Techanical Score : | Techanical Score : | Techanical Score : | Techanical Score : | Techanical Score :
Comp. # : 2 | Comp. # : 2 | Comp. # : 2 | Currency :INR | Currency :INR | Currency :INR | Quotation Date : | Quotation Date : | Quotation Date : | Quotation Date : | Quotation Date : | Quotation Date :
Comp. # : 2 | Comp. # : 2 | Comp. # : 2 | BUDGET PRICE :.00 | BUDGET PRICE :.00 | BUDGET PRICE :.00 | Quotation Validity Date : | Quotation Validity Date : | Quotation Validity Date : | Quotation Validity Date : | Quotation Validity Date : | Quotation Validity Date :
Sr No. | Item Code | Item Name | UOM | Qty | Minimum Amount | Unit Price | Amount | Unit Price | Amount | Unit Price | Amount
1 |  | HVAC High side Work | NOS | 1 | 1537050 |  | 1850809 |  | 1820500 |  | 2225500
1 |  | Note Prices shall be based on supply, installation, testing commissioning (SITC) at site including all taxes, duties, transportation insurance etc.
2 | a | AIR HANDLING UNIT CHW FLOOR MOUNTED AIR HANDLING UNIT SITC of double skin floor mounted AHU with suitable plug type fans with IE3 efficient 3phase motor, UVGI, Moisture eliminators etc. The thickness of panel to be with 42+ -3mm thick PUF Insulation. The coil shall be of hard copper tubes covered by aluminium fins with 13-15 FPI. The AHU to have a SS condensate drain tray which shall be duly insulated with 13mm thick class O nitrile rubber insulation. The contractor to furnish the GA drawings of AHU prior to ordering with necessary technical catalogues and fan curve selections. The noise level near the AHU should not cross more than 60dbA at 1m away from the unit. Also the AHU shall have a prefilter of MERV 8 with necessary framework. AHU body frame shall be with Aluminium . AHU shall have TEFC Squirrel Cage IP 55 Protected VFD Compatible induction motor, copper header, Copper to MS adopter, vibration isolation pad. Scope also includes limit switch with lights inside AHU. AHUs shall be selected for a maximum face velocity of 500 FPM (2.5MPS) and as per schedule of air handling units. Fan outlet velocity shall not exceed 1600 FPM (8.12 MPS). Chilled water inlet Outlet temp to be 8 13.5°C. AHUs shall be of following design parameters Capacity Tonnage ESP No. of USGPM (Cfm) TR (mm WG) Rows 11200 25 40 4 6 60 | No | 1 | 450000 | 485309 | 485309 | 450000 | 450000 | 675000 | 675000
3 | a | VRF FLOOR MOUNTED AIR HANDLING UNIT SITC of double skin floor mounted AHU with suitable plug type fans with rated 3phase motor. The thickness of panel to be with 42+ -3mm thick PUF Insulation. The coil shall be of hard copper tubes covered by aluminium fins with 13-15 FPI. The AHU to have a SS condensate drain tray which shall be duly insulated with 13mm thick class O nitrile rubber insulation. The contractor to furnish the GA drawings of AHU prior to ordering with necessary technical catalogues and fan curve selections. The noise level near the AHU should not cross more than 60-65dbA at 3m away from the unit. Also the AHU shall have a prefilter of MERV 8 with necessary framework. AHU body frame shall be with Aluminium. AHU shall have TEFC Squirrel Cage IP 55 Protected VFD Compatible induction motor, and vibration isolation pads. Scope also includes limit switch with lights in AHU. Cooling Coil section with AHRI certified Coil (0.15mm AL 13 FPI fins 12.7 mm OD 27 SWG Cu Tube) suitable for VRF Outdoor Unit (R410a refrigerant). AHUs shall be selected for a maximum face velocity of 500 FPM (2.5MPS) and as per schedule of air handling units. Fan outlet velocity shall not exceed 1600 FPM (8.12 MPS). AHUs shall be of following design parameters Capacity Tonnage ESP No. of (Cfm) TR (mm WG) Rows 10500 27 40 4 6 | No. | 1 | 425000 | 475825 | 475825 | 425000 | 425000 | 635000 | 635000
4 | a | SUPPLY OF VRF OUT-DOOR UNITS Supply of air cooled variable refrigerant flow modular type ODUs each comprising of multiple rotary scroll compressors fully inverter driven, full charge of refrigerant gas (R-410a), lubricating oil and all accessories as per the specifications. TheODUs shall be suitable for operation on 415 ± 10% volts, 50Hz, 3 phase AC power supply and the condensing units shall be of following capacities OUTDOOR UNITS 34 HP at site conditions. Note The unit shall be selected taking indoor and ambient deration, refrigerant pipe length deration in to account. | No. | 1 | 559550 | 559550 | 559550 | 695000 | 695000 | 755000 | 755000
5 |  | AHU CONTROLLER AND EEV KIT - Supply of AHU Controller, Electronic Expansion Valve (EEV) Kit and all other necessary accessories to connect with VRF ODU s. | No. | 1 | 25000 | 75050 | 75050 | 65000 | 65000 | 25000 | 25000
6 |  | FRAME WORK - Supply, fabrication and installation of PCC Siporex blocks for AHU support. AHU framework shall be part of AHU supply. Each AHU shall require 9nos. of blocks. | Sets | 3 | 0 | 0 | 0 | 25000 | 75000 | 15000 | 45000
7 |  | SPARE FILTER - One set of MERV 8 throw away type filters to be provided for all AHUs. These filters will be used for commissioning. Original set of filters will be installed as instructed by Architect Consultants. | Sets | 2 | 37000 | 45600 | 91200 | 35000 | 70000 | 18500 | 37000
8 |  | GENERAL NOTES a. Fan outlet velocity - 1600 FPM b. Contractor shall submit static pressure calculation for all above units to Client Consultant. c. Any change in motor HP shall be made at no extra cost to client. d. Fan efficiency shall be minimum 75% e. The cost shall be included liftting shifting of each equipment material with all necesaary arrnagement. Also, it shall be included the cost of scaffloding required for Installation of such material equipment.
9 |  | VENTILATION SYSTEM INLINE CIRCULAR FAN SITC of Inline Circular fan (silent type) with speed control, direct drive package - motor with outlet dampers, fan inlet outlet flexible connection, hanging arrangement with vibration isolators etc. Power will be provided 5 ft away from fan and necessary control wiring with plug will be provided by AC contractor. Motor efficiency IE2 IE3, AMCA Certification and Noise levels at 1m distance to be specified.The fans shall have BMS Compatibility.
10 | a | 700 CFM @ 25 mmwg ESP | Nos | 2 | 33000 | 58900 | 117800 | 16500 | 33000 | 20500 | 41000
11 | b | 100 CFM @ 15 mmwg ESP | No | 1 | 7500 | 46075 | 46075 | 7500 | 7500 | 12500 | 12500
12 |  | NOTES a. Contractor shall submit static pressure calculation for all above units to Client Consultant. b. Any change in motor HP shall be made at no extra cost to client. c. The cost shall be included liftting shifting of each equipment material with all necesaary arrnagement. Also, it shall be included the cost of scaffloding required for Installation of such material equipment.
2 |  | HVAC Low side Work | NOS | 1 | 2761764.55 |  | 3887289.8 |  | 3062800 |  | 4029985
13 |  | Note Prices shall be based on supply, installation, testing commissioning (SITC) at site including all taxes, duties, transportation insurance etc.
14 | 2.1 | CHILLED WATER PIPING WITH INSULATION
15 |  | CHW PIPE SITC of MS Heavy duty class C ERW Chilled Water pipe conforming to IS 1239 - 2004 primer painted including bends, tees, MS supports, PUFF saddles, anchor fasteners, steel angles and any other material required to complete the work. The piping flange connection bolts, washers and nuts should be hot dipped galvanised. Flourscent Plastic Sticker or paint shall be applied to indicate Water flow directions. Only End flanges to be used for capping of pipes. inch inch Table E inch inch of BS code for flange thickness to be adhered. Dia 50 mm | Rmt | 15 | 18750 | 2992.5 | 44887.5 | 1650 | 24750 | 1250 | 18750
16 |  | CHILLED WATER PIPING INSULATION SITC of insulation for chilled water. piping. For internal pipe - Stick 25mm thick Nitrile rubber Insulation with anti microbial coating, sealing all joints. putting all joints at 300 mm intervals with PVC bands and finally sealing with 3M glass cloth vapour barrier. Dia 50 mm | Rmt | 15 | 11250 | 2707.5 | 40612.5 | 750 | 11250 | 750 | 11250
17 | a | BUTTERFLY VALVES SITC of CI Butterfly valves shall be wafer type, bi-directional Butterfly valves MSS SP-67; ANSI Class 150 carbon steel body conforming to ASTM A216, Type WCB, TFE seats and TFE packing, stainless steel (SS410) PTFE coated shafts, matching flanges, locking devices extended flow control lever, insulation, nuts, bolts and neoprene gasket etc. Valve should be suitable for 16 kg or Sq.cm Pressure. Make Advance or Audco or Kirlsokar F 50 mm | Nos. | 4 | 22000 | 7125 | 28500 | 5500 | 22000 | 6500 | 26000
18 | a | Y-STRAINER - SITC of following sizes of Carbon steel type Y-strainer with matching flanges, Staineless steel mesh, bolts, supports etc. Valve should be suitable for 16 kg or Sq.cm. Pressure. F 50 mm | Nos. | 1 | 4650 | 8312.5 | 8312.5 | 5500 | 5500 | 4650 | 4650
19 | a | PIBCV VALVES SITC of Pressure Independent Balancing cum Control Valves (PIBCV) including integrated motorised control valve and balancing device for combined flow and water balancing requirement. Valve body to be rated for PN 16. The valve design flow rate should be factory calibrated with + or - 5% flow accuracy. Valve shall have necessary measuring ports, drain port, flanges etc., Valve shall also provide temperature sensor with necessary cabling (min 5mtr length to be considered with each valve). The balancing to be done through microprocessor based hand held terminal or POT and the same results shall be furnished in the water balancing report as part of commissioning report and handing over manual. F 50 mm | Nos. | 1 | 49400 | 49400 | 49400 | 65000 | 65000 | 75000 | 75000
20 | b | BALL VALVE SITC of following sizes of Brass Ball Valve consist of Cap, matching flanges, bolts, supports, etc. Valve should be suitable for 16 kg or Sq.cm. Pressure. Dia 20 m | Nos. | 2 | 4100 | 3800 | 7600 | 2200 | 4400 | 2050 | 4100
21 | a | Auto Air Vent Valves Providing and fitting Auto Vent Valves. SITC of Auto air vent in each risers common headers AHU. 3 or 4 inch inch auto vent valves at each coil or riser or header | Nos. | 2 | 3000 | 4275 | 8550 | 1500 | 3000 | 2450 | 4900
22 |  | SITC of Pressure gauges Thermometers - Necessary pressure gauges and thermometers 4 inch Dial type.
23 | a | Pressure gauges Range 0-10 Kg or CM2 | Nos. | 2 | 3300 | 7125 | 14250 | 2200 | 4400 | 1650 | 3300
24 | b | Thermometer, Range 0-50 deg C | Nos. | 2 | 2800 | 6935 | 13870 | 1400 | 2800 | 1450 | 2900
25 | c | Thermowells | Nos. | 4 | 2200 | 7790 | 31160 | 550 | 2200 | 1050 | 4200
26 |  | DRAIN PIPING - SITC of UPVC Drain Pipe from unit drain pans to nearest floor drain, complete with all screwed joints and providing fixing in position the necessary elbows, tees, reducers, interconnection, flanges, P-trap, connector to floor trap along with 9mm thick tubular nitrile rubber insulation.
27 | a | 40mm dia. | Rmt. | 10 | 2200 | 299.25 | 2992.5 | 220 | 2200 | 450 | 4500
28 | b | 32mm dia. | Rmt. | 15 | 2700 | 266 | 3990 | 180 | 2700 | 425 | 6375
29 | c | 25mm dia. | Rmt. | 20 | 3200 | 237.5 | 4750 | 160 | 3200 | 390 | 7800
30 |  | NOTES FOR PIPING a Cover all open pipe ends with muslin cloth during construction b Pipe cleaning chemical treatment as per specs shall be included in the piping cost. c Unit rates for all indicated sizes of pipes valves shall be furnished. d Cleaning or Painting of pipe before insulation shall be included in piping cost. e The piping support should be as per tender specification and additional supports are to be provided Contractor as decided by Consultant. f All the valves shall be insulated with the same material as that of Chilled water pipng and cost of insulation for valves shall be considered.
31 | 3 | INDIGENOUS WORK
32 | a | INSTALLATION OF VRF OUT-DOOR UNITS with Controller EEV KIT Installation, Charging, Testing and commissioning of VRF system with Environment friendly refrigerant for the below mentioned system along with controller and EEV kit. This shall include lifting, shifting and positioning of outdoor units, nitrogen leak testing, oil charging, vaccumisation etc., 34H | No. | 1 | 35000 | 42750 | 42750 | 80000 | 80000 | 35000 | 35000
33 | a | VRF REFRIGERANT PIPING FITTING WITH INSULATION SITC of high pressure copper refrigerant piping suitable for R 410a refrigerant of suitable size as required and duly insulated with 19mm thick closed cell elastomeric insulation in tubing form. External Refrigerant piping shall be laid on GI covered cable trays. Piping inside occupied spaces shall be supported using GI ladder type cable trays throughtout. Entire refrigerant piping work be carried out in accordance with the specifications. 10500 CFM AHU with 34HP VRF ODU s Note Referiferant piping shall include liquid + gas pipe with all necessory fittings. Also, the size of the same shall be as per manufactured standard | Rmt | 50 | 121125 | 2422.5 | 121125 | 2500 | 125000 | 3450 | 172500
34 | 3.3 | Additional gas charging - Over and above standard Gas charging quantity | Kg | 25 | 30000 | 1425 | 35625 | 1200 | 30000 | 2450 | 61250
35 |  | REFNET JOINTS - SITC of Special Refrigerant T-joints for VRV units | No | 1 | 2375 | 2375 | 2375 | 4500 | 4500 | 8500 | 8500
36 |  | POWER CABLING - Supply, Laying, Testing Commissioning of Power cabling with PVC armoured copper cable with terminations between ODU and ELCB. Power to ELCB to be provided near each ODU by electrical contractor (Supply to be provided within 3 metres near ODU).
37 | a | 10 sqmm 4 core | Rmt | 100 | 55000 | 1748 | 174800 | 550 | 55000 | 1250 | 125000
38 | c | 8 SWG Copper Wire | Rmt | 200 | 36000 | 1325.25 | 265050 | 180 | 36000 | 1500 | 300000
39 | a | COMMUNICATION CABLE SITC of communication cables between outdoor units and indoor units and Indoor to Indoor units, ODU and Intelligent Touch Controller. 1.5 sqmm 2 cor | Rmt | 90 | 14400 | 237.5 | 21375 | 160 | 14400 | 230 | 20700
40 | b | CABLE TRAYS Supplying Fixing of following sizes of GI cable tray duly painted perforated type of height 75mm along with necessary bends, reducers etc. anchored along the wall or suspended from the ceiling with necessary MS supports. 300mm wide | Rmt | 200 | 130000 | 902.5 | 180500 | 850 | 170000 | 650 | 130000
41 |  | FRAMEWORK FOR VRF ODU - Supply, Fabrication and Installation of MS frame using channels or angle iron sections as required for mounting of air cooled remote condenser in service areas or terrace level. The frame work shall be applied with red oxide primer and thereafter, two coats of enamel paint of approved colour. The general arrangement drawing for frame work shall be got approved from the Architects or Structural Engineers prior to commencement of fabrication. | No. | 2 | 17000 | 13775 | 27550 | 8500 | 17000 | 25000 | 50000
42 | Note : | Quantities of refrigerant piping and cabling are based on the drawings with Indoor Outdoor units Locations shown and for the specified configuration. Vendor to confirm refrigerant piping and cabling quantities based on the system configuration being offered by them.
43 | a | DX DUCTABLE UNITS SITC of Ductable Split units with Inverter compressor and R407c or R410a referigerant gas. The units should be complete with indoor unit, condensing unit, controls, control panel, wiring, refrigerant piping, gas charging, etc. The control cabling and insulated refrigerant piping should be based on the distance between indoor unit and condensing unit being 50 Mtr or Ckt. Unit shall have corded remote. Refrigerant piping slope to be maintained towards condensing unit. Make Bluestar or Carrier or Daikin or Voltas or Bluestar 3.0 TR Ducted unit with condensing units | Nos. | 2 | 169100 | 84550 | 169100 | 115000 | 230000 | 175000 | 350000
44 | a | REFERERANT PIPING WITH 13MM INSULATION SITC of Refrigerant piping with pressure testing, vacuum refrigerant charging with 13mm thick nitrile rubber tubular insulation Piping Make Maxflow or Mandev or Heling Insulation Make Armaflex K-flex 3.0 TR Ducted unit with condensing units | Rmt | 100 | 155000 | 2422.5 | 242250 | 1550 | 155000 | 1850 | 185000
45 |  | POWER CONTROL CABLE Supply, laying, dressing, testing and commissioning of 1100V grade copper conductor, galvanized steel wire or strip armoured XLP, PVC sheathed power and control cables of following sizes to be laid on trays or wall or racks including clamping and earthing as per Specification. Cabling to be provided from starter panel to the individual unit including necessary termination. Make Polycab, KEI Finolex
46 | a | Power Cabling between the MCB`s or MCCB`s and the Air Conditioning unit | Rmt | 20 | 5985 | 299.25 | 5985 | 450 | 9000 | 650 | 13000
47 | b | Control Cabling between indoor outdoor units | Rmt | 120 | 21600 | 233.7 | 28044 | 180 | 21600 | 210 | 25200
48 |  | FRAME WORK Supply, fabrication, installation of MS base frame or platform for outdoor units as mentioned in the drawing which shall be completed with vibration isolation pads, supports, hangers, railing, brackets etc. Construction as approved by Architect or Consultant. Apply 2 coats of paint Finish painting to be as approved by Architect. Outdoor unit structure with access ladder to be provided by A.C contractor | Nos | 2 | 0 | 0 | 0 | 3500 | 7000 | 15000 | 30000
49 |  | MCB FOR DX ODU - SITC of IP65 rated PVC enclosure with 16A TPN MCB For HVAC Outdoor Units | Nos. | 2 | 3000 | 13775 | 27550 | 1500 | 3000 | 4500 | 9000
50 |  | Note All cables conduits to be FRLS. MCCB s earthing of required rating sizes shall be provided by Electrical contractor.
51 | 6 | SHEET METAL WORKS
52 |  | GI SHEET RECTANGULAR METAL DUCTING - Supply, Fabrication, Testing, and Commissioning of Factory Fabricated GI Sheet Metal 180GSM Rectangular boxed ducting, Plenums, Cowls, Elbows with turning vanes, Splitters, Reducers, Flanges, Collars etc as per SMACNA standards, The complete ducting shall be provided with MS Supports, Rods, Angles, Flanges, Bracing, Rubber Gaskets, Wooden frames, Canvas Connections, etc. as per drawings and specifications.
53 | a | 18 Gauge GI Sheet Metal Duct (Above 2001mm Plenum) | Sq.mtr | 15 | 26077.5 | 1738.5 | 26077.5 | 1850 | 27750 | 1950 | 29250
54 | b | 20 Gauge GI Sheet Metal Duct (1101-2000mm) | Sq.mtr | 10 | 15342.5 | 1534.25 | 15342.5 | 1650 | 16500 | 1750 | 17500
55 | c | 22 Gauge GI Sheet Metal Duct (601-1100mm) | Sq.mtr | 250 | 345562.5 | 1382.25 | 345562.5 | 1450 | 362500 | 1550 | 387500
56 | d | 24 Gauge GI Sheet Metal Duct (0-600mm) | Sq.mtr | 300 | 369075 | 1230.25 | 369075 | 1250 | 375000 | 1350 | 405000
57 | a | GI SHEET ROUND METAL DUCTING Supply, Fabrication, Testing, Air Flow Balancing and Commissioning of Factory Fabricated GI Sheet Metal 180GSM Round ducting, Splitters, Flanges, Collars etc as per SMACNA standards. The complete ducting shall be provided with MS Supports, Rods, Angles, Flanges, Bracing, Rubber Gaskets, etc. as per drawings and specifications. 24 Gauge GI Sheet Metal Duct (0-600mm) | Sq.mtr | 25 | 46250 | 1942.75 | 48568.75 | 1850 | 46250 | 1850 | 46250
58 |  | AIR BALANCING LEAK TEST - Air balancing activity with calibrated air hood and subsequent air balancing report with consultants approval for entire project. Also, cost shall include light or smoke test of complete duct length. | Lot | 1 | 15000 | 52250 | 52250 | 15000 | 15000 | 20000 | 20000
59 |  | EXTRUDED ALUMINIUM GRILLES - SITC of Aluminium extruded powder coated 150mm width grilles model EP-00 or 15 or 30 with four side flanges, etc.
60 | a | Linear Grille | Sq.mtr | 10 | 76665 | 7666.5 | 76665 | 8500 | 85000 | 8750 | 87500
61 | b | Curve Grille | Sq.mtr | 3 | 26832.75 | 8944.25 | 26832.75 | 9500 | 28500 | 10430 | 31290
62 |  | EXTRUDED ALUMINIUM CEILING SQUARE DIFFUSER - Supply, Installation, Testing and Balancing of supply return air diffusers as per the approved shop drawings and specifications. Each diffuser shall be equipped with fixed air distribution grid, removable key-operated volume control damper, complete with insulated plenum box. The diffusers shall be anti-smudge ring or flush type. Powder coated extruded aluminium diffusers of approved colour shade of following sizes
63 |  | Supply Air Square Diffuser with Plenum Box Control Damper - 225x225mm Neck Size | Nos. | 4 | 9000 | 3325 | 13300 | 2800 | 11200 | 2250 | 9000
64 |  | Return Air Round Diffuser - 225x225mm Neck Size | No. | 4 | 8000 | 3040 | 12160 | 2000 | 8000 | 2450 | 9800
65 |  | EXTRUDED ALUMINIUM CEILING ROUND DIFFUSER Supply, Installation, Testing and Balancing of supply return air diffusers as per the approved shop drawings and specifications. Each diffuser shall be equipped with fixed air distribution grid, removable key-operated volume control damper, complete with insulated plenum box. The diffusers shall be anti-smudge ring or flush type. Powder coated extruded aluminium diffusers of approved colour shade of following sizes Supply Air Round Diffuser with Plenum Box Control Damper 300mmF Neck Size | Nos. | 2 | 4300 | 3040 | 6080 | 3200 | 6400 | 2150 | 4300
66 |  | MULTI LEAF VOLUME CONTROL DAMPER SITC of opposed blade aerofoil type 1.2 mm thick Anodized Aluminium volume control dampers for ducts shall be provided with concealed gears, plastic operator and quadrants for manual control of volume of air flow and for proper balancing of the air distribution system as per the approved shop drawings and specifications. Makes Dynacraft or Cosmos | Sq.mtr | 2 | 17888.5 | 8944.25 | 17888.5 | 10500 | 21000 | 10500 | 21000
67 |  | OPPOSED BLADE DAMPER - SITC of Aluminium Opposed blade dampers black powder coated vertical blades type for supply air collar. The damper should be gear operated type. | Sq.mtr | 2 | 10920 | 8075 | 16150 | 5500 | 11000 | 5460 | 10920
68 |  | MOTORISED FIRE DAMPER - Supply, installation, testing and commissioning of UL 555 or UL 555 S motorized fire or smoke dampers at wall or floor crossing consist of 2.0 Hours rating, 16G GI frame blade, 20G GI casing, brass bushing for friction free operation, S.S jamb seal for minimum leakage, ON or OFF type actuator with transformer etc. as per specification and approved shop drawings. (Actuators of 24VAC built with Auxiliary switch provides feedback for BMS systems)
69 | a | Fire or Smoke damper | Sq.mtr | 4 | 39865.8 | 9966.45 | 39865.8 | 12500 | 50000 | 18500 | 74000
70 | b | Actuator with trnasformer | Nos. | 7 | 79800 | 11400 | 79800 | 14500 | 101500 | 16500 | 115500
71 | c | Control logic wiring for shutting all fire dampers in each AHU s, when AHU is OFF for any reason. | Lot | 1 | 10000 | 19000 | 19000 | 10000 | 10000 | 15000 | 15000
72 |  | JET NOZZLE Supply, Installation, Testing and Balancing of Powder coated extruded aluminium Jet nozzles with shutter type damper etc. as per the approved shop drawings and specifications. 325mm F Neck Size | Nos. | 30 | 165000 | 6175 | 185250 | 5500 | 165000 | 6250 | 187500
73 | a | DISC VALVE SITC of Aluminium powder coated Disc valve suitable for exhausting toilet foul air, comprising of an adjustable centre cone and coupling sleeve made of Aluminium sheet duly epoxy painted with approved color. 150mmF | Nos. | 18 | 22500 | 1520 | 27360 | 1250 | 22500 | 1850 | 33300
74 |  | PRE-INULATED FLEXIBLE DUCT - SITC of following sizes of insulated flexible ducting with its matching supports, clamps and square to round pieces and other accessories fittings etc. The flexible duct shall me made of triple lamination of aluminium foil, polyester and metalised polyester film permanently bonded to a coated spring steel wire helix. The exterior shall be wrapped with 25mm thick 16 kg or cum fibreglass insulation. The outer insulation jacket or vapour barrier made of fibreglass reinforced metalised polyester film laminate.
75 | a | 350mmF | Rmt | 30 | 22500 | 2337 | 70110 | 750 | 22500 | 1450 | 43500
76 | b | 300mmF | Rmt | 5 | 3250 | 1713.8 | 8569 | 650 | 3250 | 1250 | 6250
77 | c | 250mmF | Rmt | 5 | 2750 | 1402.2 | 7011 | 550 | 2750 | 1150 | 5750
78 | d | 150mmF | Rmt | 20 | 9000 | 1092.5 | 21850 | 450 | 9000 | 1050 | 21000
79 | 6.14 | CANVAS CONNECTION
80 |  | Supply fixing of fire rated flexible Canvas connections between mouth piece and initial piece of ducting with inspection zip.
81 | a | For AHU | Nos | 2 | 5300 | 4750 | 9500 | 3000 | 6000 | 2650 | 5300
82 | b | For Fan | Nos | 2 | 4750 | 2375 | 4750 | 3000 | 6000 | 2850 | 5700
83 |  | NOTES The ducting support should be as per tender specification and additional supports are to be provided by Contractor as decided by Consultant. Muslin cloth cover for all air outlets during construction. Air Flow balancing and Pressure testing of complete duct work as per DW or SMACNA standard. Light testing or smoke testing shall be employed for leaks Silicon sealant for longitudinal transverse joints as per specification. Jet Nozzle, Diffusers grilles shall be powder coated as per color approved by Architect.
84 |  | THERMAL INSULATION FOR DUCTS - Supply fixing of Thermal insulation for supply air duct using 13mm thick class inch O inch Closed cell nitrile rubber with anti-microbial coating on it. Insulation shall have Thermal conductivity of 0.033 W or (m.K) and water vapor permeance of 0.10. Joints should be sealed with 50 mm wide 3 mm thick self adhesive tape. The duct shall be stick with recommended adhesive. | Sq.mtr | 410 | 266500 | 869.25 | 356392.5 | 650 | 266500 | 750 | 307500
85 |  | ACOUSTIC INSULATION FOR DUCTS - Supply fixing acoustic insulation for ducting using Class inch 1 inch closed cell elastomeric insulation of 10mm thick Nitrile rubber insulation adhesive, longitudinal transverse joints sealed with adhesive in neat clean manner. Material shall be processed Nitrile Rubber foam with anti-microbial protection. Insulation shall have thermal conductivity of 0.047 W or (m.K) and density of 140 - 180 kg or m³. | Sq.mtr | 30 | 37500 | 1686.25 | 50587.5 | 1250 | 37500 | 1450 | 43500
86 |  | ACOUSTIC INSULATION FOR AHU ROOM - Supply fixing of Acoustic insulation for plant room using 50mm thick Twiga 300 rigid board stick using shalikote primer and GI frame work. Insulation to be covered with glass fiber cloth finally with 24 G perforated Al. sheet. | Sq.mtr | 75 | 78750 | 2812 | 210900 | 1050 | 78750 | 1250 | 93750
87 |  | Note a. Insulation work to be coordinated with other agencies and repair to be included by contractor as per site requirement. b. Vendors to take care of the installation, if any damages takes place the vendor to repair or replace and hand over to clients in good and acceptable condition. c. Thermal insulation shall be internal for Elliptical or Expossed ducting.
88 | 8 | ELECTRICAL WORKS
89 |  | STARTER PANEL - SITC of indoor or outdoor, wall mounting type 3PH, 415VAC MOTOR STARTERS IN CRCA SHEET STEEL ENCLOSURE with necssary supporting brackets and required accessories, etc., The Enclosure shall be provided with knockouts suitable for cable termination at TOP BOTTOM for incoming and outgoing power cables of A2XFY type and size specified. The starters shall be complete with suitable MPCB or MCCB, Contactor, Bi-metal O or L relay with SPP, ON or OFF Push buttons, on or off or trip indication Lamp, on off push button, phase indication Lamp. Selection of relay, contractor, MPCB or MCCB etc. as per Type-2 Coordination.
90 | a | 11200 CFM AHU - 7.5KW, 3PH, Starter Delta type | No. | 1 | 55000 | 80750 | 80750 | 55000 | 55000 | 125000 | 125000
91 | b | 10500CFM AHU - 7.5KW, 3PH, Starter Delta type | No. | 1 | 55000 | 76000 | 76000 | 55000 | 55000 | 125000 | 125000
92 |  | MCB FOR VRF ODU - SITC of IP65 rated PVC enclosure with 40A TPN MCB For HVAC Outdoor Units | Nos. | 2 | 0 | 0 | 0 | 8500 | 17000 | 6500 | 13000
93 |  | POWER CABLING - Supply, handling, laying effecting proper connections testing and commissioning of following sizes of 1.1 KV grade XLPE insulated FRLS Aluminium or Copper conductor cables laid over MS supports cable racks or fixing on walls including clamping the cable to supports in an approved manner as required complete with Copper earthing as specified for continuous earthing along with cable. All complete as required and as per final instruction as given by Owners or Consultants and as per Technical specifications. Earthing shall be measured separately and shall be connected in two runs. Power to ELCB to be provided near each ODU by electrical contractor.
94 |  | Power Cable CU 6 sqmm 6 core - 7.5KW | Rmt | 20 | 0 | 0 | 0 | 650 | 13000 | 1050 | 21000
95 |  | Earthing 8 SWG GI Earthing | Rmt | 40 | 0 | 0 | 0 | 180 | 7200 | 150 | 6000
96 | a | CABLE TERMINATION Supply Making of Cable termination of armoured or unarmoured cables 1.1 KV grade including installation of cable glands, cable lugs (Aluminium for A2XFY copper for 2XFY YY Double compression type), heat shrinkable sleeves on long ends, crimping paste etc. The work includes testing commissioning of cables, meggaring values submitting reports of tests. (One set includes termination of all cores of one end only). All crimping tools dies shall be arranged by contractor. CU 6 sqmm 6 core - 7.5KW | Nos. | 2 | 0 | 0 | 0 | 550 | 1100 | 3000 | 6000
97 | a | CABLE TRAYS Supplying Fixing of following sizes of GI cable tray duly painted perforated type of height 50mm along with necessary bends, reducers etc. anchored along the wall or suspended from the ceiling with necessary MS supports. 150mm wide | Rmt | 15 | 8250 | 712.5 | 10687.5 | 550 | 8250 | 550 | 8250
3 |  | Kitchen Ventilation High side Work | NOS | 1 | 350000 |  | 1 |  | 350000 |  | 670000
98 |  | Note Prices shall be based on supply, installation, testing commissioning (SITC) at site including all taxes, duties, transportation insurance etc.
99 | 1 | VENTILATION SYSTEM
100 | a | KITCHEN EXHAUST AIR FAN SITC of SISW Centrifugal Blower, Belt Direct Drive, Statically Dynamically Balanced, Backward Curved Impeller fan, Dunlop Anti- Vibration Pads etc. Motor should be outside stream with TEFC squirrel cage, weather protection shield, IP 55 rating with Class F Insulation, suitable for 3phase, 415volts, 50hz power supply. Sound level should be 60dB @ 3mtr distance. Fan should be painted with 2 coat of zinc chromate primer and 2 coats Epoxy paint. The quote shall include with MS frame, starter panel along with its required cable. Supplied with Dunlop Anti- Vibration Pads Canvass Connection. (Vendor to crosscheck static pressure calculation). 5000 CFM, 60mm Static (Class F) | No | 1 | 155000 | 1 | 1 | 155000 | 155000 | 265000 | 265000
101 | a | INDUSTRIAL GRADE ELECTROSTATIC AIR CLEANER SITC of Dry scrubber – Electrostatic Air cleaner with starter panel as per specifications, suitable for following capacities, including electrical starter panel . The Air filtration efficiency should be between 90 to 95% units shall be staked one above other or side by side as per site requirement, if vendor will propose multiple units. Finishing - Power coated, Dark Blue Operating voltage - 220 Vac+ or -10%, 50 Hz (Single phase) Features - Short circuit, arc protection and auto restore power supply, BMS (Building Management System) terminals provided, Auto power cut-off when door is opened, Indicator LEDs for normal or wash indicator, Set of Terminals for remote LED normal or wash indicator Efficiency - Upto 95%, meets NIOSH 5026 Oil Mist Test Particle Size - Collects particles as small as 0.01 microns Motor - Sealead ball bearings UL, single phase. Cell - Ionizing voltage - 12 KVdc Collector voltage - 6 KVdc One cell comprising of 9 ionizing wires and 25 collection plates Controls - Auto cut-off when door is opened. Indicator lights for fault, normal or wash function. Pre-filter - Aluminium mesh, washable Dry contact for BMS. 5000 CFM | No | 1 | 185000 | 0 | 0 | 185000 | 185000 | 345000 | 345000
102 |  | FRAMEWORK FOR FANS - Supply, Fabrication and Installation of MS frame using channels or angle iron sections as required for mounting of ventilation fans scrubber in areas shown in the layout. The frame work shall be applied with red oxide primer and thereafter, two coats of enamel paint of approved colour. The general arrangement drawing for frame work shall be got approved from the Architects or Structural Engineers prior to commencement of fabrication. |  |  | 0
103 | a | Exhaust Fan - 5000CFM | Lot | 1 | 6500 | 0 | 0 | 6500 | 6500 | 35000 | 35000
104 | b | Dry Scrubber - 5000 CFM | Lot | 1 | 3500 | 0 | 0 | 3500 | 3500 | 25000 | 25000
105 |  | Note a. Fan outlet velocity - 1600 FPM b. All cabinet fans should have plenum section. c. Fresh air fan if any,should to have 6mm thick synthetic media washable filter with framework. d. Contractor shall submit static pressure calculation for all above units to Client or Consultant. e. Any change in motor HP or coil selection shall be made at no extra cost to client. f. Fan efficiency shall be minimum 75% g. The cost shall be included liftting shifting of each equipment or material with all necesaary arrnagement. Also, it shall be included the cost of scaffloding required for Installation of such material or equipment. |  |  | 0
4 |  | Kitchen Ventilation Low side Work | NOS | 1 | 566000 |  | 1 |  | 587000 |  | 718500
106 |  | Note Prices shall be based on supply, installation, testing commissioning (SITC) at site including all taxes, duties, transportation insurance etc.
107 |  | SHEET METAL WORKS
108 |  | GI SHEET METAL DUCTING - Supply, Fabrication, Testing, Air Flow Balancing and Commissioning of Factory Fabricated GI Sheet Metal 180GSM Rectangular boxed ducting, Plenums, Cowls, Elbows, Splitters, Reducers, Flanges, Collars etc as per SMACNA standards, The complete ducting shall be provided with MS Supports, Rods, Angles, Flanges, Bracing, Rubber Gaskets, Wooden frames, Canvas Connections, etc. as per drawings and specifications.
109 |  | 22 Gauge GI Sheet Metal Duct (601-1100mm) | Sq.mtr | 50 | 67500 | 0 | 0 | 1450 | 72500 | 1350 | 67500
110 |  | 24 Gauge GI Sheet Metal Duct (0-600mm) | Sq.mtr | 150 | 187500 | 0 | 0 | 1250 | 187500 | 1550 | 232500
111 |  | SS EXHAUST AND FRESH AIR GRILLS - SITC of 18G SS 304 Fresh Air Grilles adjustable Double Deflector With S.S Volume Control Dampers. Grills to be of Double Deflection Type for ease of deflection on all sides. | Sq.mtr | 0.75 | 7875 | 0 | 0 | 22500 | 16875 | 10500 | 7875
112 |  | DOOR TRANSFER GRILLE SITC of Aluminium extruded powder coated Door transfer grills. Door transfer grille (Back to Back) | Sq.mtr | 0.25 | 2625 | 0 | 0 | 10500 | 2625 | 11500 | 2875
113 |  | MULTI LEAF VOLUME CONTROL DAMPER - SITC of opposed blade aerofoil type 1.2 mm thick Anodized Aluminium volume control dampers for ducts shall be provided with concealed gears, plastic operator and quadrants for manual control of volume of air flow and for proper balancing of the air distribution system as per the approved shop drawings and specifications. | Sq.mtr | 2.5 | 23750 | 0 | 0 | 10500 | 26250 | 9500 | 23750
114 |  | CURTAIN TYPE FIRE DAMPER - SITC of curtain type fire dampers consist of 16G GI frame, 20G GI interlocking blades secured with SS springs, blades outside airstream clamped with fusible link UL-555 listed with melting point 165 225°F, etc; as per the approved shop drawings and specifications. |  |  | 0
115 |  | Bare fire dampers | Sq.mtr | 0.3 | 3750 | 0 | 0 | 12500 | 3750 | 16500 | 4950
116 |  | Fusible link as per specification UL 555 and CBRI approved | No. | 1 | 1600 | 1 | 1 | 4500 | 4500 | 1600 | 1600
117 |  | CANVAS CONNECTION - Supply fixing of flexible Canvas connections between mouth piece and initial piece of ducting. Flexible connections shall be fire resistant made of closely woven, double layer canvass neoprene coated fibre glass. |  |  | 0
118 |  | Cabiner Exhaust Fan | Nos | 1 | 3000 | 0 | 0 | 3000 | 3000 | 3250 | 3250
119 |  | Dry Scrubber | Nos | 1 | 3000 | 0 | 0 | 3000 | 3000 | 3500 | 3500
120 |  | NOTES The ducting support should be as per tender specification and additional supports are to be provided by Contractor as decided by Consultant. Muslin cloth cover for all air outlets during construction. Pressure testing of complete duct work as per DW SMACNA standard. Silicon sealant for longitudinal transverse joints as per specification. Diffusers grilles shall be powder coated as per color approved by Architect. |  |  | 0
121 |  | THERMAL INSULATION SITC of Rockwool roll Insulation with stonewool fibres bonded with thermosetting resins, with factory applied laminated Woven Fiber glass cloth of 271GSM. Nominal density 48 Kg CuM. Thermal conductivity, < 0.042 W m.K at 50°C. All Insulation material and adhesives shall be as per Class O for surface spread and in accordance with BS 476, Class O for non-combustible grade. Also, cost shall include all necessary support and accessories. 50 mm Thick | Sq.mtr | 200 | 170000 | 0 | 0 | 850 | 170000 | 1250 | 250000
122 |  | ELECTRICAL WORKS |  |  | 0
123 |  | STARTER PANEL with VFD SITC of indoor outdoor, wall mounting type 3PH, 415VAC MOTOR STARTERS IN CRCA SHEET STEEL ENCLOSURE with necssary supporting brackets and required accessories, etc., The Enclosure shall be provided with knockouts suitable for cable termination at TOP BOTTOM for incoming and outgoing power cables of A2XFY type and size specified. The starters shall be complete with suitable MPCB MCCB, Contactor, Bi-metal O L relay with SPP, ON OFF Push buttons, on off trip indication Lamp, on off push button, phase indication Lamp. Selection of relay, contractor, MPCB MCCB etc. as per Type-2 Coordination. Starter panel shall be BMS compatible. Variable frequency drives shall be provided with necessary sensors and controllers complete with control wiring in all respect as required. VFDs shall be provided with necessary bypass arrangement inside electrical starter panels with IP-55 enclosure. 5.5KW, 3PH, DOL Starter type for exhaust air fan | No | 1 | 75000 | 0 | 0 | 75000 | 75000 | 95000 | 95000
124 |  | POWER CABLING - Supply, handling, laying effecting proper connections testing and commissioning of following sizes of 1.1 KV grade XLPE insulated FRLS Aluminium Copper conductor cables laid over MS supports cable racks or fixing on walls including clamping the cable to supports in an approved manner as required complete with Copper earthing as specified for continuous earthing along with cable. All complete as required and as per final instruction as given by Owners Consultants and as per Technical specifications. Earthing shall be measured separately and shall be connected in two runs. Power to ELCB to be provided near each ODU by electrical contractor. Power Cable |  |  | 0
125 |  | CU 2.5 sqmm 4 core - Exhaust Fan | Rmt | 10 | 3500 | 0 | 0 | 450 | 4500 | 350 | 3500
126 |  | CU 2.5 sqmm 3 core - Dry Scrubber | Rmt | 10 | 1800 | 0 | 0 | 180 | 1800 | 320 | 3200
127 |  | Earthing - 8 SWG GI Earthing | Rmt | 20 | 3000 | 0 | 0 | 180 | 3600 | 150 | 3000
128 |  | CABLE TERMINATION Supply Making of Cable termination of armoured unarmoured cables 1.1 KV grade including installation of cable glands, cable lugs (Aluminium for A2XFY copper for 2XFY YY Double compression type), heat shrinkable sleeves on long ends, crimping paste etc. The work includes testing commissioning of cables, meggaring values submitting reports of tests. (One set includes termination of all cores of one end only). All crimping tools dies shall be arranged by contractor. CU 2.5 sqmm 4 core - Exhaust Fan | Nos. | 2 | 1100 | 0 | 0 | 550 | 1100 | 2500 | 5000
129 |  | CABLE TRAYS Supplying Fixing of following sizes of GI cable tray duly painted perforated type of height 50mm along with necessary bends, reducers etc. anchored along the wall suspended from the ceiling with necessary MS supports. 150mm wide | Rmt | 20 | 11000 | 0 | 0 | 550 | 11000 | 550 | 11000

## Round 4&5
|  | RFQ No: R1359 COST COMPARISON REPORT | RFQ No: R1359 COST COMPARISON REPORT | RFQ No: R1359 COST COMPARISON REPORT | Comp. Date : 06/08/2024 | Comp. Date : 06/08/2024 | Comp. Date : 06/08/2024 | Vendor Name : PIONEER PROJECT SOLUTION (T054969) | [10 empty] | Vendor Name : CRYSTAL AIRCOOL (RV242522537) | [10 empty] | Vendor Name : ANJLE MEP PROJECT PVT LTD (RV242523025)
|  | RFQ No: R1359 COST COMPARISON REPORT | RFQ No: R1359 COST COMPARISON REPORT | RFQ No: R1359 COST COMPARISON REPORT | RFQ #: R1359 | RFQ #: R1359 | RFQ #: R1359 | Contact Name : ASHRAF | [10 empty] | Contact Name : JOHN | [10 empty] | Contact Name : PREMKANT
|  | RFQ No: R1359 COST COMPARISON REPORT | RFQ No: R1359 COST COMPARISON REPORT | RFQ No: R1359 COST COMPARISON REPORT | RFQ Date : 24/07/2024 17:16:44 | RFQ Date : 24/07/2024 17:16:44 | RFQ Date : 24/07/2024 17:16:44 | Vendor City : | [10 empty] | Vendor City : | [10 empty] | Vendor City :
|  | RFQ No: R1359 COST COMPARISON REPORT | RFQ No: R1359 COST COMPARISON REPORT | RFQ No: R1359 COST COMPARISON REPORT | BCD Date : 25/07/2024 14:03:00 | BCD Date : 25/07/2024 14:03:00 | BCD Date : 25/07/2024 14:03:00 | Telephone # : | [10 empty] | Telephone # : | [10 empty] | Telephone # :
|  | RFQ No: R1359 COST COMPARISON REPORT | RFQ No: R1359 COST COMPARISON REPORT | RFQ No: R1359 COST COMPARISON REPORT |  |  |  | Mobile # : 98106 34901 | [10 empty] | Mobile # : | [10 empty] | Mobile # :
PR Number : BLR-2425-00064 | PR Number : BLR-2425-00064 | PR Number : BLR-2425-00064 | PR Number : BLR-2425-00064 | PR Number : BLR-2425-00064 | PR Number : BLR-2425-00064 | PR Number : BLR-2425-00064 | PR Number : BLR-2425-00064 | Email : projectspioneer@gmail.com | [10 empty] | Email : crystalhvac002@gmail.com | [10 empty] | Email : anjlemepprojects@gmail.com
Package / RFQ Name : TFAS / RFQ / BLR-2425-00064 | Package / RFQ Name : TFAS / RFQ / BLR-2425-00064 | Package / RFQ Name : TFAS / RFQ / BLR-2425-00064 | Package / RFQ Name : TFAS / RFQ / BLR-2425-00064 | Package / RFQ Name : TFAS / RFQ / BLR-2425-00064 | Package / RFQ Name : TFAS / RFQ / BLR-2425-00064 | Package / RFQ Name : TFAS / RFQ / BLR-2425-00064 | Package / RFQ Name : TFAS / RFQ / BLR-2425-00064 | Round # : 4 (Auction) | [10 empty] | Round # : 4 (Auction) | [10 empty] | Round # : 4 (Auction)
Buyer : Binu Balachandran / Technical : / Approver : | Buyer : Binu Balachandran / Technical : / Approver : | Buyer : Binu Balachandran / Technical : / Approver : | Buyer : Binu Balachandran / Technical : / Approver : | Buyer : Binu Balachandran / Technical : / Approver : | Buyer : Binu Balachandran / Technical : / Approver : | Buyer : Binu Balachandran / Technical : / Approver : | Buyer : Binu Balachandran / Technical : / Approver : | Quotation Date : |  | Quotation Validity Date : | [5 empty] | Quotation Validity Date : |  |  | Quotation Date : |  | Quotation Validity Date : | [5 empty] | Quotation Validity Date : |  |  | Quotation Date : |  | Quotation Validity Date : | [5 empty] | Quotation Validity Date :
Comp. # : 4 | Comp. # : 4 | Comp. # : 4 | Comp. # : 4 | Comp. # : 4 | Currency :INR | Currency :INR | Currency :INR | Buyer Remark : | [10 empty] | Buyer Remark : | [10 empty] | Buyer Remark :
Comp. # : 4 | Comp. # : 4 | Comp. # : 4 | Comp. # : 4 | Comp. # : 4 | BUDGET PRICE : | .00 |  | Quote Currency : INR | [10 empty] | Quote Currency : INR | [10 empty] | Quote Currency : INR
# | Item Code | Item Description | Unit | Qty | Last PO Details | Lowest Unit Rate | Lowest Vendor | Price | Disc % | GST % | Unit Price | Total | Converted Total (INR) | Disc % | GST % | Technical | Unit Price | Converted Total (INR) | Price | Disc % | GST % | Unit Price | Total | Converted Total (INR) | Disc % | GST % | Technical | Unit Price | Converted Total (INR) | Price | Disc % | GST % | Unit Price | Total | Converted Total (INR) | Disc % | GST % | Technical | Unit Price | Converted Total (INR)
1 |  | HVAC High side Work | NOS | 1 |  | 1765500 | PIONEER PROJECT SOLUTION | 1820500 | 0 | 0 | 1765500 | 1765500 | 1765500 | 0 | 0 |  | 1765500 | 1765500 | 1948220 | 0 | 0 | 1850809 | 1850809 | 1850809 | 0 | 28 |  | 1850809 | 1850809 | 2225500 | 0 | 0 | 2202500 | 2202500 | 2202500 | 0 | 0 |  | 2202500 | 2202500
2 |  | HVAC Low side Work | NOS | 1 |  | 2850800 | PIONEER PROJECT SOLUTION | 3062800 | 0 | 0 | 2850800 | 2850800 | 2850800 | 0 | 0 |  | 2850800 | 2850800 | 4091884 | 0 | 0 | 3887289.8 | 3887289.8 | 3887289.8 | 0 | 18 |  | 3776692.05 | 3776692.05 | 4029985 | 0 | 0 | 3979985 | 3979985 | 3979985 | 0 | 0 |  | 3979985 | 3979985
3 |  | Kitchen Ventilation High side Work | NOS | 1 |  | 1 | CRYSTAL AIRCOOL | 350000 | 0 | 0 | 318000 | 318000 | 318000 | 0 | 0 |  | 318000 | 318000 | 1 | 0 | 0 | 1 | 1 | 1 | 0 | 0 |  | 1 | 1 | 670000 | 0 | 0 | 670000 | 670000 | 670000 | 0 | 0 |  | 670000 | 670000
4 |  | Kitchen Ventilation Low side Work | NOS | 1 |  | 1 | CRYSTAL AIRCOOL | 587000 | 0 | 0 | 551000 | 551000 | 551000 | 0 | 0 |  | 551000 | 551000 | 1 | 0 | 0 | 1 | 1 | 1 | 0 | 0 |  | 1 | 1 | 718500 | 0 | 0 | 711000 | 711000 | 711000 | 0 | 0 |  | 711000 | 711000
Item Total | [8 empty] | 0 | 0 |  | 5485300 | 5485300 | 0 | 0 |  |  | 5485300 |  | 0 | 0 |  | 5738100.8 | 5738100.8 | 0 | 1198031.09 |  |  | 5627503.05 |  | 0 | 0 |  | 7563485 | 7563485 | 0 | 0 |  |  | 7563485
Discount Total Value | [7 empty] | Grand Dis. Amt | 0 |  |  | 0 | 0 | 0 |  |  |  | 0 | Grand Dis. Amt | 0 |  |  | 0 | 0 | 0 |  |  |  | 0 | Grand Dis. Amt | 0 |  |  | 0 | 0 | 0 |  |  |  | 0
GST Total Amount | [11 empty] | 0 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 1198031.09 |  |  |  |  | 0 | 0 |  |  |  |  | 0
Net Landed Cost | [10 empty] | INR | 5485300 | 5485300 |  |  |  | INR | 5485300 |  |  |  | INR | 5738100.8 | 5738100.8 |  |  |  | INR | 6825534.14 |  |  |  | INR | 7563485 | 7563485 |  |  |  | INR | 7563485
Vendor Status | [7 empty] | Round # : 4 (Auction) | Round # : 4 (Auction) | Round # : 5 (RFQ) | Round # : 5 (RFQ)
Sr No. | Vendor Code | Vendor Name | [5 empty] | Status | Remarks | Status | Remarks
1 | T054969 | PIONEER PROJECT SOLUTION | [5 empty] | Participate |  | Participate
2 | RV232419193 | ANJLE MEP PROJECTS PVT LTD | [5 empty] | Not Participate |  | Not Participate
3 | RV242522852 | HAIER INDIA | [5 empty] | Not Participate |  | Not Participate
4 | RV242522537 | CRYSTAL AIRCOOL | [5 empty] | Participate |  | Participate
5 | T054973 | EMPIRE FURNITURES | [5 empty] | Participate |  | Participate
6 | RV242523025 | ANJLE MEP PROJECT PVT LTD | [5 empty] | Participate |  | Participate
7 | T054523 | Gold Fingers | [5 empty] | Participate |  | Participate
8 | RV232419136 | NAS Contracts Private Limited | [5 empty] | Not Participate |  | Not Participate
9 | RV242523149 | INTER CARE ENTERPRISES | [7 empty] | Participate

## BOQ Price Bid
|  | RFQ No: R1359 COST COMPARISON REPORT | RFQ No: R1359 COST COMPARISON REPORT | Comp. Date : 29/07/2024 | Comp. Date : 29/07/2024 | Comp. Date : 29/07/2024 | Vendor Name : PIONEER PROJECT SOLUTION | Vendor Name : PIONEER PROJECT SOLUTION | Vendor Name : CRYSTAL AIRCOOL | Vendor Name : CRYSTAL AIRCOOL | Vendor Name : ANJLE MEP PROJECT PVT LTD | Vendor Name : ANJLE MEP PROJECT PVT LTD
|  | RFQ No: R1359 COST COMPARISON REPORT | RFQ No: R1359 COST COMPARISON REPORT | RFQ #: R1359 | RFQ #: R1359 | RFQ #: R1359 | Contact Name : ASHRAF | Contact Name : ASHRAF | Contact Name : JOHN | Contact Name : JOHN | Contact Name : PREMKANT | Contact Name : PREMKANT
|  | RFQ No: R1359 COST COMPARISON REPORT | RFQ No: R1359 COST COMPARISON REPORT | RFQ Date : 24/07/2024 17:16:44 | RFQ Date : 24/07/2024 17:16:44 | RFQ Date : 24/07/2024 17:16:44 | Vendor City : | Vendor City : | Vendor City : | Vendor City : | Vendor City : | Vendor City :
|  | RFQ No: R1359 COST COMPARISON REPORT | RFQ No: R1359 COST COMPARISON REPORT | BCD Date : 25/07/2024 14:03:00 | BCD Date : 25/07/2024 14:03:00 | BCD Date : 25/07/2024 14:03:00 | Telephone # : | Telephone # : | Telephone # : | Telephone # : | Telephone # : | Telephone # :
|  | RFQ No: R1359 COST COMPARISON REPORT | RFQ No: R1359 COST COMPARISON REPORT |  |  |  | Mobile # : 98106 34901 | Mobile # : 98106 34901 | Mobile # : | Mobile # : | Mobile # : | Mobile # :
PR Number : BLR-2425-00064 | PR Number : BLR-2425-00064 | PR Number : BLR-2425-00064 | PR Number : BLR-2425-00064 | PR Number : BLR-2425-00064 | PR Number : BLR-2425-00064 | PR Number : BLR-2425-00064 | Email : projectspioneer@gmail.com | Email : projectspioneer@gmail.com | Email : crystalhvac002@gmail.com | Email : crystalhvac002@gmail.com | Email : anjlemepprojects@gmail.com | Email : anjlemepprojects@gmail.com
Package / RFQ Name : TFAS / RFQ / BLR-2425-00064 | Package / RFQ Name : TFAS / RFQ / BLR-2425-00064 | Package / RFQ Name : TFAS / RFQ / BLR-2425-00064 | Package / RFQ Name : TFAS / RFQ / BLR-2425-00064 | Package / RFQ Name : TFAS / RFQ / BLR-2425-00064 | Package / RFQ Name : TFAS / RFQ / BLR-2425-00064 | Package / RFQ Name : TFAS / RFQ / BLR-2425-00064 | Round # : 4 (Auction) | Round # : 4 (Auction) |  |  | Round # : 4 (Auction) | Round # : 4 (Auction)
Buyer : Binu Balachandran | Buyer : Binu Balachandran | Buyer : Binu Balachandran | Buyer : Binu Balachandran | Buyer : Binu Balachandran | Buyer : Binu Balachandran | Buyer : Binu Balachandran | Techanical Score : | Techanical Score : |  |  | Techanical Score : | Techanical Score :
Comp. # : 4 | Comp. # : 4 | Comp. # : 4 | Comp. # : 4 | Currency :INR | Currency :INR | Currency :INR | Quotation Date : | Quotation Date : |  |  | Quotation Date : | Quotation Date :
Comp. # : 4 | Comp. # : 4 | Comp. # : 4 | Comp. # : 4 | BUDGET PRICE :.00 | BUDGET PRICE :.00 | BUDGET PRICE :.00 | Quotation Validity Date : | Quotation Validity Date : |  |  | Quotation Validity Date : | Quotation Validity Date :
Sr No. | Item Code | Item Name | Item Description | UOM | Qty | Minimum Amount | Unit Price | Amount |  |  | Unit Price | Amount
1 |  | HVAC High side Work | HVAC High side Work for 080 Domestic lounge Phase -2 | NOS | 1 |  |  | 1820500 |  |  |  | 2225500
1 |  | Note Prices shall be based on supply, installation, testing commissioning (SITC) at site including all taxes, duties, transportation insurance etc. | Note Prices shall be based on supply, installation, testing commissioning (SITC) at site including all taxes, duties, transportation insurance etc.
2 | a | AIR HANDLING UNIT CHW FLOOR MOUNTED AIR HANDLING UNIT SITC of double skin floor mounted AHU with suitable plug type fans with IE3 efficient 3phase motor, UVGI, Moisture eliminators etc. The thickness of panel to be with 42+ -3mm thick PUF Insulation. The coil shall be of hard copper tubes covered by aluminium fins with 13-15 FPI. The AHU to have a SS condensate drain tray which shall be duly insulated with 13mm thick class O nitrile rubber insulation. The contractor to furnish the GA drawings of AHU prior to ordering with necessary technical catalogues and fan curve selections. The noise level near the AHU should not cross more than 60dbA at 1m away from the unit. Also the AHU shall have a prefilter of MERV 8 with necessary framework. AHU body frame shall be with Aluminium . AHU shall have TEFC Squirrel Cage IP 55 Protected VFD Compatible induction motor, copper header, Copper to MS adopter, vibration isolation pad. Scope also includes limit switch with lights inside AHU. AHUs shall be selected for a maximum face velocity of 500 FPM (2.5MPS) and as per schedule of air handling units. Fan outlet velocity shall not exceed 1600 FPM (8.12 MPS). Chilled water inlet Outlet temp to be 8 13.5°C. AHUs shall be of following design parameters Capacity Tonnage ESP No. of USGPM (Cfm) TR (mm WG) Rows 11200 25 40 4 6 60 | AIR HANDLING UNIT CHW FLOOR MOUNTED AIR HANDLING UNIT SITC of double skin floor mounted AHU with suitable plug type fans with IE3 efficient 3phase motor, UVGI, Moisture eliminators etc. The thickness of panel to be with 42+ -3mm thick PUF Insulation. The coil shall be of hard copper tubes covered by aluminium fins with 13-15 FPI. The AHU to have a SS condensate drain tray which shall be duly insulated with 13mm thick class O nitrile rubber insulation. The contractor to furnish the GA drawings of AHU prior to ordering with necessary technical catalogues and fan curve selections. The noise level near the AHU should not cross more than 60dbA at 1m away from the unit. Also the AHU shall have a prefilter of MERV 8 with necessary framework. AHU body frame shall be with Aluminium . AHU shall have TEFC Squirrel Cage IP 55 Protected VFD Compatible induction motor, copper header, Copper to MS adopter, vibration isolation pad. Scope also includes limit switch with lights inside AHU. AHUs shall be selected for a maximum face velocity of 500 FPM (2.5MPS) and as per schedule of air handling units. Fan outlet velocity shall not exceed 1600 FPM (8.12 MPS). Chilled water inlet Outlet temp to be 8 13.5°C. AHUs shall be of following design parameters Capacity Tonnage ESP No. of USGPM (Cfm) TR (mm WG) Rows 11200 25 40 4 6 60 | No | 1 |  | 450000 | 450000 |  |  | 675000 | 675000
3 | a | VRF FLOOR MOUNTED AIR HANDLING UNIT SITC of double skin floor mounted AHU with suitable plug type fans with rated 3phase motor. The thickness of panel to be with 42+ -3mm thick PUF Insulation. The coil shall be of hard copper tubes covered by aluminium fins with 13-15 FPI. The AHU to have a SS condensate drain tray which shall be duly insulated with 13mm thick class O nitrile rubber insulation. The contractor to furnish the GA drawings of AHU prior to ordering with necessary technical catalogues and fan curve selections. The noise level near the AHU should not cross more than 60-65dbA at 3m away from the unit. Also the AHU shall have a prefilter of MERV 8 with necessary framework. AHU body frame shall be with Aluminium. AHU shall have TEFC Squirrel Cage IP 55 Protected VFD Compatible induction motor, and vibration isolation pads. Scope also includes limit switch with lights in AHU. Cooling Coil section with AHRI certified Coil (0.15mm AL 13 FPI fins 12.7 mm OD 27 SWG Cu Tube) suitable for VRF Outdoor Unit (R410a refrigerant). AHUs shall be selected for a maximum face velocity of 500 FPM (2.5MPS) and as per schedule of air handling units. Fan outlet velocity shall not exceed 1600 FPM (8.12 MPS). AHUs shall be of following design parameters Capacity Tonnage ESP No. of (Cfm) TR (mm WG) Rows 10500 27 40 4 6 | VRF FLOOR MOUNTED AIR HANDLING UNIT SITC of double skin floor mounted AHU with suitable plug type fans with rated 3phase motor. The thickness of panel to be with 42+ -3mm thick PUF Insulation. The coil shall be of hard copper tubes covered by aluminium fins with 13-15 FPI. The AHU to have a SS condensate drain tray which shall be duly insulated with 13mm thick class O nitrile rubber insulation. The contractor to furnish the GA drawings of AHU prior to ordering with necessary technical catalogues and fan curve selections. The noise level near the AHU should not cross more than 60-65dbA at 3m away from the unit. Also the AHU shall have a prefilter of MERV 8 with necessary framework. AHU body frame shall be with Aluminium. AHU shall have TEFC Squirrel Cage IP 55 Protected VFD Compatible induction motor, and vibration isolation pads. Scope also includes limit switch with lights in AHU. Cooling Coil section with AHRI certified Coil (0.15mm AL 13 FPI fins 12.7 mm OD 27 SWG Cu Tube) suitable for VRF Outdoor Unit (R410a refrigerant). AHUs shall be selected for a maximum face velocity of 500 FPM (2.5MPS) and as per schedule of air handling units. Fan outlet velocity shall not exceed 1600 FPM (8.12 MPS). AHUs shall be of following design parameters Capacity Tonnage ESP No. of (Cfm) TR (mm WG) Rows 10500 27 40 4 6 | No. | 1 |  | 425000 | 425000 |  |  | 635000 | 635000
4 | a | SUPPLY OF VRF OUT-DOOR UNITS Supply of air cooled variable refrigerant flow modular type ODUs each comprising of multiple rotary scroll compressors fully inverter driven, full charge of refrigerant gas (R-410a), lubricating oil and all accessories as per the specifications. TheODUs shall be suitable for operation on 415 ± 10% volts, 50Hz, 3 phase AC power supply and the condensing units shall be of following capacities OUTDOOR UNITS 34 HP at site conditions. Note The unit shall be selected taking indoor and ambient deration, refrigerant pipe length deration in to account. | SUPPLY OF VRF OUT-DOOR UNITS Supply of air cooled variable refrigerant flow modular type ODUs each comprising of multiple rotary scroll compressors fully inverter driven, full charge of refrigerant gas (R-410a), lubricating oil and all accessories as per the specifications. TheODUs shall be suitable for operation on 415 ± 10% volts, 50Hz, 3 phase AC power supply and the condensing units shall be of following capacities OUTDOOR UNITS 34 HP at site conditions. Note The unit shall be selected taking indoor and ambient deration, refrigerant pipe length deration in to account. | No. | 1 |  | 695000 | 695000 |  |  | 755000 | 755000
5 |  | AHU CONTROLLER AND EEV KIT - Supply of AHU Controller, Electronic Expansion Valve (EEV) Kit and all other necessary accessories to connect with VRF ODU s. | AHU CONTROLLER AND EEV KIT - Supply of AHU Controller, Electronic Expansion Valve (EEV) Kit and all other necessary accessories to connect with VRF ODU s. | No. | 1 |  | 65000 | 65000 |  |  | 25000 | 25000
6 |  | FRAME WORK - Supply, fabrication and installation of PCC Siporex blocks for AHU support. AHU framework shall be part of AHU supply. Each AHU shall require 9nos. of blocks. | FRAME WORK - Supply, fabrication and installation of PCC Siporex blocks for AHU support. AHU framework shall be part of AHU supply. Each AHU shall require 9nos. of blocks. | Sets | 3 |  | 25000 | 75000 |  |  | 15000 | 45000
7 |  | SPARE FILTER - One set of MERV 8 throw away type filters to be provided for all AHUs. These filters will be used for commissioning. Original set of filters will be installed as instructed by Architect Consultants. | SPARE FILTER - One set of MERV 8 throw away type filters to be provided for all AHUs. These filters will be used for commissioning. Original set of filters will be installed as instructed by Architect Consultants. | Sets | 2 |  | 35000 | 70000 |  |  | 18500 | 37000
8 |  | GENERAL NOTES a. Fan outlet velocity - 1600 FPM b. Contractor shall submit static pressure calculation for all above units to Client Consultant. c. Any change in motor HP shall be made at no extra cost to client. d. Fan efficiency shall be minimum 75% e. The cost shall be included liftting shifting of each equipment material with all necesaary arrnagement. Also, it shall be included the cost of scaffloding required for Installation of such material equipment. | GENERAL NOTES a. Fan outlet velocity - 1600 FPM b. Contractor shall submit static pressure calculation for all above units to Client Consultant. c. Any change in motor HP shall be made at no extra cost to client. d. Fan efficiency shall be minimum 75% e. The cost shall be included liftting shifting of each equipment material with all necesaary arrnagement. Also, it shall be included the cost of scaffloding required for Installation of such material equipment.
9 |  | VENTILATION SYSTEM INLINE CIRCULAR FAN SITC of Inline Circular fan (silent type) with speed control, direct drive package - motor with outlet dampers, fan inlet outlet flexible connection, hanging arrangement with vibration isolators etc. Power will be provided 5 ft away from fan and necessary control wiring with plug will be provided by AC contractor. Motor efficiency IE2 IE3, AMCA Certification and Noise levels at 1m distance to be specified.The fans shall have BMS Compatibility. | VENTILATION SYSTEM INLINE CIRCULAR FAN SITC of Inline Circular fan (silent type) with speed control, direct drive package - motor with outlet dampers, fan inlet outlet flexible connection, hanging arrangement with vibration isolators etc. Power will be provided 5 ft away from fan and necessary control wiring with plug will be provided by AC contractor. Motor efficiency IE2 IE3, AMCA Certification and Noise levels at 1m distance to be specified.The fans shall have BMS Compatibility.
10 | a | 700 CFM @ 25 mmwg ESP | 700 CFM @ 25 mmwg ESP | Nos | 2 |  | 16500 | 33000 |  |  | 20500 | 41000
11 | b | 100 CFM @ 15 mmwg ESP | 100 CFM @ 15 mmwg ESP | No | 1 |  | 7500 | 7500 |  |  | 12500 | 12500
12 |  | NOTES a. Contractor shall submit static pressure calculation for all above units to Client Consultant. b. Any change in motor HP shall be made at no extra cost to client. c. The cost shall be included liftting shifting of each equipment material with all necesaary arrnagement. Also, it shall be included the cost of scaffloding required for Installation of such material equipment. | NOTES a. Contractor shall submit static pressure calculation for all above units to Client Consultant. b. Any change in motor HP shall be made at no extra cost to client. c. The cost shall be included liftting shifting of each equipment material with all necesaary arrnagement. Also, it shall be included the cost of scaffloding required for Installation of such material equipment.
2 |  | HVAC Low side Work | HVAC Low side Work for 080 Domestic lounge Phase -2 | NOS | 1 |  |  | 3062800 |  |  |  | 4029985
13 |  | Note Prices shall be based on supply, installation, testing commissioning (SITC) at site including all taxes, duties, transportation insurance etc. | Note Prices shall be based on supply, installation, testing commissioning (SITC) at site including all taxes, duties, transportation insurance etc.
14 | 2.1 | CHILLED WATER PIPING WITH INSULATION | CHILLED WATER PIPING WITH INSULATION
15 |  | CHW PIPE SITC of MS Heavy duty class C ERW Chilled Water pipe conforming to IS 1239 - 2004 primer painted including bends, tees, MS supports, PUFF saddles, anchor fasteners, steel angles and any other material required to complete the work. The piping flange connection bolts, washers and nuts should be hot dipped galvanised. Flourscent Plastic Sticker or paint shall be applied to indicate Water flow directions. Only End flanges to be used for capping of pipes. inch inch Table E inch inch of BS code for flange thickness to be adhered. Dia 50 mm | CHW PIPE SITC of MS Heavy duty class C ERW Chilled Water pipe conforming to IS 1239 - 2004 primer painted including bends, tees, MS supports, PUFF saddles, anchor fasteners, steel angles and any other material required to complete the work. The piping flange connection bolts, washers and nuts should be hot dipped galvanised. Flourscent Plastic Sticker or paint shall be applied to indicate Water flow directions. Only End flanges to be used for capping of pipes. inch inch Table E inch inch of BS code for flange thickness to be adhered. Dia 50 mm | Rmt | 15 |  | 1650 | 24750 |  |  | 1250 | 18750
16 |  | CHILLED WATER PIPING INSULATION SITC of insulation for chilled water. piping. For internal pipe - Stick 25mm thick Nitrile rubber Insulation with anti microbial coating, sealing all joints. putting all joints at 300 mm intervals with PVC bands and finally sealing with 3M glass cloth vapour barrier. Dia 50 mm | CHILLED WATER PIPING INSULATION SITC of insulation for chilled water. piping. For internal pipe - Stick 25mm thick Nitrile rubber Insulation with anti microbial coating, sealing all joints. putting all joints at 300 mm intervals with PVC bands and finally sealing with 3M glass cloth vapour barrier. Dia 50 mm | Rmt | 15 |  | 750 | 11250 |  |  | 750 | 11250
17 | a | BUTTERFLY VALVES SITC of CI Butterfly valves shall be wafer type, bi-directional Butterfly valves MSS SP-67; ANSI Class 150 carbon steel body conforming to ASTM A216, Type WCB, TFE seats and TFE packing, stainless steel (SS410) PTFE coated shafts, matching flanges, locking devices extended flow control lever, insulation, nuts, bolts and neoprene gasket etc. Valve should be suitable for 16 kg or Sq.cm Pressure. Make Advance or Audco or Kirlsokar F 50 mm | BUTTERFLY VALVES SITC of CI Butterfly valves shall be wafer type, bi-directional Butterfly valves MSS SP-67; ANSI Class 150 carbon steel body conforming to ASTM A216, Type WCB, TFE seats and TFE packing, stainless steel (SS410) PTFE coated shafts, matching flanges, locking devices extended flow control lever, insulation, nuts, bolts and neoprene gasket etc. Valve should be suitable for 16 kg or Sq.cm Pressure. Make Advance or Audco or Kirlsokar F 50 mm | Nos. | 4 |  | 5500 | 22000 |  |  | 6500 | 26000
18 | a | Y-STRAINER - SITC of following sizes of Carbon steel type Y-strainer with matching flanges, Staineless steel mesh, bolts, supports etc. Valve should be suitable for 16 kg or Sq.cm. Pressure. F 50 mm | Y-STRAINER - SITC of following sizes of Carbon steel type Y-strainer with matching flanges, Staineless steel mesh, bolts, supports etc. Valve should be suitable for 16 kg or Sq.cm. Pressure. F 50 mm | Nos. | 1 |  | 5500 | 5500 |  |  | 4650 | 4650
19 | a | PIBCV VALVES SITC of Pressure Independent Balancing cum Control Valves (PIBCV) including integrated motorised control valve and balancing device for combined flow and water balancing requirement. Valve body to be rated for PN 16. The valve design flow rate should be factory calibrated with + or - 5% flow accuracy. Valve shall have necessary measuring ports, drain port, flanges etc., Valve shall also provide temperature sensor with necessary cabling (min 5mtr length to be considered with each valve). The balancing to be done through microprocessor based hand held terminal or POT and the same results shall be furnished in the water balancing report as part of commissioning report and handing over manual. F 50 mm | PIBCV VALVES SITC of Pressure Independent Balancing cum Control Valves (PIBCV) including integrated motorised control valve and balancing device for combined flow and water balancing requirement. Valve body to be rated for PN 16. The valve design flow rate should be factory calibrated with + or - 5% flow accuracy. Valve shall have necessary measuring ports, drain port, flanges etc., Valve shall also provide temperature sensor with necessary cabling (min 5mtr length to be considered with each valve). The balancing to be done through microprocessor based hand held terminal or POT and the same results shall be furnished in the water balancing report as part of commissioning report and handing over manual. F 50 mm | Nos. | 1 |  | 65000 | 65000 |  |  | 75000 | 75000
20 | b | BALL VALVE SITC of following sizes of Brass Ball Valve consist of Cap, matching flanges, bolts, supports, etc. Valve should be suitable for 16 kg or Sq.cm. Pressure. Dia 20 m | BALL VALVE SITC of following sizes of Brass Ball Valve consist of Cap, matching flanges, bolts, supports, etc. Valve should be suitable for 16 kg or Sq.cm. Pressure. Dia 20 m | Nos. | 2 |  | 2200 | 4400 |  |  | 2050 | 4100
21 | a | Auto Air Vent Valves Providing and fitting Auto Vent Valves. SITC of Auto air vent in each risers common headers AHU. 3 or 4 inch inch auto vent valves at each coil or riser or header | Auto Air Vent Valves Providing and fitting Auto Vent Valves. SITC of Auto air vent in each risers common headers AHU. 3 or 4 inch inch auto vent valves at each coil or riser or header | Nos. | 2 |  | 1500 | 3000 |  |  | 2450 | 4900
22 |  | SITC of Pressure gauges Thermometers - Necessary pressure gauges and thermometers 4 inch Dial type. | SITC of Pressure gauges Thermometers - Necessary pressure gauges and thermometers 4 inch Dial type.
23 | a | Pressure gauges Range 0-10 Kg or CM2 | Pressure gauges Range 0-10 Kg or CM2 | Nos. | 2 |  | 2200 | 4400 |  |  | 1650 | 3300
24 | b | Thermometer, Range 0-50 deg C | Thermometer, Range 0-50 deg C | Nos. | 2 |  | 1400 | 2800 |  |  | 1450 | 2900
25 | c | Thermowells | Thermowells | Nos. | 4 |  | 550 | 2200 |  |  | 1050 | 4200
26 |  | DRAIN PIPING - SITC of UPVC Drain Pipe from unit drain pans to nearest floor drain, complete with all screwed joints and providing fixing in position the necessary elbows, tees, reducers, interconnection, flanges, P-trap, connector to floor trap along with 9mm thick tubular nitrile rubber insulation. | DRAIN PIPING - SITC of UPVC Drain Pipe from unit drain pans to nearest floor drain, complete with all screwed joints and providing fixing in position the necessary elbows, tees, reducers, interconnection, flanges, P-trap, connector to floor trap along with 9mm thick tubular nitrile rubber insulation.
27 | a | 40mm dia. | 40mm dia. | Rmt. | 10 |  | 220 | 2200 |  |  | 450 | 4500
28 | b | 32mm dia. | 32mm dia. | Rmt. | 15 |  | 180 | 2700 |  |  | 425 | 6375
29 | c | 25mm dia. | 25mm dia. | Rmt. | 20 |  | 160 | 3200 |  |  | 390 | 7800
30 |  | NOTES FOR PIPING a Cover all open pipe ends with muslin cloth during construction b Pipe cleaning chemical treatment as per specs shall be included in the piping cost. c Unit rates for all indicated sizes of pipes valves shall be furnished. d Cleaning or Painting of pipe before insulation shall be included in piping cost. e The piping support should be as per tender specification and additional supports are to be provided Contractor as decided by Consultant. f All the valves shall be insulated with the same material as that of Chilled water pipng and cost of insulation for valves shall be considered. | NOTES FOR PIPING a Cover all open pipe ends with muslin cloth during construction b Pipe cleaning chemical treatment as per specs shall be included in the piping cost. c Unit rates for all indicated sizes of pipes valves shall be furnished. d Cleaning or Painting of pipe before insulation shall be included in piping cost. e The piping support should be as per tender specification and additional supports are to be provided Contractor as decided by Consultant. f All the valves shall be insulated with the same material as that of Chilled water pipng and cost of insulation for valves shall be considered.
31 | 3 | INDIGENOUS WORK | INDIGENOUS WORK
32 | a | INSTALLATION OF VRF OUT-DOOR UNITS with Controller EEV KIT Installation, Charging, Testing and commissioning of VRF system with Environment friendly refrigerant for the below mentioned system along with controller and EEV kit. This shall include lifting, shifting and positioning of outdoor units, nitrogen leak testing, oil charging, vaccumisation etc., 34H | INSTALLATION OF VRF OUT-DOOR UNITS with Controller EEV KIT Installation, Charging, Testing and commissioning of VRF system with Environment friendly refrigerant for the below mentioned system along with controller and EEV kit. This shall include lifting, shifting and positioning of outdoor units, nitrogen leak testing, oil charging, vaccumisation etc., 34H | No. | 1 |  | 80000 | 80000 |  |  | 35000 | 35000
33 | a | VRF REFRIGERANT PIPING FITTING WITH INSULATION SITC of high pressure copper refrigerant piping suitable for R 410a refrigerant of suitable size as required and duly insulated with 19mm thick closed cell elastomeric insulation in tubing form. External Refrigerant piping shall be laid on GI covered cable trays. Piping inside occupied spaces shall be supported using GI ladder type cable trays throughtout. Entire refrigerant piping work be carried out in accordance with the specifications. 10500 CFM AHU with 34HP VRF ODU s Note Referiferant piping shall include liquid + gas pipe with all necessory fittings. Also, the size of the same shall be as per manufactured standard | VRF REFRIGERANT PIPING FITTING WITH INSULATION SITC of high pressure copper refrigerant piping suitable for R 410a refrigerant of suitable size as required and duly insulated with 19mm thick closed cell elastomeric insulation in tubing form. External Refrigerant piping shall be laid on GI covered cable trays. Piping inside occupied spaces shall be supported using GI ladder type cable trays throughtout. Entire refrigerant piping work be carried out in accordance with the specifications. 10500 CFM AHU with 34HP VRF ODU s Note Referiferant piping shall include liquid + gas pipe with all necessory fittings. Also, the size of the same shall be as per manufactured standard | Rmt | 50 |  | 2500 | 125000 |  |  | 3450 | 172500
34 | 3.3 | Additional gas charging - Over and above standard Gas charging quantity | Additional gas charging - Over and above standard Gas charging quantity | Kg | 25 |  | 1200 | 30000 |  |  | 2450 | 61250
35 |  | REFNET JOINTS - SITC of Special Refrigerant T-joints for VRV units | REFNET JOINTS - SITC of Special Refrigerant T-joints for VRV units | No | 1 |  | 4500 | 4500 |  |  | 8500 | 8500
36 |  | POWER CABLING - Supply, Laying, Testing Commissioning of Power cabling with PVC armoured copper cable with terminations between ODU and ELCB. Power to ELCB to be provided near each ODU by electrical contractor (Supply to be provided within 3 metres near ODU). | POWER CABLING - Supply, Laying, Testing Commissioning of Power cabling with PVC armoured copper cable with terminations between ODU and ELCB. Power to ELCB to be provided near each ODU by electrical contractor (Supply to be provided within 3 metres near ODU).
37 | a | 10 sqmm 4 core | 10 sqmm 4 core | Rmt | 100 |  | 550 | 55000 |  |  | 1250 | 125000
38 | c | 8 SWG Copper Wire | 8 SWG Copper Wire | Rmt | 200 |  | 180 | 36000 |  |  | 1500 | 300000
39 | a | COMMUNICATION CABLE SITC of communication cables between outdoor units and indoor units and Indoor to Indoor units, ODU and Intelligent Touch Controller. 1.5 sqmm 2 cor | COMMUNICATION CABLE SITC of communication cables between outdoor units and indoor units and Indoor to Indoor units, ODU and Intelligent Touch Controller. 1.5 sqmm 2 cor | Rmt | 90 |  | 160 | 14400 |  |  | 230 | 20700
40 | b | CABLE TRAYS Supplying Fixing of following sizes of GI cable tray duly painted perforated type of height 75mm along with necessary bends, reducers etc. anchored along the wall or suspended from the ceiling with necessary MS supports. 300mm wide | CABLE TRAYS Supplying Fixing of following sizes of GI cable tray duly painted perforated type of height 75mm along with necessary bends, reducers etc. anchored along the wall or suspended from the ceiling with necessary MS supports. 300mm wide | Rmt | 200 |  | 850 | 170000 |  |  | 650 | 130000
41 |  | FRAMEWORK FOR VRF ODU - Supply, Fabrication and Installation of MS frame using channels or angle iron sections as required for mounting of air cooled remote condenser in service areas or terrace level. The frame work shall be applied with red oxide primer and thereafter, two coats of enamel paint of approved colour. The general arrangement drawing for frame work shall be got approved from the Architects or Structural Engineers prior to commencement of fabrication. | FRAMEWORK FOR VRF ODU - Supply, Fabrication and Installation of MS frame using channels or angle iron sections as required for mounting of air cooled remote condenser in service areas or terrace level. The frame work shall be applied with red oxide primer and thereafter, two coats of enamel paint of approved colour. The general arrangement drawing for frame work shall be got approved from the Architects or Structural Engineers prior to commencement of fabrication. | No. | 2 |  | 8500 | 17000 |  |  | 25000 | 50000
42 | Note : | Quantities of refrigerant piping and cabling are based on the drawings with Indoor Outdoor units Locations shown and for the specified configuration. Vendor to confirm refrigerant piping and cabling quantities based on the system configuration being offered by them. | Quantities of refrigerant piping and cabling are based on the drawings with Indoor Outdoor units Locations shown and for the specified configuration. Vendor to confirm refrigerant piping and cabling quantities based on the system configuration being offered by them.
43 | a | DX DUCTABLE UNITS SITC of Ductable Split units with Inverter compressor and R407c or R410a referigerant gas. The units should be complete with indoor unit, condensing unit, controls, control panel, wiring, refrigerant piping, gas charging, etc. The control cabling and insulated refrigerant piping should be based on the distance between indoor unit and condensing unit being 50 Mtr or Ckt. Unit shall have corded remote. Refrigerant piping slope to be maintained towards condensing unit. Make Bluestar or Carrier or Daikin or Voltas or Bluestar 3.0 TR Ducted unit with condensing units | DX DUCTABLE UNITS SITC of Ductable Split units with Inverter compressor and R407c or R410a referigerant gas. The units should be complete with indoor unit, condensing unit, controls, control panel, wiring, refrigerant piping, gas charging, etc. The control cabling and insulated refrigerant piping should be based on the distance between indoor unit and condensing unit being 50 Mtr or Ckt. Unit shall have corded remote. Refrigerant piping slope to be maintained towards condensing unit. Make Bluestar or Carrier or Daikin or Voltas or Bluestar 3.0 TR Ducted unit with condensing units | Nos. | 2 |  | 115000 | 230000 |  |  | 175000 | 350000
44 | a | REFERERANT PIPING WITH 13MM INSULATION SITC of Refrigerant piping with pressure testing, vacuum refrigerant charging with 13mm thick nitrile rubber tubular insulation Piping Make Maxflow or Mandev or Heling Insulation Make Armaflex K-flex 3.0 TR Ducted unit with condensing units | REFERERANT PIPING WITH 13MM INSULATION SITC of Refrigerant piping with pressure testing, vacuum refrigerant charging with 13mm thick nitrile rubber tubular insulation Piping Make Maxflow or Mandev or Heling Insulation Make Armaflex K-flex 3.0 TR Ducted unit with condensing units | Rmt | 100 |  | 1550 | 155000 |  |  | 1850 | 185000
45 |  | POWER CONTROL CABLE Supply, laying, dressing, testing and commissioning of 1100V grade copper conductor, galvanized steel wire or strip armoured XLP, PVC sheathed power and control cables of following sizes to be laid on trays or wall or racks including clamping and earthing as per Specification. Cabling to be provided from starter panel to the individual unit including necessary termination. Make Polycab, KEI Finolex | POWER CONTROL CABLE Supply, laying, dressing, testing and commissioning of 1100V grade copper conductor, galvanized steel wire or strip armoured XLP, PVC sheathed power and control cables of following sizes to be laid on trays or wall or racks including clamping and earthing as per Specification. Cabling to be provided from starter panel to the individual unit including necessary termination. Make Polycab, KEI Finolex
46 | a | Power Cabling between the MCB`s or MCCB`s and the Air Conditioning unit | Power Cabling between the MCB`s or MCCB`s and the Air Conditioning unit | Rmt | 20 |  | 450 | 9000 |  |  | 650 | 13000
47 | b | Control Cabling between indoor outdoor units | Control Cabling between indoor outdoor units | Rmt | 120 |  | 180 | 21600 |  |  | 210 | 25200
48 |  | FRAME WORK Supply, fabrication, installation of MS base frame or platform for outdoor units as mentioned in the drawing which shall be completed with vibration isolation pads, supports, hangers, railing, brackets etc. Construction as approved by Architect or Consultant. Apply 2 coats of paint Finish painting to be as approved by Architect. Outdoor unit structure with access ladder to be provided by A.C contractor | FRAME WORK Supply, fabrication, installation of MS base frame or platform for outdoor units as mentioned in the drawing which shall be completed with vibration isolation pads, supports, hangers, railing, brackets etc. Construction as approved by Architect or Consultant. Apply 2 coats of paint Finish painting to be as approved by Architect. Outdoor unit structure with access ladder to be provided by A.C contractor | Nos | 2 |  | 3500 | 7000 |  |  | 15000 | 30000
49 |  | MCB FOR DX ODU - SITC of IP65 rated PVC enclosure with 16A TPN MCB For HVAC Outdoor Units | MCB FOR DX ODU - SITC of IP65 rated PVC enclosure with 16A TPN MCB For HVAC Outdoor Units | Nos. | 2 |  | 1500 | 3000 |  |  | 4500 | 9000
50 |  | Note All cables conduits to be FRLS. MCCB s earthing of required rating sizes shall be provided by Electrical contractor. | Note All cables conduits to be FRLS. MCCB s earthing of required rating sizes shall be provided by Electrical contractor.
51 | 6 | SHEET METAL WORKS | SHEET METAL WORKS
52 |  | GI SHEET RECTANGULAR METAL DUCTING - Supply, Fabrication, Testing, and Commissioning of Factory Fabricated GI Sheet Metal 180GSM Rectangular boxed ducting, Plenums, Cowls, Elbows with turning vanes, Splitters, Reducers, Flanges, Collars etc as per SMACNA standards, The complete ducting shall be provided with MS Supports, Rods, Angles, Flanges, Bracing, Rubber Gaskets, Wooden frames, Canvas Connections, etc. as per drawings and specifications. | GI SHEET RECTANGULAR METAL DUCTING - Supply, Fabrication, Testing, and Commissioning of Factory Fabricated GI Sheet Metal 180GSM Rectangular boxed ducting, Plenums, Cowls, Elbows with turning vanes, Splitters, Reducers, Flanges, Collars etc as per SMACNA standards, The complete ducting shall be provided with MS Supports, Rods, Angles, Flanges, Bracing, Rubber Gaskets, Wooden frames, Canvas Connections, etc. as per drawings and specifications.
53 | a | 18 Gauge GI Sheet Metal Duct (Above 2001mm Plenum) | 18 Gauge GI Sheet Metal Duct (Above 2001mm Plenum) | Sq.mtr | 15 |  | 1850 | 27750 |  |  | 1950 | 29250
54 | b | 20 Gauge GI Sheet Metal Duct (1101-2000mm) | 20 Gauge GI Sheet Metal Duct (1101-2000mm) | Sq.mtr | 10 |  | 1650 | 16500 |  |  | 1750 | 17500
55 | c | 22 Gauge GI Sheet Metal Duct (601-1100mm) | 22 Gauge GI Sheet Metal Duct (601-1100mm) | Sq.mtr | 250 |  | 1450 | 362500 |  |  | 1550 | 387500
56 | d | 24 Gauge GI Sheet Metal Duct (0-600mm) | 24 Gauge GI Sheet Metal Duct (0-600mm) | Sq.mtr | 300 |  | 1250 | 375000 |  |  | 1350 | 405000
57 | a | GI SHEET ROUND METAL DUCTING Supply, Fabrication, Testing, Air Flow Balancing and Commissioning of Factory Fabricated GI Sheet Metal 180GSM Round ducting, Splitters, Flanges, Collars etc as per SMACNA standards. The complete ducting shall be provided with MS Supports, Rods, Angles, Flanges, Bracing, Rubber Gaskets, etc. as per drawings and specifications. 24 Gauge GI Sheet Metal Duct (0-600mm) | GI SHEET ROUND METAL DUCTING Supply, Fabrication, Testing, Air Flow Balancing and Commissioning of Factory Fabricated GI Sheet Metal 180GSM Round ducting, Splitters, Flanges, Collars etc as per SMACNA standards. The complete ducting shall be provided with MS Supports, Rods, Angles, Flanges, Bracing, Rubber Gaskets, etc. as per drawings and specifications. 24 Gauge GI Sheet Metal Duct (0-600mm) | Sq.mtr | 25 |  | 1850 | 46250 |  |  | 1850 | 46250
58 |  | AIR BALANCING LEAK TEST - Air balancing activity with calibrated air hood and subsequent air balancing report with consultants approval for entire project. Also, cost shall include light or smoke test of complete duct length. | AIR BALANCING LEAK TEST - Air balancing activity with calibrated air hood and subsequent air balancing report with consultants approval for entire project. Also, cost shall include light or smoke test of complete duct length. | Lot | 1 |  | 15000 | 15000 |  |  | 20000 | 20000
59 |  | EXTRUDED ALUMINIUM GRILLES - SITC of Aluminium extruded powder coated 150mm width grilles model EP-00 or 15 or 30 with four side flanges, etc. | EXTRUDED ALUMINIUM GRILLES - SITC of Aluminium extruded powder coated 150mm width grilles model EP-00 or 15 or 30 with four side flanges, etc.
60 | a | Linear Grille | Linear Grille | Sq.mtr | 10 |  | 8500 | 85000 |  |  | 8750 | 87500
61 | b | Curve Grille | Curve Grille | Sq.mtr | 3 |  | 9500 | 28500 |  |  | 10430 | 31290
62 |  | EXTRUDED ALUMINIUM CEILING SQUARE DIFFUSER - Supply, Installation, Testing and Balancing of supply return air diffusers as per the approved shop drawings and specifications. Each diffuser shall be equipped with fixed air distribution grid, removable key-operated volume control damper, complete with insulated plenum box. The diffusers shall be anti-smudge ring or flush type. Powder coated extruded aluminium diffusers of approved colour shade of following sizes | EXTRUDED ALUMINIUM CEILING SQUARE DIFFUSER - Supply, Installation, Testing and Balancing of supply return air diffusers as per the approved shop drawings and specifications. Each diffuser shall be equipped with fixed air distribution grid, removable key-operated volume control damper, complete with insulated plenum box. The diffusers shall be anti-smudge ring or flush type. Powder coated extruded aluminium diffusers of approved colour shade of following sizes
63 |  | Supply Air Square Diffuser with Plenum Box Control Damper - 225x225mm Neck Size | Supply Air Square Diffuser with Plenum Box Control Damper - 225x225mm Neck Size | Nos. | 4 |  | 2800 | 11200 |  |  | 2250 | 9000
64 |  | Return Air Round Diffuser - 225x225mm Neck Size | Return Air Round Diffuser - 225x225mm Neck Size | No. | 4 |  | 2000 | 8000 |  |  | 2450 | 9800
65 |  | EXTRUDED ALUMINIUM CEILING ROUND DIFFUSER Supply, Installation, Testing and Balancing of supply return air diffusers as per the approved shop drawings and specifications. Each diffuser shall be equipped with fixed air distribution grid, removable key-operated volume control damper, complete with insulated plenum box. The diffusers shall be anti-smudge ring or flush type. Powder coated extruded aluminium diffusers of approved colour shade of following sizes Supply Air Round Diffuser with Plenum Box Control Damper 300mmF Neck Size | EXTRUDED ALUMINIUM CEILING ROUND DIFFUSER Supply, Installation, Testing and Balancing of supply return air diffusers as per the approved shop drawings and specifications. Each diffuser shall be equipped with fixed air distribution grid, removable key-operated volume control damper, complete with insulated plenum box. The diffusers shall be anti-smudge ring or flush type. Powder coated extruded aluminium diffusers of approved colour shade of following sizes Supply Air Round Diffuser with Plenum Box Control Damper 300mmF Neck Size | Nos. | 2 |  | 3200 | 6400 |  |  | 2150 | 4300
66 |  | MULTI LEAF VOLUME CONTROL DAMPER SITC of opposed blade aerofoil type 1.2 mm thick Anodized Aluminium volume control dampers for ducts shall be provided with concealed gears, plastic operator and quadrants for manual control of volume of air flow and for proper balancing of the air distribution system as per the approved shop drawings and specifications. Makes Dynacraft or Cosmos | MULTI LEAF VOLUME CONTROL DAMPER SITC of opposed blade aerofoil type 1.2 mm thick Anodized Aluminium volume control dampers for ducts shall be provided with concealed gears, plastic operator and quadrants for manual control of volume of air flow and for proper balancing of the air distribution system as per the approved shop drawings and specifications. Makes Dynacraft or Cosmos | Sq.mtr | 2 |  | 10500 | 21000 |  |  | 10500 | 21000
67 |  | OPPOSED BLADE DAMPER - SITC of Aluminium Opposed blade dampers black powder coated vertical blades type for supply air collar. The damper should be gear operated type. | OPPOSED BLADE DAMPER - SITC of Aluminium Opposed blade dampers black powder coated vertical blades type for supply air collar. The damper should be gear operated type. | Sq.mtr | 2 |  | 5500 | 11000 |  |  | 5460 | 10920
68 |  | MOTORISED FIRE DAMPER - Supply, installation, testing and commissioning of UL 555 or UL 555 S motorized fire or smoke dampers at wall or floor crossing consist of 2.0 Hours rating, 16G GI frame blade, 20G GI casing, brass bushing for friction free operation, S.S jamb seal for minimum leakage, ON or OFF type actuator with transformer etc. as per specification and approved shop drawings. (Actuators of 24VAC built with Auxiliary switch provides feedback for BMS systems) | MOTORISED FIRE DAMPER - Supply, installation, testing and commissioning of UL 555 or UL 555 S motorized fire or smoke dampers at wall or floor crossing consist of 2.0 Hours rating, 16G GI frame blade, 20G GI casing, brass bushing for friction free operation, S.S jamb seal for minimum leakage, ON or OFF type actuator with transformer etc. as per specification and approved shop drawings. (Actuators of 24VAC built with Auxiliary switch provides feedback for BMS systems)
69 | a | Fire or Smoke damper | Fire or Smoke damper | Sq.mtr | 4 |  | 12500 | 50000 |  |  | 18500 | 74000
70 | b | Actuator with trnasformer | Actuator with trnasformer | Nos. | 7 |  | 14500 | 101500 |  |  | 16500 | 115500
71 | c | Control logic wiring for shutting all fire dampers in each AHU s, when AHU is OFF for any reason. | Control logic wiring for shutting all fire dampers in each AHU s, when AHU is OFF for any reason. | Lot | 1 |  | 10000 | 10000 |  |  | 15000 | 15000
72 |  | JET NOZZLE Supply, Installation, Testing and Balancing of Powder coated extruded aluminium Jet nozzles with shutter type damper etc. as per the approved shop drawings and specifications. 325mm F Neck Size | JET NOZZLE Supply, Installation, Testing and Balancing of Powder coated extruded aluminium Jet nozzles with shutter type damper etc. as per the approved shop drawings and specifications. 325mm F Neck Size | Nos. | 30 |  | 5500 | 165000 |  |  | 6250 | 187500
73 | a | DISC VALVE SITC of Aluminium powder coated Disc valve suitable for exhausting toilet foul air, comprising of an adjustable centre cone and coupling sleeve made of Aluminium sheet duly epoxy painted with approved color. 150mmF | DISC VALVE SITC of Aluminium powder coated Disc valve suitable for exhausting toilet foul air, comprising of an adjustable centre cone and coupling sleeve made of Aluminium sheet duly epoxy painted with approved color. 150mmF | Nos. | 18 |  | 1250 | 22500 |  |  | 1850 | 33300
74 |  | PRE-INULATED FLEXIBLE DUCT - SITC of following sizes of insulated flexible ducting with its matching supports, clamps and square to round pieces and other accessories fittings etc. The flexible duct shall me made of triple lamination of aluminium foil, polyester and metalised polyester film permanently bonded to a coated spring steel wire helix. The exterior shall be wrapped with 25mm thick 16 kg or cum fibreglass insulation. The outer insulation jacket or vapour barrier made of fibreglass reinforced metalised polyester film laminate. | PRE-INULATED FLEXIBLE DUCT - SITC of following sizes of insulated flexible ducting with its matching supports, clamps and square to round pieces and other accessories fittings etc. The flexible duct shall me made of triple lamination of aluminium foil, polyester and metalised polyester film permanently bonded to a coated spring steel wire helix. The exterior shall be wrapped with 25mm thick 16 kg or cum fibreglass insulation. The outer insulation jacket or vapour barrier made of fibreglass reinforced metalised polyester film laminate.
75 | a | 350mmF | 350mmF | Rmt | 30 |  | 750 | 22500 |  |  | 1450 | 43500
76 | b | 300mmF | 300mmF | Rmt | 5 |  | 650 | 3250 |  |  | 1250 | 6250
77 | c | 250mmF | 250mmF | Rmt | 5 |  | 550 | 2750 |  |  | 1150 | 5750
78 | d | 150mmF | 150mmF | Rmt | 20 |  | 450 | 9000 |  |  | 1050 | 21000
79 | 6.14 | CANVAS CONNECTION | CANVAS CONNECTION
80 |  | Supply fixing of fire rated flexible Canvas connections between mouth piece and initial piece of ducting with inspection zip. | Supply fixing of fire rated flexible Canvas connections between mouth piece and initial piece of ducting with inspection zip.
81 | a | For AHU | For AHU | Nos | 2 |  | 3000 | 6000 |  |  | 2650 | 5300
82 | b | For Fan | For Fan | Nos | 2 |  | 3000 | 6000 |  |  | 2850 | 5700
83 |  | NOTES The ducting support should be as per tender specification and additional supports are to be provided by Contractor as decided by Consultant. Muslin cloth cover for all air outlets during construction. Air Flow balancing and Pressure testing of complete duct work as per DW or SMACNA standard. Light testing or smoke testing shall be employed for leaks Silicon sealant for longitudinal transverse joints as per specification. Jet Nozzle, Diffusers grilles shall be powder coated as per color approved by Architect. | NOTES The ducting support should be as per tender specification and additional supports are to be provided by Contractor as decided by Consultant. Muslin cloth cover for all air outlets during construction. Air Flow balancing and Pressure testing of complete duct work as per DW or SMACNA standard. Light testing or smoke testing shall be employed for leaks Silicon sealant for longitudinal transverse joints as per specification. Jet Nozzle, Diffusers grilles shall be powder coated as per color approved by Architect.
84 |  | THERMAL INSULATION FOR DUCTS - Supply fixing of Thermal insulation for supply air duct using 13mm thick class inch O inch Closed cell nitrile rubber with anti-microbial coating on it. Insulation shall have Thermal conductivity of 0.033 W or (m.K) and water vapor permeance of 0.10. Joints should be sealed with 50 mm wide 3 mm thick self adhesive tape. The duct shall be stick with recommended adhesive. | THERMAL INSULATION FOR DUCTS - Supply fixing of Thermal insulation for supply air duct using 13mm thick class inch O inch Closed cell nitrile rubber with anti-microbial coating on it. Insulation shall have Thermal conductivity of 0.033 W or (m.K) and water vapor permeance of 0.10. Joints should be sealed with 50 mm wide 3 mm thick self adhesive tape. The duct shall be stick with recommended adhesive. | Sq.mtr | 410 |  | 650 | 266500 |  |  | 750 | 307500
85 |  | ACOUSTIC INSULATION FOR DUCTS - Supply fixing acoustic insulation for ducting using Class inch 1 inch closed cell elastomeric insulation of 10mm thick Nitrile rubber insulation adhesive, longitudinal transverse joints sealed with adhesive in neat clean manner. Material shall be processed Nitrile Rubber foam with anti-microbial protection. Insulation shall have thermal conductivity of 0.047 W or (m.K) and density of 140 - 180 kg or m³. | ACOUSTIC INSULATION FOR DUCTS - Supply fixing acoustic insulation for ducting using Class inch 1 inch closed cell elastomeric insulation of 10mm thick Nitrile rubber insulation adhesive, longitudinal transverse joints sealed with adhesive in neat clean manner. Material shall be processed Nitrile Rubber foam with anti-microbial protection. Insulation shall have thermal conductivity of 0.047 W or (m.K) and density of 140 - 180 kg or m³. | Sq.mtr | 30 |  | 1250 | 37500 |  |  | 1450 | 43500
86 |  | ACOUSTIC INSULATION FOR AHU ROOM - Supply fixing of Acoustic insulation for plant room using 50mm thick Twiga 300 rigid board stick using shalikote primer and GI frame work. Insulation to be covered with glass fiber cloth finally with 24 G perforated Al. sheet. | ACOUSTIC INSULATION FOR AHU ROOM - Supply fixing of Acoustic insulation for plant room using 50mm thick Twiga 300 rigid board stick using shalikote primer and GI frame work. Insulation to be covered with glass fiber cloth finally with 24 G perforated Al. sheet. | Sq.mtr | 75 |  | 1050 | 78750 |  |  | 1250 | 93750
87 |  | Note a. Insulation work to be coordinated with other agencies and repair to be included by contractor as per site requirement. b. Vendors to take care of the installation, if any damages takes place the vendor to repair or replace and hand over to clients in good and acceptable condition. c. Thermal insulation shall be internal for Elliptical or Expossed ducting. | Note a. Insulation work to be coordinated with other agencies and repair to be included by contractor as per site requirement. b. Vendors to take care of the installation, if any damages takes place the vendor to repair or replace and hand over to clients in good and acceptable condition. c. Thermal insulation shall be internal for Elliptical or Expossed ducting.
88 | 8 | ELECTRICAL WORKS | ELECTRICAL WORKS
89 |  | STARTER PANEL - SITC of indoor or outdoor, wall mounting type 3PH, 415VAC MOTOR STARTERS IN CRCA SHEET STEEL ENCLOSURE with necssary supporting brackets and required accessories, etc., The Enclosure shall be provided with knockouts suitable for cable termination at TOP BOTTOM for incoming and outgoing power cables of A2XFY type and size specified. The starters shall be complete with suitable MPCB or MCCB, Contactor, Bi-metal O or L relay with SPP, ON or OFF Push buttons, on or off or trip indication Lamp, on off push button, phase indication Lamp. Selection of relay, contractor, MPCB or MCCB etc. as per Type-2 Coordination. | STARTER PANEL - SITC of indoor or outdoor, wall mounting type 3PH, 415VAC MOTOR STARTERS IN CRCA SHEET STEEL ENCLOSURE with necssary supporting brackets and required accessories, etc., The Enclosure shall be provided with knockouts suitable for cable termination at TOP BOTTOM for incoming and outgoing power cables of A2XFY type and size specified. The starters shall be complete with suitable MPCB or MCCB, Contactor, Bi-metal O or L relay with SPP, ON or OFF Push buttons, on or off or trip indication Lamp, on off push button, phase indication Lamp. Selection of relay, contractor, MPCB or MCCB etc. as per Type-2 Coordination.
90 | a | 11200 CFM AHU - 7.5KW, 3PH, Starter Delta type | 11200 CFM AHU - 7.5KW, 3PH, Starter Delta type | No. | 1 |  | 55000 | 55000 |  |  | 125000 | 125000
91 | b | 10500CFM AHU - 7.5KW, 3PH, Starter Delta type | 10500CFM AHU - 7.5KW, 3PH, Starter Delta type | No. | 1 |  | 55000 | 55000 |  |  | 125000 | 125000
92 |  | MCB FOR VRF ODU - SITC of IP65 rated PVC enclosure with 40A TPN MCB For HVAC Outdoor Units | MCB FOR VRF ODU - SITC of IP65 rated PVC enclosure with 40A TPN MCB For HVAC Outdoor Units | Nos. | 2 |  | 8500 | 17000 |  |  | 6500 | 13000
93 |  | POWER CABLING - Supply, handling, laying effecting proper connections testing and commissioning of following sizes of 1.1 KV grade XLPE insulated FRLS Aluminium or Copper conductor cables laid over MS supports cable racks or fixing on walls including clamping the cable to supports in an approved manner as required complete with Copper earthing as specified for continuous earthing along with cable. All complete as required and as per final instruction as given by Owners or Consultants and as per Technical specifications. Earthing shall be measured separately and shall be connected in two runs. Power to ELCB to be provided near each ODU by electrical contractor. | POWER CABLING - Supply, handling, laying effecting proper connections testing and commissioning of following sizes of 1.1 KV grade XLPE insulated FRLS Aluminium or Copper conductor cables laid over MS supports cable racks or fixing on walls including clamping the cable to supports in an approved manner as required complete with Copper earthing as specified for continuous earthing along with cable. All complete as required and as per final instruction as given by Owners or Consultants and as per Technical specifications. Earthing shall be measured separately and shall be connected in two runs. Power to ELCB to be provided near each ODU by electrical contractor.
94 |  | Power Cable CU 6 sqmm 6 core - 7.5KW | Power Cable CU 6 sqmm 6 core - 7.5KW | Rmt | 20 |  | 650 | 13000 |  |  | 1050 | 21000
95 |  | Earthing 8 SWG GI Earthing | Earthing 8 SWG GI Earthing | Rmt | 40 |  | 180 | 7200 |  |  | 150 | 6000
96 | a | CABLE TERMINATION Supply Making of Cable termination of armoured or unarmoured cables 1.1 KV grade including installation of cable glands, cable lugs (Aluminium for A2XFY copper for 2XFY YY Double compression type), heat shrinkable sleeves on long ends, crimping paste etc. The work includes testing commissioning of cables, meggaring values submitting reports of tests. (One set includes termination of all cores of one end only). All crimping tools dies shall be arranged by contractor. CU 6 sqmm 6 core - 7.5KW | CABLE TERMINATION Supply Making of Cable termination of armoured or unarmoured cables 1.1 KV grade including installation of cable glands, cable lugs (Aluminium for A2XFY copper for 2XFY YY Double compression type), heat shrinkable sleeves on long ends, crimping paste etc. The work includes testing commissioning of cables, meggaring values submitting reports of tests. (One set includes termination of all cores of one end only). All crimping tools dies shall be arranged by contractor. CU 6 sqmm 6 core - 7.5KW | Nos. | 2 |  | 550 | 1100 |  |  | 3000 | 6000
97 | a | CABLE TRAYS Supplying Fixing of following sizes of GI cable tray duly painted perforated type of height 50mm along with necessary bends, reducers etc. anchored along the wall or suspended from the ceiling with necessary MS supports. 150mm wide | CABLE TRAYS Supplying Fixing of following sizes of GI cable tray duly painted perforated type of height 50mm along with necessary bends, reducers etc. anchored along the wall or suspended from the ceiling with necessary MS supports. 150mm wide | Rmt | 15 |  | 550 | 8250 |  |  | 550 | 8250
3 |  | Kitchen Ventilation High side Work | Kitchen Ventilation High side Work for 080 Domestic lounge Phase -2 | NOS | 1 |  |  | 350000 |  |  |  | 670000
98 |  | Note Prices shall be based on supply, installation, testing commissioning (SITC) at site including all taxes, duties, transportation insurance etc. | Note Prices shall be based on supply, installation, testing commissioning (SITC) at site including all taxes, duties, transportation insurance etc.
99 | 1 | VENTILATION SYSTEM | VENTILATION SYSTEM
100 | a | KITCHEN EXHAUST AIR FAN SITC of SISW Centrifugal Blower, Belt Direct Drive, Statically Dynamically Balanced, Backward Curved Impeller fan, Dunlop Anti- Vibration Pads etc. Motor should be outside stream with TEFC squirrel cage, weather protection shield, IP 55 rating with Class F Insulation, suitable for 3phase, 415volts, 50hz power supply. Sound level should be 60dB @ 3mtr distance. Fan should be painted with 2 coat of zinc chromate primer and 2 coats Epoxy paint. The quote shall include with MS frame, starter panel along with its required cable. Supplied with Dunlop Anti- Vibration Pads Canvass Connection. (Vendor to crosscheck static pressure calculation). 5000 CFM, 60mm Static (Class F) | KITCHEN EXHAUST AIR FAN SITC of SISW Centrifugal Blower, Belt Direct Drive, Statically Dynamically Balanced, Backward Curved Impeller fan, Dunlop Anti- Vibration Pads etc. Motor should be outside stream with TEFC squirrel cage, weather protection shield, IP 55 rating with Class F Insulation, suitable for 3phase, 415volts, 50hz power supply. Sound level should be 60dB @ 3mtr distance. Fan should be painted with 2 coat of zinc chromate primer and 2 coats Epoxy paint. The quote shall include with MS frame, starter panel along with its required cable. Supplied with Dunlop Anti- Vibration Pads Canvass Connection. (Vendor to crosscheck static pressure calculation). 5000 CFM, 60mm Static (Class F) | No | 1 |  | 155000 | 155000 |  |  | 265000 | 265000
101 | a | INDUSTRIAL GRADE ELECTROSTATIC AIR CLEANER SITC of Dry scrubber – Electrostatic Air cleaner with starter panel as per specifications, suitable for following capacities, including electrical starter panel . The Air filtration efficiency should be between 90 to 95% units shall be staked one above other or side by side as per site requirement, if vendor will propose multiple units. Finishing - Power coated, Dark Blue Operating voltage - 220 Vac+ or -10%, 50 Hz (Single phase) Features - Short circuit, arc protection and auto restore power supply, BMS (Building Management System) terminals provided, Auto power cut-off when door is opened, Indicator LEDs for normal or wash indicator, Set of Terminals for remote LED normal or wash indicator Efficiency - Upto 95%, meets NIOSH 5026 Oil Mist Test Particle Size - Collects particles as small as 0.01 microns Motor - Sealead ball bearings UL, single phase. Cell - Ionizing voltage - 12 KVdc Collector voltage - 6 KVdc One cell comprising of 9 ionizing wires and 25 collection plates Controls - Auto cut-off when door is opened. Indicator lights for fault, normal or wash function. Pre-filter - Aluminium mesh, washable Dry contact for BMS. 5000 CFM | INDUSTRIAL GRADE ELECTROSTATIC AIR CLEANER SITC of Dry scrubber – Electrostatic Air cleaner with starter panel as per specifications, suitable for following capacities, including electrical starter panel . The Air filtration efficiency should be between 90 to 95% units shall be staked one above other or side by side as per site requirement, if vendor will propose multiple units. Finishing - Power coated, Dark Blue Operating voltage - 220 Vac+ or -10%, 50 Hz (Single phase) Features - Short circuit, arc protection and auto restore power supply, BMS (Building Management System) terminals provided, Auto power cut-off when door is opened, Indicator LEDs for normal or wash indicator, Set of Terminals for remote LED normal or wash indicator Efficiency - Upto 95%, meets NIOSH 5026 Oil Mist Test Particle Size - Collects particles as small as 0.01 microns Motor - Sealead ball bearings UL, single phase. Cell - Ionizing voltage - 12 KVdc Collector voltage - 6 KVdc One cell comprising of 9 ionizing wires and 25 collection plates Controls - Auto cut-off when door is opened. Indicator lights for fault, normal or wash function. Pre-filter - Aluminium mesh, washable Dry contact for BMS. 5000 CFM | No | 1 |  | 185000 | 185000 |  |  | 345000 | 345000
102 |  | FRAMEWORK FOR FANS - Supply, Fabrication and Installation of MS frame using channels or angle iron sections as required for mounting of ventilation fans scrubber in areas shown in the layout. The frame work shall be applied with red oxide primer and thereafter, two coats of enamel paint of approved colour. The general arrangement drawing for frame work shall be got approved from the Architects or Structural Engineers prior to commencement of fabrication. | FRAMEWORK FOR FANS - Supply, Fabrication and Installation of MS frame using channels or angle iron sections as required for mounting of ventilation fans scrubber in areas shown in the layout. The frame work shall be applied with red oxide primer and thereafter, two coats of enamel paint of approved colour. The general arrangement drawing for frame work shall be got approved from the Architects or Structural Engineers prior to commencement of fabrication.
103 | a | Exhaust Fan - 5000CFM | Exhaust Fan - 5000CFM | Lot | 1 |  | 6500 | 6500 |  |  | 35000 | 35000
104 | b | Dry Scrubber - 5000 CFM | Dry Scrubber - 5000 CFM | Lot | 1 |  | 3500 | 3500 |  |  | 25000 | 25000
105 |  | Note a. Fan outlet velocity - 1600 FPM b. All cabinet fans should have plenum section. c. Fresh air fan if any,should to have 6mm thick synthetic media washable filter with framework. d. Contractor shall submit static pressure calculation for all above units to Client or Consultant. e. Any change in motor HP or coil selection shall be made at no extra cost to client. f. Fan efficiency shall be minimum 75% g. The cost shall be included liftting shifting of each equipment or material with all necesaary arrnagement. Also, it shall be included the cost of scaffloding required for Installation of such material or equipment. | Note a. Fan outlet velocity - 1600 FPM b. All cabinet fans should have plenum section. c. Fresh air fan if any,should to have 6mm thick synthetic media washable filter with framework. d. Contractor shall submit static pressure calculation for all above units to Client or Consultant. e. Any change in motor HP or coil selection shall be made at no extra cost to client. f. Fan efficiency shall be minimum 75% g. The cost shall be included liftting shifting of each equipment or material with all necesaary arrnagement. Also, it shall be included the cost of scaffloding required for Installation of such material or equipment.
4 |  | Kitchen Ventilation Low side Work | Kitchen Ventilation Low side Work for 080 Domestic lounge Phase -2 | NOS | 1 |  |  | 587000 |  |  |  | 718500
106 |  | Note Prices shall be based on supply, installation, testing commissioning (SITC) at site including all taxes, duties, transportation insurance etc. | Note Prices shall be based on supply, installation, testing commissioning (SITC) at site including all taxes, duties, transportation insurance etc.
107 |  | SHEET METAL WORKS | SHEET METAL WORKS
108 |  | GI SHEET METAL DUCTING - Supply, Fabrication, Testing, Air Flow Balancing and Commissioning of Factory Fabricated GI Sheet Metal 180GSM Rectangular boxed ducting, Plenums, Cowls, Elbows, Splitters, Reducers, Flanges, Collars etc as per SMACNA standards, The complete ducting shall be provided with MS Supports, Rods, Angles, Flanges, Bracing, Rubber Gaskets, Wooden frames, Canvas Connections, etc. as per drawings and specifications. | GI SHEET METAL DUCTING - Supply, Fabrication, Testing, Air Flow Balancing and Commissioning of Factory Fabricated GI Sheet Metal 180GSM Rectangular boxed ducting, Plenums, Cowls, Elbows, Splitters, Reducers, Flanges, Collars etc as per SMACNA standards, The complete ducting shall be provided with MS Supports, Rods, Angles, Flanges, Bracing, Rubber Gaskets, Wooden frames, Canvas Connections, etc. as per drawings and specifications.
109 |  | 22 Gauge GI Sheet Metal Duct (601-1100mm) | 22 Gauge GI Sheet Metal Duct (601-1100mm) | Sq.mtr | 50 |  | 1450 | 72500 |  |  | 1350 | 67500
110 |  | 24 Gauge GI Sheet Metal Duct (0-600mm) | 24 Gauge GI Sheet Metal Duct (0-600mm) | Sq.mtr | 150 |  | 1250 | 187500 |  |  | 1550 | 232500
111 |  | SS EXHAUST AND FRESH AIR GRILLS - SITC of 18G SS 304 Fresh Air Grilles adjustable Double Deflector With S.S Volume Control Dampers. Grills to be of Double Deflection Type for ease of deflection on all sides. | SS EXHAUST AND FRESH AIR GRILLS - SITC of 18G SS 304 Fresh Air Grilles adjustable Double Deflector With S.S Volume Control Dampers. Grills to be of Double Deflection Type for ease of deflection on all sides. | Sq.mtr | 0.75 |  | 22500 | 16875 |  |  | 10500 | 7875
112 |  | DOOR TRANSFER GRILLE SITC of Aluminium extruded powder coated Door transfer grills. Door transfer grille (Back to Back) | DOOR TRANSFER GRILLE SITC of Aluminium extruded powder coated Door transfer grills. Door transfer grille (Back to Back) | Sq.mtr | 0.25 |  | 10500 | 2625 |  |  | 11500 | 2875
113 |  | MULTI LEAF VOLUME CONTROL DAMPER - SITC of opposed blade aerofoil type 1.2 mm thick Anodized Aluminium volume control dampers for ducts shall be provided with concealed gears, plastic operator and quadrants for manual control of volume of air flow and for proper balancing of the air distribution system as per the approved shop drawings and specifications. | MULTI LEAF VOLUME CONTROL DAMPER - SITC of opposed blade aerofoil type 1.2 mm thick Anodized Aluminium volume control dampers for ducts shall be provided with concealed gears, plastic operator and quadrants for manual control of volume of air flow and for proper balancing of the air distribution system as per the approved shop drawings and specifications. | Sq.mtr | 2.5 |  | 10500 | 26250 |  |  | 9500 | 23750
114 |  | CURTAIN TYPE FIRE DAMPER - SITC of curtain type fire dampers consist of 16G GI frame, 20G GI interlocking blades secured with SS springs, blades outside airstream clamped with fusible link UL-555 listed with melting point 165 225°F, etc; as per the approved shop drawings and specifications. | CURTAIN TYPE FIRE DAMPER - SITC of curtain type fire dampers consist of 16G GI frame, 20G GI interlocking blades secured with SS springs, blades outside airstream clamped with fusible link UL-555 listed with melting point 165 225°F, etc; as per the approved shop drawings and specifications.
115 |  | Bare fire dampers | Bare fire dampers | Sq.mtr | 0.3 |  | 12500 | 3750 |  |  | 16500 | 4950
116 |  | Fusible link as per specification UL 555 and CBRI approved | Fusible link as per specification UL 555 and CBRI approved | No. | 1 |  | 4500 | 4500 |  |  | 1600 | 1600
117 |  | CANVAS CONNECTION - Supply fixing of flexible Canvas connections between mouth piece and initial piece of ducting. Flexible connections shall be fire resistant made of closely woven, double layer canvass neoprene coated fibre glass. | CANVAS CONNECTION - Supply fixing of flexible Canvas connections between mouth piece and initial piece of ducting. Flexible connections shall be fire resistant made of closely woven, double layer canvass neoprene coated fibre glass.
118 |  | Cabiner Exhaust Fan | Cabiner Exhaust Fan | Nos | 1 |  | 3000 | 3000 |  |  | 3250 | 3250
119 |  | Dry Scrubber | Dry Scrubber | Nos | 1 |  | 3000 | 3000 |  |  | 3500 | 3500
120 |  | NOTES The ducting support should be as per tender specification and additional supports are to be provided by Contractor as decided by Consultant. Muslin cloth cover for all air outlets during construction. Pressure testing of complete duct work as per DW SMACNA standard. Silicon sealant for longitudinal transverse joints as per specification. Diffusers grilles shall be powder coated as per color approved by Architect. | NOTES The ducting support should be as per tender specification and additional supports are to be provided by Contractor as decided by Consultant. Muslin cloth cover for all air outlets during construction. Pressure testing of complete duct work as per DW SMACNA standard. Silicon sealant for longitudinal transverse joints as per specification. Diffusers grilles shall be powder coated as per color approved by Architect.
121 |  | THERMAL INSULATION SITC of Rockwool roll Insulation with stonewool fibres bonded with thermosetting resins, with factory applied laminated Woven Fiber glass cloth of 271GSM. Nominal density 48 Kg CuM. Thermal conductivity, < 0.042 W m.K at 50°C. All Insulation material and adhesives shall be as per Class O for surface spread and in accordance with BS 476, Class O for non-combustible grade. Also, cost shall include all necessary support and accessories. 50 mm Thick | THERMAL INSULATION SITC of Rockwool roll Insulation with stonewool fibres bonded with thermosetting resins, with factory applied laminated Woven Fiber glass cloth of 271GSM. Nominal density 48 Kg CuM. Thermal conductivity, < 0.042 W m.K at 50°C. All Insulation material and adhesives shall be as per Class O for surface spread and in accordance with BS 476, Class O for non-combustible grade. Also, cost shall include all necessary support and accessories. 50 mm Thick | Sq.mtr | 200 |  | 850 | 170000 |  |  | 1250 | 250000
122 |  | ELECTRICAL WORKS | ELECTRICAL WORKS
123 |  | STARTER PANEL with VFD SITC of indoor outdoor, wall mounting type 3PH, 415VAC MOTOR STARTERS IN CRCA SHEET STEEL ENCLOSURE with necssary supporting brackets and required accessories, etc., The Enclosure shall be provided with knockouts suitable for cable termination at TOP BOTTOM for incoming and outgoing power cables of A2XFY type and size specified. The starters shall be complete with suitable MPCB MCCB, Contactor, Bi-metal O L relay with SPP, ON OFF Push buttons, on off trip indication Lamp, on off push button, phase indication Lamp. Selection of relay, contractor, MPCB MCCB etc. as per Type-2 Coordination. Starter panel shall be BMS compatible. Variable frequency drives shall be provided with necessary sensors and controllers complete with control wiring in all respect as required. VFDs shall be provided with necessary bypass arrangement inside electrical starter panels with IP-55 enclosure. 5.5KW, 3PH, DOL Starter type for exhaust air fan | STARTER PANEL with VFD SITC of indoor outdoor, wall mounting type 3PH, 415VAC MOTOR STARTERS IN CRCA SHEET STEEL ENCLOSURE with necssary supporting brackets and required accessories, etc., The Enclosure shall be provided with knockouts suitable for cable termination at TOP BOTTOM for incoming and outgoing power cables of A2XFY type and size specified. The starters shall be complete with suitable MPCB MCCB, Contactor, Bi-metal O L relay with SPP, ON OFF Push buttons, on off trip indication Lamp, on off push button, phase indication Lamp. Selection of relay, contractor, MPCB MCCB etc. as per Type-2 Coordination. Starter panel shall be BMS compatible. Variable frequency drives shall be provided with necessary sensors and controllers complete with control wiring in all respect as required. VFDs shall be provided with necessary bypass arrangement inside electrical starter panels with IP-55 enclosure. 5.5KW, 3PH, DOL Starter type for exhaust air fan | No | 1 |  | 75000 | 75000 |  |  | 95000 | 95000
124 |  | POWER CABLING - Supply, handling, laying effecting proper connections testing and commissioning of following sizes of 1.1 KV grade XLPE insulated FRLS Aluminium Copper conductor cables laid over MS supports cable racks or fixing on walls including clamping the cable to supports in an approved manner as required complete with Copper earthing as specified for continuous earthing along with cable. All complete as required and as per final instruction as given by Owners Consultants and as per Technical specifications. Earthing shall be measured separately and shall be connected in two runs. Power to ELCB to be provided near each ODU by electrical contractor. Power Cable | POWER CABLING - Supply, handling, laying effecting proper connections testing and commissioning of following sizes of 1.1 KV grade XLPE insulated FRLS Aluminium Copper conductor cables laid over MS supports cable racks or fixing on walls including clamping the cable to supports in an approved manner as required complete with Copper earthing as specified for continuous earthing along with cable. All complete as required and as per final instruction as given by Owners Consultants and as per Technical specifications. Earthing shall be measured separately and shall be connected in two runs. Power to ELCB to be provided near each ODU by electrical contractor. Power Cable
125 |  | CU 2.5 sqmm 4 core - Exhaust Fan | CU 2.5 sqmm 4 core - Exhaust Fan | Rmt | 10 |  | 450 | 4500 |  |  | 350 | 3500
126 |  | CU 2.5 sqmm 3 core - Dry Scrubber | CU 2.5 sqmm 3 core - Dry Scrubber | Rmt | 10 |  | 180 | 1800 |  |  | 320 | 3200
127 |  | Earthing - 8 SWG GI Earthing | Earthing - 8 SWG GI Earthing | Rmt | 20 |  | 180 | 3600 |  |  | 150 | 3000
128 |  | CABLE TERMINATION Supply Making of Cable termination of armoured unarmoured cables 1.1 KV grade including installation of cable glands, cable lugs (Aluminium for A2XFY copper for 2XFY YY Double compression type), heat shrinkable sleeves on long ends, crimping paste etc. The work includes testing commissioning of cables, meggaring values submitting reports of tests. (One set includes termination of all cores of one end only). All crimping tools dies shall be arranged by contractor. CU 2.5 sqmm 4 core - Exhaust Fan | CABLE TERMINATION Supply Making of Cable termination of armoured unarmoured cables 1.1 KV grade including installation of cable glands, cable lugs (Aluminium for A2XFY copper for 2XFY YY Double compression type), heat shrinkable sleeves on long ends, crimping paste etc. The work includes testing commissioning of cables, meggaring values submitting reports of tests. (One set includes termination of all cores of one end only). All crimping tools dies shall be arranged by contractor. CU 2.5 sqmm 4 core - Exhaust Fan | Nos. | 2 |  | 550 | 1100 |  |  | 2500 | 5000
129 |  | CABLE TRAYS Supplying Fixing of following sizes of GI cable tray duly painted perforated type of height 50mm along with necessary bends, reducers etc. anchored along the wall suspended from the ceiling with necessary MS supports. 150mm wide | CABLE TRAYS Supplying Fixing of following sizes of GI cable tray duly painted perforated type of height 50mm along with necessary bends, reducers etc. anchored along the wall suspended from the ceiling with necessary MS supports. 150mm wide | Rmt | 20 |  | 550 | 11000 |  |  | 550 | 11000

## Technical Score Detail
|  | RFQ No: R1359 COST COMPARISON REPORT | RFQ No: R1359 COST COMPARISON REPORT | RFQ No: R1359 COST COMPARISON REPORT | Comp. Date : 29/07/2024 | Comp. Date : 29/07/2024 | Comp. Date : 29/07/2024 | Vendor Name : PIONEER PROJECT SOLUTION | [11 empty] | Vendor Name : CRYSTAL AIRCOOL | [11 empty] | Vendor Name : ANJLE MEP PROJECT PVT LTD
|  | RFQ No: R1359 COST COMPARISON REPORT | RFQ No: R1359 COST COMPARISON REPORT | RFQ No: R1359 COST COMPARISON REPORT | RFQ #: R1359 | RFQ #: R1359 | RFQ #: R1359 | Contact Name : ASHRAF | [11 empty] | Contact Name : JOHN | [11 empty] | Contact Name : PREMKANT
|  | RFQ No: R1359 COST COMPARISON REPORT | RFQ No: R1359 COST COMPARISON REPORT | RFQ No: R1359 COST COMPARISON REPORT | RFQ Date : 24/07/2024 17:16:44 | RFQ Date : 24/07/2024 17:16:44 | RFQ Date : 24/07/2024 17:16:44 | Vendor City : | [11 empty] | Vendor City : | [11 empty] | Vendor City :
|  | RFQ No: R1359 COST COMPARISON REPORT | RFQ No: R1359 COST COMPARISON REPORT | RFQ No: R1359 COST COMPARISON REPORT | BCD Date : 25/07/2024 14:03:00 | BCD Date : 25/07/2024 14:03:00 | BCD Date : 25/07/2024 14:03:00 | Telephone # : | [11 empty] | Telephone # : | [11 empty] | Telephone # :
|  | RFQ No: R1359 COST COMPARISON REPORT | RFQ No: R1359 COST COMPARISON REPORT | RFQ No: R1359 COST COMPARISON REPORT |  |  |  | Mobile # : 98106 34901 | [11 empty] | Mobile # : | [11 empty] | Mobile # :
PR Number : BLR-2425-00064 | PR Number : BLR-2425-00064 | PR Number : BLR-2425-00064 | PR Number : BLR-2425-00064 | PR Number : BLR-2425-00064 | PR Number : BLR-2425-00064 | PR Number : BLR-2425-00064 | PR Number : BLR-2425-00064 | Email : projectspioneer@gmail.com | [11 empty] | Email : crystalhvac002@gmail.com | [11 empty] | Email : anjlemepprojects@gmail.com
Package / RFQ Name : TFAS / RFQ / BLR-2425-00064 | Package / RFQ Name : TFAS / RFQ / BLR-2425-00064 | Package / RFQ Name : TFAS / RFQ / BLR-2425-00064 | Package / RFQ Name : TFAS / RFQ / BLR-2425-00064 | Package / RFQ Name : TFAS / RFQ / BLR-2425-00064 | Package / RFQ Name : TFAS / RFQ / BLR-2425-00064 | Package / RFQ Name : TFAS / RFQ / BLR-2425-00064 | Package / RFQ Name : TFAS / RFQ / BLR-2425-00064 | Round # : 1 (RFQ) |  | Round # : 2 (RFQ) |  | Round # : 3 (Auction) |  | Round # : 3 (Auction) |  | Round # : 4 (Auction) |  | Round # : 4 (Auction) |  | Round # : 1 (RFQ) |  | Round # : 2 (RFQ) |  | Round # : 3 (Auction) |  | Round # : 3 (Auction) |  | Round # : 4 (Auction) |  | Round # : 4 (Auction) |  | Round # : 1 (RFQ) |  | Round # : 2 (RFQ) |  | Round # : 3 (Auction) |  | Round # : 3 (Auction) |  | Round # : 4 (Auction) |  | Round # : 4 (Auction)
Buyer : Binu Balachandran | Buyer : Binu Balachandran | Buyer : Binu Balachandran | Buyer : Binu Balachandran | Buyer : Binu Balachandran | Buyer : Binu Balachandran | Buyer : Binu Balachandran | Buyer : Binu Balachandran | Quotation Date : |  | Quotation Date : |  | Quotation Date : |  | Quotation Date : |  | Quotation Date : |  | Quotation Date : |  | Quotation Date : |  | Quotation Date : |  | Quotation Date : |  | Quotation Date : |  | Quotation Date : |  | Quotation Date : |  | Quotation Date : |  | Quotation Date : |  | Quotation Date : |  | Quotation Date : |  | Quotation Date : |  | Quotation Date :
Comp. # : 4 | Comp. # : 4 | Comp. # : 4 | Comp. # : 4 | Comp. # : 4 | Currency :INR | Currency :INR | Currency :INR | Quotation Validity Date : |  | Quotation Validity Date : |  | Quotation Validity Date : |  | Quotation Validity Date : |  | Quotation Validity Date : |  | Quotation Validity Date : |  | Quotation Validity Date : |  | Quotation Validity Date : |  | Quotation Validity Date : |  | Quotation Validity Date : |  | Quotation Validity Date : |  | Quotation Validity Date : |  | Quotation Validity Date : |  | Quotation Validity Date : |  | Quotation Validity Date : |  | Quotation Validity Date : |  | Quotation Validity Date : |  | Quotation Validity Date :
Comp. # : 4 | Comp. # : 4 | Comp. # : 4 | Comp. # : 4 | Comp. # : 4 | BUDGET PRICE : | .00 |  | Quote Currency : |  | Quote Currency : |  | Quote Currency : |  | Quote Currency : |  | Quote Currency : |  | Quote Currency : |  | Quote Currency : |  | Quote Currency : |  | Quote Currency : |  | Quote Currency : |  | Quote Currency : |  | Quote Currency : |  | Quote Currency : |  | Quote Currency : |  | Quote Currency : |  | Quote Currency : |  | Quote Currency : |  | Quote Currency :
# | Item Code | Item Description | Last PO Details | Unit | Qty | Last PO Unit Rate | Last PO Total Value | Score | Justification | Score | Justification | Score | Justification | Score | Justification | Score | Justification | Score | Justification | Score | Justification | Score | Justification | Score | Justification | Score | Justification | Score | Justification | Score | Justification | Score | Justification | Score | Justification | Score | Justification | Score | Justification | Score | Justification | Score | Justification
1 |  | HVAC High side Work |  | NOS | 1.000 | 0.00 | 0.00
2 |  | Note Prices shall be based on supply, installation, testing commissioning (SITC) at site including all taxes, duties, transportation insurance etc. |  |  | 0.000 | 0.00 | 0.00
3 | a | AIR HANDLING UNIT CHW FLOOR MOUNTED AIR HANDLING UNIT SITC of double skin floor mounted AHU with suitable plug type fans with IE3 efficient 3phase motor, UVGI, Moisture eliminators etc. The thickness of panel to be with 42+ -3mm thick PUF Insulation. The coil shall be of hard copper tubes covered by aluminium fins with 13-15 FPI. The AHU to have a SS condensate drain tray which shall be duly insulated with 13mm thick class O nitrile rubber insulation. The contractor to furnish the GA drawings of AHU prior to ordering with necessary technical catalogues and fan curve selections. The noise level near the AHU should not cross more than 60dbA at 1m away from the unit. Also the AHU shall have a prefilter of MERV 8 with necessary framework. AHU body frame shall be with Aluminium . AHU shall have TEFC Squirrel Cage IP 55 Protected VFD Compatible induction motor, copper header, Copper to MS adopter, vibration isolation pad. Scope also includes limit switch with lights inside AHU. AHUs shall be selected for a maximum face velocity of 500 FPM (2.5MPS) and as per schedule of air handling units. Fan outlet velocity shall not exceed 1600 FPM (8.12 MPS). Chilled water inlet Outlet temp to be 8 13.5°C. AHUs shall be of following design parameters Capacity Tonnage ESP No. of USGPM (Cfm) TR (mm WG) Rows 11200 25 40 4 6 60 |  | No | 1.000 | 0.00 | 0.00
4 | a | VRF FLOOR MOUNTED AIR HANDLING UNIT SITC of double skin floor mounted AHU with suitable plug type fans with rated 3phase motor. The thickness of panel to be with 42+ -3mm thick PUF Insulation. The coil shall be of hard copper tubes covered by aluminium fins with 13-15 FPI. The AHU to have a SS condensate drain tray which shall be duly insulated with 13mm thick class O nitrile rubber insulation. The contractor to furnish the GA drawings of AHU prior to ordering with necessary technical catalogues and fan curve selections. The noise level near the AHU should not cross more than 60-65dbA at 3m away from the unit. Also the AHU shall have a prefilter of MERV 8 with necessary framework. AHU body frame shall be with Aluminium. AHU shall have TEFC Squirrel Cage IP 55 Protected VFD Compatible induction motor, and vibration isolation pads. Scope also includes limit switch with lights in AHU. Cooling Coil section with AHRI certified Coil (0.15mm AL 13 FPI fins 12.7 mm OD 27 SWG Cu Tube) suitable for VRF Outdoor Unit (R410a refrigerant). AHUs shall be selected for a maximum face velocity of 500 FPM (2.5MPS) and as per schedule of air handling units. Fan outlet velocity shall not exceed 1600 FPM (8.12 MPS). AHUs shall be of following design parameters Capacity Tonnage ESP No. of (Cfm) TR (mm WG) Rows 10500 27 40 4 6 |  | No. | 1.000 | 0.00 | 0.00
5 | a | SUPPLY OF VRF OUT-DOOR UNITS Supply of air cooled variable refrigerant flow modular type ODUs each comprising of multiple rotary scroll compressors fully inverter driven, full charge of refrigerant gas (R-410a), lubricating oil and all accessories as per the specifications. TheODUs shall be suitable for operation on 415 ± 10% volts, 50Hz, 3 phase AC power supply and the condensing units shall be of following capacities OUTDOOR UNITS 34 HP at site conditions. Note The unit shall be selected taking indoor and ambient deration, refrigerant pipe length deration in to account. |  | No. | 1.000 | 0.00 | 0.00
6 |  | AHU CONTROLLER AND EEV KIT - Supply of AHU Controller, Electronic Expansion Valve (EEV) Kit and all other necessary accessories to connect with VRF ODU s. |  | No. | 1.000 | 0.00 | 0.00
7 |  | FRAME WORK - Supply, fabrication and installation of PCC Siporex blocks for AHU support. AHU framework shall be part of AHU supply. Each AHU shall require 9nos. of blocks. |  | Sets | 3.000 | 0.00 | 0.00
8 |  | SPARE FILTER - One set of MERV 8 throw away type filters to be provided for all AHUs. These filters will be used for commissioning. Original set of filters will be installed as instructed by Architect Consultants. |  | Sets | 2.000 | 0.00 | 0.00
9 |  | GENERAL NOTES a. Fan outlet velocity - 1600 FPM b. Contractor shall submit static pressure calculation for all above units to Client Consultant. c. Any change in motor HP shall be made at no extra cost to client. d. Fan efficiency shall be minimum 75% e. The cost shall be included liftting shifting of each equipment material with all necesaary arrnagement. Also, it shall be included the cost of scaffloding required for Installation of such material equipment. |  |  | 0.000 | 0.00 | 0.00
10 |  | VENTILATION SYSTEM INLINE CIRCULAR FAN SITC of Inline Circular fan (silent type) with speed control, direct drive package - motor with outlet dampers, fan inlet outlet flexible connection, hanging arrangement with vibration isolators etc. Power will be provided 5 ft away from fan and necessary control wiring with plug will be provided by AC contractor. Motor efficiency IE2 IE3, AMCA Certification and Noise levels at 1m distance to be specified.The fans shall have BMS Compatibility. |  |  | 0.000 | 0.00 | 0.00
11 | a | 700 CFM @ 25 mmwg ESP |  | Nos | 2.000 | 0.00 | 0.00
12 | b | 100 CFM @ 15 mmwg ESP |  | No | 1.000 | 0.00 | 0.00
13 |  | NOTES a. Contractor shall submit static pressure calculation for all above units to Client Consultant. b. Any change in motor HP shall be made at no extra cost to client. c. The cost shall be included liftting shifting of each equipment material with all necesaary arrnagement. Also, it shall be included the cost of scaffloding required for Installation of such material equipment. |  |  | 0.000 | 0.00 | 0.00
14 |  | HVAC Low side Work |  | NOS | 1.000 | 0.00 | 0.00
15 |  | Note Prices shall be based on supply, installation, testing commissioning (SITC) at site including all taxes, duties, transportation insurance etc. |  |  | 0.000 | 0.00 | 0.00
16 | 2.1 | CHILLED WATER PIPING WITH INSULATION |  |  | 0.000 | 0.00 | 0.00
17 |  | CHW PIPE SITC of MS Heavy duty class C ERW Chilled Water pipe conforming to IS 1239 - 2004 primer painted including bends, tees, MS supports, PUFF saddles, anchor fasteners, steel angles and any other material required to complete the work. The piping flange connection bolts, washers and nuts should be hot dipped galvanised. Flourscent Plastic Sticker or paint shall be applied to indicate Water flow directions. Only End flanges to be used for capping of pipes. inch inch Table E inch inch of BS code for flange thickness to be adhered. Dia 50 mm |  | Rmt | 15.000 | 0.00 | 0.00
18 |  | CHILLED WATER PIPING INSULATION SITC of insulation for chilled water. piping. For internal pipe - Stick 25mm thick Nitrile rubber Insulation with anti microbial coating, sealing all joints. putting all joints at 300 mm intervals with PVC bands and finally sealing with 3M glass cloth vapour barrier. Dia 50 mm |  | Rmt | 15.000 | 0.00 | 0.00
19 | a | BUTTERFLY VALVES SITC of CI Butterfly valves shall be wafer type, bi-directional Butterfly valves MSS SP-67; ANSI Class 150 carbon steel body conforming to ASTM A216, Type WCB, TFE seats and TFE packing, stainless steel (SS410) PTFE coated shafts, matching flanges, locking devices extended flow control lever, insulation, nuts, bolts and neoprene gasket etc. Valve should be suitable for 16 kg or Sq.cm Pressure. Make Advance or Audco or Kirlsokar F 50 mm |  | Nos. | 4.000 | 0.00 | 0.00
20 | a | Y-STRAINER - SITC of following sizes of Carbon steel type Y-strainer with matching flanges, Staineless steel mesh, bolts, supports etc. Valve should be suitable for 16 kg or Sq.cm. Pressure. F 50 mm |  | Nos. | 1.000 | 0.00 | 0.00
21 | a | PIBCV VALVES SITC of Pressure Independent Balancing cum Control Valves (PIBCV) including integrated motorised control valve and balancing device for combined flow and water balancing requirement. Valve body to be rated for PN 16. The valve design flow rate should be factory calibrated with + or - 5% flow accuracy. Valve shall have necessary measuring ports, drain port, flanges etc., Valve shall also provide temperature sensor with necessary cabling (min 5mtr length to be considered with each valve). The balancing to be done through microprocessor based hand held terminal or POT and the same results shall be furnished in the water balancing report as part of commissioning report and handing over manual. F 50 mm |  | Nos. | 1.000 | 0.00 | 0.00
22 | b | BALL VALVE SITC of following sizes of Brass Ball Valve consist of Cap, matching flanges, bolts, supports, etc. Valve should be suitable for 16 kg or Sq.cm. Pressure. Dia 20 m |  | Nos. | 2.000 | 0.00 | 0.00
23 | a | Auto Air Vent Valves Providing and fitting Auto Vent Valves. SITC of Auto air vent in each risers common headers AHU. 3 or 4 inch inch auto vent valves at each coil or riser or header |  | Nos. | 2.000 | 0.00 | 0.00
24 |  | SITC of Pressure gauges Thermometers - Necessary pressure gauges and thermometers 4 inch Dial type. |  |  | 0.000 | 0.00 | 0.00
25 | a | Pressure gauges Range 0-10 Kg or CM2 |  | Nos. | 2.000 | 0.00 | 0.00
26 | b | Thermometer, Range 0-50 deg C |  | Nos. | 2.000 | 0.00 | 0.00
27 | c | Thermowells |  | Nos. | 4.000 | 0.00 | 0.00
28 |  | DRAIN PIPING - SITC of UPVC Drain Pipe from unit drain pans to nearest floor drain, complete with all screwed joints and providing fixing in position the necessary elbows, tees, reducers, interconnection, flanges, P-trap, connector to floor trap along with 9mm thick tubular nitrile rubber insulation. |  |  | 0.000 | 0.00 | 0.00
29 | a | 40mm dia. |  | Rmt. | 10.000 | 0.00 | 0.00
30 | b | 32mm dia. |  | Rmt. | 15.000 | 0.00 | 0.00
31 | c | 25mm dia. |  | Rmt. | 20.000 | 0.00 | 0.00
32 |  | NOTES FOR PIPING a Cover all open pipe ends with muslin cloth during construction b Pipe cleaning chemical treatment as per specs shall be included in the piping cost. c Unit rates for all indicated sizes of pipes valves shall be furnished. d Cleaning or Painting of pipe before insulation shall be included in piping cost. e The piping support should be as per tender specification and additional supports are to be provided Contractor as decided by Consultant. f All the valves shall be insulated with the same material as that of Chilled water pipng and cost of insulation for valves shall be considered. |  |  | 0.000 | 0.00 | 0.00
33 | 3 | INDIGENOUS WORK |  |  | 0.000 | 0.00 | 0.00
34 | a | INSTALLATION OF VRF OUT-DOOR UNITS with Controller EEV KIT Installation, Charging, Testing and commissioning of VRF system with Environment friendly refrigerant for the below mentioned system along with controller and EEV kit. This shall include lifting, shifting and positioning of outdoor units, nitrogen leak testing, oil charging, vaccumisation etc., 34H |  | No. | 1.000 | 0.00 | 0.00
35 | a | VRF REFRIGERANT PIPING FITTING WITH INSULATION SITC of high pressure copper refrigerant piping suitable for R 410a refrigerant of suitable size as required and duly insulated with 19mm thick closed cell elastomeric insulation in tubing form. External Refrigerant piping shall be laid on GI covered cable trays. Piping inside occupied spaces shall be supported using GI ladder type cable trays throughtout. Entire refrigerant piping work be carried out in accordance with the specifications. 10500 CFM AHU with 34HP VRF ODU s Note Referiferant piping shall include liquid + gas pipe with all necessory fittings. Also, the size of the same shall be as per manufactured standard |  | Rmt | 50.000 | 0.00 | 0.00
36 | 3.3 | Additional gas charging - Over and above standard Gas charging quantity |  | Kg | 25.000 | 0.00 | 0.00
37 |  | REFNET JOINTS - SITC of Special Refrigerant T-joints for VRV units |  | No | 1.000 | 0.00 | 0.00
38 |  | POWER CABLING - Supply, Laying, Testing Commissioning of Power cabling with PVC armoured copper cable with terminations between ODU and ELCB. Power to ELCB to be provided near each ODU by electrical contractor (Supply to be provided within 3 metres near ODU). |  |  | 0.000 | 0.00 | 0.00
39 | a | 10 sqmm 4 core |  | Rmt | 100.000 | 0.00 | 0.00
40 | c | 8 SWG Copper Wire |  | Rmt | 200.000 | 0.00 | 0.00
41 | a | COMMUNICATION CABLE SITC of communication cables between outdoor units and indoor units and Indoor to Indoor units, ODU and Intelligent Touch Controller. 1.5 sqmm 2 cor |  | Rmt | 90.000 | 0.00 | 0.00
42 | b | CABLE TRAYS Supplying Fixing of following sizes of GI cable tray duly painted perforated type of height 75mm along with necessary bends, reducers etc. anchored along the wall or suspended from the ceiling with necessary MS supports. 300mm wide |  | Rmt | 200.000 | 0.00 | 0.00
43 |  | FRAMEWORK FOR VRF ODU - Supply, Fabrication and Installation of MS frame using channels or angle iron sections as required for mounting of air cooled remote condenser in service areas or terrace level. The frame work shall be applied with red oxide primer and thereafter, two coats of enamel paint of approved colour. The general arrangement drawing for frame work shall be got approved from the Architects or Structural Engineers prior to commencement of fabrication. |  | No. | 2.000 | 0.00 | 0.00
44 | Note : | Quantities of refrigerant piping and cabling are based on the drawings with Indoor Outdoor units Locations shown and for the specified configuration. Vendor to confirm refrigerant piping and cabling quantities based on the system configuration being offered by them. |  |  | 0.000 | 0.00 | 0.00
45 | a | DX DUCTABLE UNITS SITC of Ductable Split units with Inverter compressor and R407c or R410a referigerant gas. The units should be complete with indoor unit, condensing unit, controls, control panel, wiring, refrigerant piping, gas charging, etc. The control cabling and insulated refrigerant piping should be based on the distance between indoor unit and condensing unit being 50 Mtr or Ckt. Unit shall have corded remote. Refrigerant piping slope to be maintained towards condensing unit. Make Bluestar or Carrier or Daikin or Voltas or Bluestar 3.0 TR Ducted unit with condensing units |  | Nos. | 2.000 | 0.00 | 0.00
46 | a | REFERERANT PIPING WITH 13MM INSULATION SITC of Refrigerant piping with pressure testing, vacuum refrigerant charging with 13mm thick nitrile rubber tubular insulation Piping Make Maxflow or Mandev or Heling Insulation Make Armaflex K-flex 3.0 TR Ducted unit with condensing units |  | Rmt | 100.000 | 0.00 | 0.00
47 |  | POWER CONTROL CABLE Supply, laying, dressing, testing and commissioning of 1100V grade copper conductor, galvanized steel wire or strip armoured XLP, PVC sheathed power and control cables of following sizes to be laid on trays or wall or racks including clamping and earthing as per Specification. Cabling to be provided from starter panel to the individual unit including necessary termination. Make Polycab, KEI Finolex |  |  | 0.000 | 0.00 | 0.00
48 | a | Power Cabling between the MCB`s or MCCB`s and the Air Conditioning unit |  | Rmt | 20.000 | 0.00 | 0.00
49 | b | Control Cabling between indoor outdoor units |  | Rmt | 120.000 | 0.00 | 0.00
50 |  | FRAME WORK Supply, fabrication, installation of MS base frame or platform for outdoor units as mentioned in the drawing which shall be completed with vibration isolation pads, supports, hangers, railing, brackets etc. Construction as approved by Architect or Consultant. Apply 2 coats of paint Finish painting to be as approved by Architect. Outdoor unit structure with access ladder to be provided by A.C contractor |  | Nos | 2.000 | 0.00 | 0.00
51 |  | MCB FOR DX ODU - SITC of IP65 rated PVC enclosure with 16A TPN MCB For HVAC Outdoor Units |  | Nos. | 2.000 | 0.00 | 0.00
52 |  | Note All cables conduits to be FRLS. MCCB s earthing of required rating sizes shall be provided by Electrical contractor. |  |  | 0.000 | 0.00 | 0.00
53 | 6 | SHEET METAL WORKS |  |  | 0.000 | 0.00 | 0.00
54 |  | GI SHEET RECTANGULAR METAL DUCTING - Supply, Fabrication, Testing, and Commissioning of Factory Fabricated GI Sheet Metal 180GSM Rectangular boxed ducting, Plenums, Cowls, Elbows with turning vanes, Splitters, Reducers, Flanges, Collars etc as per SMACNA standards, The complete ducting shall be provided with MS Supports, Rods, Angles, Flanges, Bracing, Rubber Gaskets, Wooden frames, Canvas Connections, etc. as per drawings and specifications. |  |  | 0.000 | 0.00 | 0.00
55 | a | 18 Gauge GI Sheet Metal Duct (Above 2001mm Plenum) |  | Sq.mtr | 15.000 | 0.00 | 0.00
56 | b | 20 Gauge GI Sheet Metal Duct (1101-2000mm) |  | Sq.mtr | 10.000 | 0.00 | 0.00
57 | c | 22 Gauge GI Sheet Metal Duct (601-1100mm) |  | Sq.mtr | 250.000 | 0.00 | 0.00
58 | d | 24 Gauge GI Sheet Metal Duct (0-600mm) |  | Sq.mtr | 300.000 | 0.00 | 0.00
59 | a | GI SHEET ROUND METAL DUCTING Supply, Fabrication, Testing, Air Flow Balancing and Commissioning of Factory Fabricated GI Sheet Metal 180GSM Round ducting, Splitters, Flanges, Collars etc as per SMACNA standards. The complete ducting shall be provided with MS Supports, Rods, Angles, Flanges, Bracing, Rubber Gaskets, etc. as per drawings and specifications. 24 Gauge GI Sheet Metal Duct (0-600mm) |  | Sq.mtr | 25.000 | 0.00 | 0.00
60 |  | AIR BALANCING LEAK TEST - Air balancing activity with calibrated air hood and subsequent air balancing report with consultants approval for entire project. Also, cost shall include light or smoke test of complete duct length. |  | Lot | 1.000 | 0.00 | 0.00
61 |  | EXTRUDED ALUMINIUM GRILLES - SITC of Aluminium extruded powder coated 150mm width grilles model EP-00 or 15 or 30 with four side flanges, etc. |  |  | 0.000 | 0.00 | 0.00
62 | a | Linear Grille |  | Sq.mtr | 10.000 | 0.00 | 0.00
63 | b | Curve Grille |  | Sq.mtr | 3.000 | 0.00 | 0.00
64 |  | EXTRUDED ALUMINIUM CEILING SQUARE DIFFUSER - Supply, Installation, Testing and Balancing of supply return air diffusers as per the approved shop drawings and specifications. Each diffuser shall be equipped with fixed air distribution grid, removable key-operated volume control damper, complete with insulated plenum box. The diffusers shall be anti-smudge ring or flush type. Powder coated extruded aluminium diffusers of approved colour shade of following sizes |  |  | 0.000 | 0.00 | 0.00
65 |  | Supply Air Square Diffuser with Plenum Box Control Damper - 225x225mm Neck Size |  | Nos. | 4.000 | 0.00 | 0.00
66 |  | Return Air Round Diffuser - 225x225mm Neck Size |  | No. | 4.000 | 0.00 | 0.00
67 |  | EXTRUDED ALUMINIUM CEILING ROUND DIFFUSER Supply, Installation, Testing and Balancing of supply return air diffusers as per the approved shop drawings and specifications. Each diffuser shall be equipped with fixed air distribution grid, removable key-operated volume control damper, complete with insulated plenum box. The diffusers shall be anti-smudge ring or flush type. Powder coated extruded aluminium diffusers of approved colour shade of following sizes Supply Air Round Diffuser with Plenum Box Control Damper 300mmF Neck Size |  | Nos. | 2.000 | 0.00 | 0.00
68 |  | MULTI LEAF VOLUME CONTROL DAMPER SITC of opposed blade aerofoil type 1.2 mm thick Anodized Aluminium volume control dampers for ducts shall be provided with concealed gears, plastic operator and quadrants for manual control of volume of air flow and for proper balancing of the air distribution system as per the approved shop drawings and specifications. Makes Dynacraft or Cosmos |  | Sq.mtr | 2.000 | 0.00 | 0.00
69 |  | OPPOSED BLADE DAMPER - SITC of Aluminium Opposed blade dampers black powder coated vertical blades type for supply air collar. The damper should be gear operated type. |  | Sq.mtr | 2.000 | 0.00 | 0.00
70 |  | MOTORISED FIRE DAMPER - Supply, installation, testing and commissioning of UL 555 or UL 555 S motorized fire or smoke dampers at wall or floor crossing consist of 2.0 Hours rating, 16G GI frame blade, 20G GI casing, brass bushing for friction free operation, S.S jamb seal for minimum leakage, ON or OFF type actuator with transformer etc. as per specification and approved shop drawings. (Actuators of 24VAC built with Auxiliary switch provides feedback for BMS systems) |  |  | 0.000 | 0.00 | 0.00
71 | a | Fire or Smoke damper |  | Sq.mtr | 4.000 | 0.00 | 0.00
72 | b | Actuator with trnasformer |  | Nos. | 7.000 | 0.00 | 0.00
73 | c | Control logic wiring for shutting all fire dampers in each AHU s, when AHU is OFF for any reason. |  | Lot | 1.000 | 0.00 | 0.00
74 |  | JET NOZZLE Supply, Installation, Testing and Balancing of Powder coated extruded aluminium Jet nozzles with shutter type damper etc. as per the approved shop drawings and specifications. 325mm F Neck Size |  | Nos. | 30.000 | 0.00 | 0.00
75 | a | DISC VALVE SITC of Aluminium powder coated Disc valve suitable for exhausting toilet foul air, comprising of an adjustable centre cone and coupling sleeve made of Aluminium sheet duly epoxy painted with approved color. 150mmF |  | Nos. | 18.000 | 0.00 | 0.00
76 |  | PRE-INULATED FLEXIBLE DUCT - SITC of following sizes of insulated flexible ducting with its matching supports, clamps and square to round pieces and other accessories fittings etc. The flexible duct shall me made of triple lamination of aluminium foil, polyester and metalised polyester film permanently bonded to a coated spring steel wire helix. The exterior shall be wrapped with 25mm thick 16 kg or cum fibreglass insulation. The outer insulation jacket or vapour barrier made of fibreglass reinforced metalised polyester film laminate. |  |  | 0.000 | 0.00 | 0.00
77 | a | 350mmF |  | Rmt | 30.000 | 0.00 | 0.00
78 | b | 300mmF |  | Rmt | 5.000 | 0.00 | 0.00
79 | c | 250mmF |  | Rmt | 5.000 | 0.00 | 0.00
80 | d | 150mmF |  | Rmt | 20.000 | 0.00 | 0.00
81 | 6.14 | CANVAS CONNECTION |  |  | 0.000 | 0.00 | 0.00
82 |  | Supply fixing of fire rated flexible Canvas connections between mouth piece and initial piece of ducting with inspection zip. |  |  | 0.000 | 0.00 | 0.00
83 | a | For AHU |  | Nos | 2.000 | 0.00 | 0.00
84 | b | For Fan |  | Nos | 2.000 | 0.00 | 0.00
85 |  | NOTES The ducting support should be as per tender specification and additional supports are to be provided by Contractor as decided by Consultant. Muslin cloth cover for all air outlets during construction. Air Flow balancing and Pressure testing of complete duct work as per DW or SMACNA standard. Light testing or smoke testing shall be employed for leaks Silicon sealant for longitudinal transverse joints as per specification. Jet Nozzle, Diffusers grilles shall be powder coated as per color approved by Architect. |  |  | 0.000 | 0.00 | 0.00
86 |  | THERMAL INSULATION FOR DUCTS - Supply fixing of Thermal insulation for supply air duct using 13mm thick class inch O inch Closed cell nitrile rubber with anti-microbial coating on it. Insulation shall have Thermal conductivity of 0.033 W or (m.K) and water vapor permeance of 0.10. Joints should be sealed with 50 mm wide 3 mm thick self adhesive tape. The duct shall be stick with recommended adhesive. |  | Sq.mtr | 410.000 | 0.00 | 0.00
87 |  | ACOUSTIC INSULATION FOR DUCTS - Supply fixing acoustic insulation for ducting using Class inch 1 inch closed cell elastomeric insulation of 10mm thick Nitrile rubber insulation adhesive, longitudinal transverse joints sealed with adhesive in neat clean manner. Material shall be processed Nitrile Rubber foam with anti-microbial protection. Insulation shall have thermal conductivity of 0.047 W or (m.K) and density of 140 - 180 kg or m³. |  | Sq.mtr | 30.000 | 0.00 | 0.00
88 |  | ACOUSTIC INSULATION FOR AHU ROOM - Supply fixing of Acoustic insulation for plant room using 50mm thick Twiga 300 rigid board stick using shalikote primer and GI frame work. Insulation to be covered with glass fiber cloth finally with 24 G perforated Al. sheet. |  | Sq.mtr | 75.000 | 0.00 | 0.00
89 |  | Note a. Insulation work to be coordinated with other agencies and repair to be included by contractor as per site requirement. b. Vendors to take care of the installation, if any damages takes place the vendor to repair or replace and hand over to clients in good and acceptable condition. c. Thermal insulation shall be internal for Elliptical or Expossed ducting. |  |  | 0.000 | 0.00 | 0.00
90 | 8 | ELECTRICAL WORKS |  |  | 0.000 | 0.00 | 0.00
91 |  | STARTER PANEL - SITC of indoor or outdoor, wall mounting type 3PH, 415VAC MOTOR STARTERS IN CRCA SHEET STEEL ENCLOSURE with necssary supporting brackets and required accessories, etc., The Enclosure shall be provided with knockouts suitable for cable termination at TOP BOTTOM for incoming and outgoing power cables of A2XFY type and size specified. The starters shall be complete with suitable MPCB or MCCB, Contactor, Bi-metal O or L relay with SPP, ON or OFF Push buttons, on or off or trip indication Lamp, on off push button, phase indication Lamp. Selection of relay, contractor, MPCB or MCCB etc. as per Type-2 Coordination. |  |  | 0.000 | 0.00 | 0.00
92 | a | 11200 CFM AHU - 7.5KW, 3PH, Starter Delta type |  | No. | 1.000 | 0.00 | 0.00
93 | b | 10500CFM AHU - 7.5KW, 3PH, Starter Delta type |  | No. | 1.000 | 0.00 | 0.00
94 |  | MCB FOR VRF ODU - SITC of IP65 rated PVC enclosure with 40A TPN MCB For HVAC Outdoor Units |  | Nos. | 2.000 | 0.00 | 0.00
95 |  | POWER CABLING - Supply, handling, laying effecting proper connections testing and commissioning of following sizes of 1.1 KV grade XLPE insulated FRLS Aluminium or Copper conductor cables laid over MS supports cable racks or fixing on walls including clamping the cable to supports in an approved manner as required complete with Copper earthing as specified for continuous earthing along with cable. All complete as required and as per final instruction as given by Owners or Consultants and as per Technical specifications. Earthing shall be measured separately and shall be connected in two runs. Power to ELCB to be provided near each ODU by electrical contractor. |  |  | 0.000 | 0.00 | 0.00
96 |  | Power Cable CU 6 sqmm 6 core - 7.5KW |  | Rmt | 20.000 | 0.00 | 0.00
97 |  | Earthing 8 SWG GI Earthing |  | Rmt | 40.000 | 0.00 | 0.00
98 | a | CABLE TERMINATION Supply Making of Cable termination of armoured or unarmoured cables 1.1 KV grade including installation of cable glands, cable lugs (Aluminium for A2XFY copper for 2XFY YY Double compression type), heat shrinkable sleeves on long ends, crimping paste etc. The work includes testing commissioning of cables, meggaring values submitting reports of tests. (One set includes termination of all cores of one end only). All crimping tools dies shall be arranged by contractor. CU 6 sqmm 6 core - 7.5KW |  | Nos. | 2.000 | 0.00 | 0.00
99 | a | CABLE TRAYS Supplying Fixing of following sizes of GI cable tray duly painted perforated type of height 50mm along with necessary bends, reducers etc. anchored along the wall or suspended from the ceiling with necessary MS supports. 150mm wide |  | Rmt | 15.000 | 0.00 | 0.00
100 |  | Kitchen Ventilation High side Work |  | NOS | 1.000 | 0.00 | 0.00
101 |  | Note Prices shall be based on supply, installation, testing commissioning (SITC) at site including all taxes, duties, transportation insurance etc. |  |  | 0.000 | 0.00 | 0.00
102 | 1 | VENTILATION SYSTEM |  |  | 0.000 | 0.00 | 0.00
103 | a | KITCHEN EXHAUST AIR FAN SITC of SISW Centrifugal Blower, Belt Direct Drive, Statically Dynamically Balanced, Backward Curved Impeller fan, Dunlop Anti- Vibration Pads etc. Motor should be outside stream with TEFC squirrel cage, weather protection shield, IP 55 rating with Class F Insulation, suitable for 3phase, 415volts, 50hz power supply. Sound level should be 60dB @ 3mtr distance. Fan should be painted with 2 coat of zinc chromate primer and 2 coats Epoxy paint. The quote shall include with MS frame, starter panel along with its required cable. Supplied with Dunlop Anti- Vibration Pads Canvass Connection. (Vendor to crosscheck static pressure calculation). 5000 CFM, 60mm Static (Class F) |  | No | 1.000 | 0.00 | 0.00
104 | a | INDUSTRIAL GRADE ELECTROSTATIC AIR CLEANER SITC of Dry scrubber – Electrostatic Air cleaner with starter panel as per specifications, suitable for following capacities, including electrical starter panel . The Air filtration efficiency should be between 90 to 95% units shall be staked one above other or side by side as per site requirement, if vendor will propose multiple units. Finishing - Power coated, Dark Blue Operating voltage - 220 Vac+ or -10%, 50 Hz (Single phase) Features - Short circuit, arc protection and auto restore power supply, BMS (Building Management System) terminals provided, Auto power cut-off when door is opened, Indicator LEDs for normal or wash indicator, Set of Terminals for remote LED normal or wash indicator Efficiency - Upto 95%, meets NIOSH 5026 Oil Mist Test Particle Size - Collects particles as small as 0.01 microns Motor - Sealead ball bearings UL, single phase. Cell - Ionizing voltage - 12 KVdc Collector voltage - 6 KVdc One cell comprising of 9 ionizing wires and 25 collection plates Controls - Auto cut-off when door is opened. Indicator lights for fault, normal or wash function. Pre-filter - Aluminium mesh, washable Dry contact for BMS. 5000 CFM |  | No | 1.000 | 0.00 | 0.00
105 |  | FRAMEWORK FOR FANS - Supply, Fabrication and Installation of MS frame using channels or angle iron sections as required for mounting of ventilation fans scrubber in areas shown in the layout. The frame work shall be applied with red oxide primer and thereafter, two coats of enamel paint of approved colour. The general arrangement drawing for frame work shall be got approved from the Architects or Structural Engineers prior to commencement of fabrication. |  |  | 0.000 | 0.00 | 0.00
106 | a | Exhaust Fan - 5000CFM |  | Lot | 1.000 | 0.00 | 0.00
107 | b | Dry Scrubber - 5000 CFM |  | Lot | 1.000 | 0.00 | 0.00
108 |  | Note a. Fan outlet velocity - 1600 FPM b. All cabinet fans should have plenum section. c. Fresh air fan if any,should to have 6mm thick synthetic media washable filter with framework. d. Contractor shall submit static pressure calculation for all above units to Client or Consultant. e. Any change in motor HP or coil selection shall be made at no extra cost to client. f. Fan efficiency shall be minimum 75% g. The cost shall be included liftting shifting of each equipment or material with all necesaary arrnagement. Also, it shall be included the cost of scaffloding required for Installation of such material or equipment. |  |  | 0.000 | 0.00 | 0.00
109 |  | Kitchen Ventilation Low side Work |  | NOS | 1.000 | 0.00 | 0.00
110 |  | Note Prices shall be based on supply, installation, testing commissioning (SITC) at site including all taxes, duties, transportation insurance etc. |  |  | 0.000 | 0.00 | 0.00
111 |  | SHEET METAL WORKS |  |  | 0.000 | 0.00 | 0.00
112 |  | GI SHEET METAL DUCTING - Supply, Fabrication, Testing, Air Flow Balancing and Commissioning of Factory Fabricated GI Sheet Metal 180GSM Rectangular boxed ducting, Plenums, Cowls, Elbows, Splitters, Reducers, Flanges, Collars etc as per SMACNA standards, The complete ducting shall be provided with MS Supports, Rods, Angles, Flanges, Bracing, Rubber Gaskets, Wooden frames, Canvas Connections, etc. as per drawings and specifications. |  |  | 0.000 | 0.00 | 0.00
113 |  | 22 Gauge GI Sheet Metal Duct (601-1100mm) |  | Sq.mtr | 50.000 | 0.00 | 0.00
114 |  | 24 Gauge GI Sheet Metal Duct (0-600mm) |  | Sq.mtr | 150.000 | 0.00 | 0.00
115 |  | SS EXHAUST AND FRESH AIR GRILLS - SITC of 18G SS 304 Fresh Air Grilles adjustable Double Deflector With S.S Volume Control Dampers. Grills to be of Double Deflection Type for ease of deflection on all sides. |  | Sq.mtr | 0.750 | 0.00 | 0.00
116 |  | DOOR TRANSFER GRILLE SITC of Aluminium extruded powder coated Door transfer grills. Door transfer grille (Back to Back) |  | Sq.mtr | 0.250 | 0.00 | 0.00
117 |  | MULTI LEAF VOLUME CONTROL DAMPER - SITC of opposed blade aerofoil type 1.2 mm thick Anodized Aluminium volume control dampers for ducts shall be provided with concealed gears, plastic operator and quadrants for manual control of volume of air flow and for proper balancing of the air distribution system as per the approved shop drawings and specifications. |  | Sq.mtr | 2.500 | 0.00 | 0.00
118 |  | CURTAIN TYPE FIRE DAMPER - SITC of curtain type fire dampers consist of 16G GI frame, 20G GI interlocking blades secured with SS springs, blades outside airstream clamped with fusible link UL-555 listed with melting point 165 225°F, etc; as per the approved shop drawings and specifications. |  |  | 0.000 | 0.00 | 0.00
119 |  | Bare fire dampers |  | Sq.mtr | 0.300 | 0.00 | 0.00
120 |  | Fusible link as per specification UL 555 and CBRI approved |  | No. | 1.000 | 0.00 | 0.00
121 |  | CANVAS CONNECTION - Supply fixing of flexible Canvas connections between mouth piece and initial piece of ducting. Flexible connections shall be fire resistant made of closely woven, double layer canvass neoprene coated fibre glass. |  |  | 0.000 | 0.00 | 0.00
122 |  | Cabiner Exhaust Fan |  | Nos | 1.000 | 0.00 | 0.00
123 |  | Dry Scrubber |  | Nos | 1.000 | 0.00 | 0.00
124 |  | NOTES The ducting support should be as per tender specification and additional supports are to be provided by Contractor as decided by Consultant. Muslin cloth cover for all air outlets during construction. Pressure testing of complete duct work as per DW SMACNA standard. Silicon sealant for longitudinal transverse joints as per specification. Diffusers grilles shall be powder coated as per color approved by Architect. |  |  | 0.000 | 0.00 | 0.00
125 |  | THERMAL INSULATION SITC of Rockwool roll Insulation with stonewool fibres bonded with thermosetting resins, with factory applied laminated Woven Fiber glass cloth of 271GSM. Nominal density 48 Kg CuM. Thermal conductivity, < 0.042 W m.K at 50°C. All Insulation material and adhesives shall be as per Class O for surface spread and in accordance with BS 476, Class O for non-combustible grade. Also, cost shall include all necessary support and accessories. 50 mm Thick |  | Sq.mtr | 200.000 | 0.00 | 0.00
126 |  | ELECTRICAL WORKS |  |  | 0.000 | 0.00 | 0.00
127 |  | STARTER PANEL with VFD SITC of indoor outdoor, wall mounting type 3PH, 415VAC MOTOR STARTERS IN CRCA SHEET STEEL ENCLOSURE with necssary supporting brackets and required accessories, etc., The Enclosure shall be provided with knockouts suitable for cable termination at TOP BOTTOM for incoming and outgoing power cables of A2XFY type and size specified. The starters shall be complete with suitable MPCB MCCB, Contactor, Bi-metal O L relay with SPP, ON OFF Push buttons, on off trip indication Lamp, on off push button, phase indication Lamp. Selection of relay, contractor, MPCB MCCB etc. as per Type-2 Coordination. Starter panel shall be BMS compatible. Variable frequency drives shall be provided with necessary sensors and controllers complete with control wiring in all respect as required. VFDs shall be provided with necessary bypass arrangement inside electrical starter panels with IP-55 enclosure. 5.5KW, 3PH, DOL Starter type for exhaust air fan |  | No | 1.000 | 0.00 | 0.00
128 |  | POWER CABLING - Supply, handling, laying effecting proper connections testing and commissioning of following sizes of 1.1 KV grade XLPE insulated FRLS Aluminium Copper conductor cables laid over MS supports cable racks or fixing on walls including clamping the cable to supports in an approved manner as required complete with Copper earthing as specified for continuous earthing along with cable. All complete as required and as per final instruction as given by Owners Consultants and as per Technical specifications. Earthing shall be measured separately and shall be connected in two runs. Power to ELCB to be provided near each ODU by electrical contractor. Power Cable |  |  | 0.000 | 0.00 | 0.00
129 |  | CU 2.5 sqmm 4 core - Exhaust Fan |  | Rmt | 10.000 | 0.00 | 0.00
130 |  | CU 2.5 sqmm 3 core - Dry Scrubber |  | Rmt | 10.000 | 0.00 | 0.00
131 |  | Earthing - 8 SWG GI Earthing |  | Rmt | 20.000 | 0.00 | 0.00
132 |  | CABLE TERMINATION Supply Making of Cable termination of armoured unarmoured cables 1.1 KV grade including installation of cable glands, cable lugs (Aluminium for A2XFY copper for 2XFY YY Double compression type), heat shrinkable sleeves on long ends, crimping paste etc. The work includes testing commissioning of cables, meggaring values submitting reports of tests. (One set includes termination of all cores of one end only). All crimping tools dies shall be arranged by contractor. CU 2.5 sqmm 4 core - Exhaust Fan |  | Nos. | 2.000 | 0.00 | 0.00
133 |  | CABLE TRAYS Supplying Fixing of following sizes of GI cable tray duly painted perforated type of height 50mm along with necessary bends, reducers etc. anchored along the wall suspended from the ceiling with necessary MS supports. 150mm wide |  | Rmt | 20.000 | 0.00 | 0.00