## Summary
Common Seating | Pioneer (R0) | Pioneer (R1) | Pioneer (Auction) | Anjle (R0) | Anjle (R1) | Anjle (Auction) | Crystal (R0) | Crystal (R1) | Crystal (Auction) | Fallow Dezience
HVAC | 4367550 | 4194542 | 4050000 | 6386575 | 4802200 | 4808980 | 5555239 | 4796492 | 4025750 | 4146522.5
Fire Sprinkler System | 165800 | 145400 | 140000 | 168250 | 149450 | 145450 | 218750 | 176150 | 150000 | 154500
FAS | 40600 | 31525 | 30000 | 31525 | 31525 | 30525 | 55325 | 42125 | 37000 | 38110
Total | 4573950 | 4371467 | 4220000 | 6586350 | 4983175 | 4984955 | 5829314 | 5014767 | 4212750 | 4339132.5
KFC | Pioneer (R0) | Pioneer (R1) | Pioneer (Auction) | Anjle (R0) | Anjle (R1) | Anjle (Auction) | Crystal (R0) | Crystal (R1) | Crystal (Auction) | Crystal (Auction)
Fire Panel | 110300 | 92250 | 88000 | 233200 | 92400 | 92400 | 112400 | 99300 | 85000 | 87550
Fire Sprinkler System | 149600 | 125850 | 115000 | 158200 | 135150 | 125150 | 166350 | 139600 | 120000 | 123600
Total | 259900 | 218100 | 203000 | 391400 | 227550 | 217550 | 278750 | 238900 | 205000 | 211150
| 4833850 | 4589567 | 4423000 | 6977750 | 5210725 | 5202505 | 6108064 | 5253667 | 4417750 | 4550282.5

## Common Seating Area
[5 empty] | Pioneer (R0) |  | Pioneer (R1) |  | Pioneer (Auction) |  | Anjle (R0) |  | Anjle (R1) |  | Anjle (Auction) |  | Crystal (R0) |  | Crystal (R1) |  | Crystal (Auction)
[5 empty] | Unit Price | Amount | Unit Price | Amount | Unit Price | Amount | Unit Price | Amount | Unit Price | Amount | Unit Price |  | Unit Price | Amount | Unit Price | Amount | Unit Price | Amount
1 |  | Common HVAC | NOS | 1 |  | 4367550 |  | 4194542 |  | 4050000 |  | 6386575 |  | 4802200 |  | 4808980 |  | 5555239 |  | 4796492 |  | 4025750
126 | Part A | VRF EQUIPMENTS (Hi Side Works)
127 | 1 | VRV VRF UNITS (Supply Part)
128 |  | Outdoor Unit (Heat Pump)
129 | 1.1 | Supply of Variable refrigerant volume flow modular type air-conditioning system suitable to operate from 415±10% volt, 50 Hz,single three phase AC power supply for Heating Cooling by using inverter driven capa`city control compressors (Hermetically sealed scroll DC Twin Rotary type) complete with individual controller and fittings with necessary wiring, connection, including suitable isolator for each selected module, termination etc. M.S. frame duly painted to locate Outdoor Unit etc. as per quantity given below including full charging of R-410A refrigerant gas complete as per specifications.
130 | 1.1.1 | 20 HP (Three Phase) | Nos | 1 | 350000 | 350000 | 350000 | 350000 | 350000 | 350000 | 465000 | 465000 | 415000 | 415000 | 425000 | 425000 | 384275 | 384275 | 360000 | 360000 | 302400 | 302400
131 | 1.1.2 | 18 HP (Three Phase) | Nos | 1 | 340000 | 340000 | 340000 | 340000 | 340000 | 340000 | 435000 | 435000 | 405000 | 405000 | 415000 | 415000 | 369632 | 369632 | 350000 | 350000 | 294000 | 294000
132 | 1.2 | Indoor Units
133 |  | Supply of following Indoor units equipped with pre-filter, fan section with low noise fan, multispeed motor, coil section with DX coil, outer cabinet, drain pan, insulation, pipe connections, corded cordless remote control etc. of various capacities as per specifications and drawings.
134 | a) | Ceiling Mounted Duct Type
135 | 1.2.1 | 1377 CFM (4.0 TR 5.0 HP) | Nos | 1 | 60000 | 60000 | 40055 | 40055 | 40055 | 40055 | 95000 | 95000 | 55000 | 55000 | 60000 | 60000 | 40055 | 40055 | 40055 | 40055 | 33646 | 33646
136 | 1.2.2 | 2047 CFM (5.5 TR 6.9 HP) | Nos | 2 | 68000 | 136000 | 68000 | 136000 | 68000 | 136000 | 115000 | 230000 | 72500 | 145000 | 72500 | 145000 | 95345 | 190690 | 73000 | 146000 | 61320 | 122640
137 | b) | 4 Way Cassette Type
138 | 1.2.3 | 4.0 TR (5.0 HP) 1218 CFM | Nos | 3 | 42500 | 127500 | 41319 | 123957 | 41319 | 123957 | 65600 | 196800 | 42000 | 126000 | 52000 | 156000 | 41319 | 123957 | 41319 | 123957 | 34707 | 104121
139 | c) | 1 Way Cassette Type
140 | 1.2.4 | 1.3 TR (1.6 HP) 346 CFM | Nos | 1 | 45600 | 45600 | 39245 | 39245 | 39245 | 39245 | 43500 | 43500 | 40500 | 40500 | 40500 | 40500 | 39245 | 39245 | 39245 | 39245 | 32965 | 32965
141 | 1.2.5 | 1.6 TR (2.0 HP) 441 CFM | Nos | 1 | 48600 | 48600 | 40096 | 40096 | 40096 | 40096 | 50500 | 50500 | 41500 | 41500 | 41500 | 41500 | 40096 | 40096 | 40096 | 40096 | 33680 | 33680
142 | d) | Hi Wall
143 | 1.2.6 | 530 CFM Hi Wall Type (1.6TR) | Nos | 1 | 26500 | 26500 | 24739 | 24739 | 24739 | 24739 | 28500 | 28500 | 24500 | 24500 | 24500 | 24500 | 24739 | 24739 | 24739 | 24739 | 20780 | 20780
144 |  | Sub-Total Part- A Rs.
145 | Part B | VRF EQUIPMENTS (Low Side Works)
146 | 1 | VRV VRF UNITS
147 |  | Outdoor Unit (Heat Pump)
148 | 1.1 | Installation, testing commissioning of Variable refrigerant volume flow modular type air-conditioning system suitable to operate from 415±10% volt, 50 Hz,single three phase AC power supply for Heating Cooling by using inverter driven capa`city control compressors (Hermetically sealed scroll DC Twin Rotary type) complete with individual controller and fittings with necessary wiring, connection, including suitable isolator for each selected module, termination etc. M.S. frame duly painted to locate Outdoor Unit etc. as per quantity given below including full charging of R-410A refrigerant gas complete as per specifications.
149 | 1.1.1 | 20 HP (Three Phase) | Nos | 1 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 55000 | 55000 | 35000 | 35000 | 35000 | 35000 | 60000 | 60000 | 40000 | 40000 | 33600 | 33600
150 | 1.1.2 | 18 HP (Three Phase) | Nos | 1 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 48500 | 48500 | 35000 | 35000 | 30000 | 30000 | 54000 | 54000 | 35000 | 35000 | 29400 | 29400
151 | 1.2 | Indoor Units
152 |  | Installation , Testing and Commissioning of following Indoor units equipped with pre-filter, fan section with low noise fan, multispeed motor, coil section with DX coil, outer cabinet, drain pan, insulation, pipe connections, corded remote control etc. of various capacities as per specifications and drawings.
153 | a) | Ceiling Mounted Duct Type
154 | 1.2.1 | 1377 CFM (4.0 TR 5.0 HP) | Nos | 1 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 10500 | 10500 | 4500 | 4500 | 4500 | 4500 | 5500 | 5500 | 4500 | 4500 | 3780 | 3780
155 | 1.2.2 | 2047 CFM (5.5 TR 6.9 HP) | Nos | 2 | 5500 | 11000 | 5500 | 11000 | 5500 | 11000 | 12500 | 25000 | 5500 | 11000 | 5500 | 11000 | 6500 | 13000 | 6000 | 12000 | 5040 | 10080
156 | b) | 4 Way Cassette Type
157 | 1.2.3 | 4.0 TR (5.0 HP) 1218 CFM | Nos | 3 | 3000 | 9000 | 3000 | 9000 | 3000 | 9000 | 5500 | 16500 | 3000 | 9000 | 3000 | 9000 | 4800 | 14400 | 4000 | 12000 | 3360 | 10080
158 | c) | 1 Way Cassette Type
159 | 1.2.4 | 1.3 TR (1.6 HP) 346 CFM | Nos | 1 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 4500 | 4500 | 3000 | 3000 | 3000 | 3000 | 2550 | 2550 | 2550 | 2550 | 2142 | 2142
160 | 1.2.5 | 1.6 TR (2.0 HP) 441 CFM | Nos | 1 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 4500 | 4500 | 3000 | 3000 | 3000 | 3000 | 2550 | 2550 | 2550 | 2550 | 2142 | 2142
161 | b) | Hi Wall
162 | 1.2.6 | 530 CFM Hi Wall Type (1.6TR) | Nos | 1 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 2500 | 2500 | 20000 | 20000 | 3000 | 3000 | 2250 | 2250 | 2000 | 2000 | 1680 | 1680
163 | 1.3.1 | Corded Remote Control (SITC) | Nos. | 5 | 4500 | 22500 | 4500 | 22500 | 4500 | 22500 | 5500 | 27500 | 4500 | 22500 | 5500 | 27500 | 6500 | 32500 | 5000 | 25000 | 4200 | 21000
164 | 1.3.2 | Cordless Remote Control (SITC) | Nos. | 4 | 4000 | 16000 | 4000 | 16000 | 4000 | 16000 | 5500 | 22000 | 4500 | 18000 | 5500 | 22000 | 4500 | 18000 | 4000 | 16000 | 3360 | 13440
165 |  | Sub-Total Part- B Rs.
166 | Part C | VENTILATION EQUIPMENTS
167 | 1 | Kitchen Scrubber (Dry Type)-With Fan Section
168 | 1.1 | Supply , Installation, Testing and Commissioning of Dry Type Scrubber each comprising of extract air intake section, electrostatic precipitation technology, dry type air cleaner to remove oil, smoke and fumes from exhaust air, as per the Specifications. Electrostatic section shall be made of 16 gauge galvanised sheet, high bake epoxy powder coated, washable type aluminium mesh filters, stainless steel spiked ionizers to create high voltage DC field, aluminum collector plates which should be alternatively charged positive and negative with large collecting area with 14 deep cell, to work as magnet for charged smoke and oil particles. Average efficiency of 90-95% in single pass as per ASHRAE test method. Electrostatic Precipitator should be able to charge particles from 0.01 micron to 10 microns through solid state power supply. Collector cell should be of permanent type and incorporate slide out facility for easy removal for cleaning. Power supplies shall be 100% solid state UL Listed, Module of capacity above 3000 CFM shall be equipped with Pulse width modulating (PWM)
169 |  | The system should be fitted with interlock switch for safety . The system should allow connection to a fan section to achieve 500 FPM velocity across the air
170 |  | Operating Voltage 220V, 50 Hz
171 |  | Ionizing Voltage 12.5 to 13 KVDC
172 |  | Collector Cell Voltage 6 to 6.5 KVDC
173 |  | Power Consumption Not more than 50W per cell.
174 | 1.2 | DIDW Blower
175 |  | DIDW Blower, motor, V belt drive, A.V mounting, supports etc. as per Specifications Drawings
176 | 1.3 | Casing
177 |  | Factory fabricated Double Skin construction shall have 25 mm thick PUF injected Panels having density 42Kg Cum with 0.6 mm pre-plasticized pre-coated Galvanised steel sheet outside 0.6 mm plain Galvanised steel sheet inside and fixed on 30x30 mm hollow extruded aluminium section. Casing shall be appropriately housed both Electrostatic Modules and Fan with Drive.
178 | 1.4 | Accessories
179 |  | The cost shall include all accessories like Adjusting motor brackets,base,vee drive belt pulleys, vibration isolators, internal frame works ,canvas connection, Inlet Outlet flange connection etc
180 |  | 17000 CMH (10000 CFM) DIDW Blower Capacity at 65 MM ESP 7.5 KW (3 Phase) motor | Nos | 1 | 525000 | 525000 | 525000 | 525000 | 525000 | 525000 | 1245000 | 1245000 | 525000 | 525000 | 515000 | 515000 | 590125 | 590125 | 548000 | 548000 | 460320 | 460320
181 | 2 | Package Type Air Washers (Floor Mounted)
182 |  | Supply , Installation , testing commissioning Of Double Skin Floor Mounted Type Packaged Air Washer with extruded aluminium section with 0.6 mm preplasticized precoated GI sheet outside and 0.6 mm plain Galvanized sheet inside, minimum of 25 mm thick PUF insulation of 38KG m3 , Backward Curved DIDW Blowers , base , drive arrangement ,Filter, 200 mm thick cooling pad section, SS-304 sump tank and housing, motor drive, water circulation pump,4 Bend PVC Eliminators, piping, valves fittings etc. suitable for Outdoor Application as per specifications and drawings .
183 | 2.1 | 14450 CMH(8500 CFM) ,55 mm ESP , 5.5 KW Motor | Nos. | 1 | 265000 | 265000 | 265000 | 265000 | 265000 | 265000 | 515000 | 515000 | 315000 | 315000 | 310000 | 310000 | 304500 | 304500 | 275000 | 275000 | 231000 | 231000
184 |  | Sub-Total Part- C Rs.
185 | Part D | LOW SIDE WORKS
186 | 1 | Piping
187 | 1.1 | Refrigerant Piping
188 | 1.1.1 | VRF VRV SYSTEM
189 |  | Interconnecting refrigerant copper pipe work suitable for R-410A refrigerant with (19mm 13mm thick) closed cell elastomeric nitrile rubber tubular insulation between each set of indoor outdoor units as per specifications, all piping inside the room shall be properly supported with MS slotted covered cable trays(on building exterior) and suitably suspended from ceiling inside the area.
190 | a. | 6.4 mm O.D.(insulation 13 mm) | RM | 4 | 550 | 2200 | 550 | 2200 | 550 | 2200 | 950 | 3800 | 650 | 2600 | 750 | 3000 | 1150 | 4600 | 675 | 2700 | 567 | 2268
191 | b. | 9.5 mm O.D.(insulation 13 mm) | RM | 36 | 650 | 23400 | 650 | 23400 | 650 | 23400 | 1150 | 41400 | 850 | 30600 | 850 | 30600 | 1350 | 48600 | 750 | 27000 | 630 | 22680
192 | c. | 12.7 mm O.D (insulation 19 mm). | RM | 18 | 850 | 15300 | 850 | 15300 | 850 | 15300 | 1450 | 26100 | 1050 | 18900 | 1050 | 18900 | 1550 | 27900 | 950 | 17100 | 798 | 14364
193 | d. | 15.9 mm O.D.(insulation 19 mm) | RM | 148 | 950 | 140600 | 950 | 140600 | 950 | 140600 | 1650 | 244200 | 1250 | 185000 | 1200 | 177600 | 1650 | 244200 | 1050 | 155400 | 882 | 130536
194 | e. | 19.1 mm O.D.(insulation 19 mm) | RM | 8 | 1050 | 8400 | 1050 | 8400 | 1050 | 8400 | 1850 | 14800 | 1450 | 11600 | 1450 | 11600 | 2250 | 18000 | 2250 | 18000 | 1890 | 15120
195 | f. | 22.2 mm O.D.(insulation 19 mm) | RM | 10 | 1250 | 12500 | 1250 | 12500 | 1250 | 12500 | 2250 | 22500 | 1650 | 16500 | 1650 | 16500 | 2550 | 25500 | 1500 | 15000 | 1260 | 12600
196 | g. | 28.6 mm O.D.(insulation 19 mm) | RM | 144 | 1450 | 208800 | 1450 | 208800 | 1450 | 208800 | 2650 | 381600 | 2450 | 352800 | 2320 | 334080 | 2850 | 410400 | 2650 | 381600 | 2226 | 320544
197 | 1.2 | Drain Piping
198 | 1.2.1 | 32 mm PVC Pipe with 9 mm insulation | RM | 40 | 180 | 7200 | 180 | 7200 | 180 | 7200 | 450 | 18000 | 250 | 10000 | 250 | 10000 | 190 | 7600 | 185 | 7400 | 155 | 6200
199 | 1.2.2 | 25 mm PVC Pipe with 9 mm insulation | RM | 25 | 160 | 4000 | 155 | 3875 | 155 | 3875 | 350 | 8750 | 210 | 5250 | 210 | 5250 | 155 | 3875 | 155 | 3875 | 130 | 3250
200 | 1.2.3 | 20 mm PVC Pipe with 9 mm insulation | RM | 15 | 140 | 2100 | 140 | 2100 | 140 | 2100 | 320 | 4800 | 210 | 3150 | 210 | 3150 | 155 | 2325 | 150 | 2250 | 126 | 1890
201 | 1.3 | Providing Fixing of Imported fittings Y-joints and headers etc. (9 IDU s and 2 ODU s) | Lot | 1 | 30000 | 30000 | 6500 | 6500 | 6500 | 6500 | 6500 | 6500 | 6500 | 6500 | 6500 | 6500 | 31500 | 31500 | 30000 | 30000 | 25200 | 25200
202 | 1.4 | Supplying, fixing, testing and commissioning of Main centralized controller Push Button Type suitable for groups of indoor outdoor units to be installed for control. (BMS Compatible). | Nos | 0 | 85000 | 0 | 85000 | 0 | 0 | 0 | 175000 |  |  |  | 165000 | [5 empty] | 0
203 | 5 | DUCTING
204 | 5.1 | G.I. Sheet Metal Ducting - Factory Fabricated
205 |  | Supply, Installation, Testing and Commissioning of factory fabricated GSS sheet metal rectangular ducting complete with neoprene rubber gaskets, elbows, splitter dampers, vanes, hangers, supports etc. as per approved drawings and specifications of following sheet thickness complete as required.
206 | 5.1.1 | 0.50 MM (26 Gauge) | Sqm. | 80 | 1050 | 84000 | 1050 | 84000 | 1050 | 84000 | 1150 | 92000 | 1050 | 84000 | 1050 | 84000 | 1550 | 124000 | 1050 | 84000 | 882 | 70560
207 | 5.1.2 | 0.63 MM (24 Gauge) | Sqm. | 260 | 1150 | 299000 | 1150 | 299000 | 1150 | 299000 | 1250 | 325000 | 1200 | 312000 | 1200 | 312000 | 1630 | 423800 | 1250 | 325000 | 1050 | 273000
208 | 5.1.3 | 0.80 MM (22 Gauge) | Sqm. | 250 | 1350 | 337500 | 1350 | 337500 | 1350 | 337500 | 1450 | 362500 | 1300 | 325000 | 1300 | 325000 | 1850 | 462500 | 1450 | 362500 | 1218 | 304500
209 | 5.1.4 | 1.00 MM (20 Gauge) | Sqm. | 30 | 1550 | 46500 | 1550 | 46500 | 1550 | 46500 | 1650 | 49500 | 1600 | 48000 | 1600 | 48000 | 1980 | 59400 | 1700 | 51000 | 1428 | 42840
210 | 5.1.5 | 1.25 MM (18 Gauge) | Sqm. | 15 | 1750 | 26250 | 1750 | 26250 | 1750 | 26250 | 1850 | 27750 | 1850 | 27750 | 1850 | 27750 | 2080 | 31200 | 1900 | 28500 | 1596 | 23940
211 | 5.2 | G.I. Sheet Metal Ducting - Site Fabricated
212 |  | Supply,Installation, Testing and Commissioning of site fabricated GSS sheet metal rectangular ducting complete with neoprene rubber gaskets, elbows, splitter dampers, vanes, hangers, supports etc. as per approved drawings and specifications of following sheet thickness complete as required.
213 | 5.2.1 | 0.63 MM (24 Gauge) | Sqm. | 60 | 1250 | 75000 | 1150 | 69000 | 1150 | 69000 | 1150 | 69000 | 1150 | 69000 | 1150 | 69000 | 1630 | 97800 | 1250 | 75000 | 1050 | 63000
214 | 5.2.2 | 0.80 MM (22 Gauge) | Sqm. | 5 | 1450 | 7250 | 1350 | 6750 | 1350 | 6750 | 1350 | 6750 | 1350 | 6750 | 1350 | 6750 | 1850 | 9250 | 1350 | 6750 | 1134 | 5670
215 | 5.2.3 | 1.00 MM (20 Gauge) | Sqm. | 0 | 1650 |  | #N/A |  | 0 | [5 empty] | 1550 | [5 empty] | 0
216 | 5.2.4 | 1.25 MM (18 Gauge) | Sqm. | 0 | 1850 |  | #N/A |  | 0 | [5 empty] | 1750 | [5 empty] | 0
217 | 5.4 | Flexible Duct
218 | 5.4.1 | 200 MM Dia | RM | 0 | 550 |  | 550 |  | 0 | [5 empty] | 1250 | [5 empty] | 0
219 | 6 | INSULATION
220 | 6.1 | Nitrile Rubber Insulation- Class O
221 |  | Supplying and fixing of closed cell elastomeric insulation of following thickness and density 55 kg cu.m.and K valueof not less than 0.037W mk at 20 deg C as per specifications and drawings (For indoor applications) with factory Laminated 7 mill woven glass cloth
222 | 6.1.1 | 19 mm thick (AC Fresh Air Duct ) | Sqm. | 340 | 750 | 255000 | 750 | 255000 | 750 | 255000 | 850 | 289000 | 750 | 255000 | 750 | 255000 | 1200 | 408000 | 1100 | 374000 | 924 | 314160
223 | 6.1.2 | 25 mm thick (Exhaust Air Duct ) | Sqm. | 320 | 950 | 304000 | 950 | 304000 | 950 | 304000 | 1050 | 336000 | 1020 | 326400 | 1020 | 326400 | 1350 | 432000 | 1250 | 400000 | 1050 | 336000
224 | 6.2 | Acoustic Lining
225 |  | Supplying and Application of Acoustic lining within the Supply Air duct with 10 mm thick class O open cell nitrile Rubber of density 140-160 kg. Cubm. as per spefications.
226 | 6.2.1 | 15 MM Thick | Sqm | 30 | 1450 | 43500 | 1450 | 43500 | 1450 | 43500 | 1450 | 43500 | 1450 | 43500 | 1450 | 43500 | 1450 | 43500 | 1450 | 43500 | 1218 | 36540
227 | 7 | DUCT ACCESSORIES
228 | 7.1 | Supply,Installation, Testing and Commissioning of GI multiblade volume control duct damper complete with neoprene rubber gaskets, nuts, bolts, screws linkages, flanges etc., as per specifications. | Sqm. | 1.5 | 6500 | 9750 | 6500 | 9750 | 6500 | 9750 | 6850 | 10275 | 6500 | 9750 | 6500 | 9750 | 8750 | 13125 | 7500 | 11250 | 6000 | 9000
229 | 7.2 | Supply,Installation, Testing and Commissioning of multiblade Al volume control Collar Grille exhaust Air Opening damper complete with suitable links, lever and quadrants for manual control of airflow and with suitable links , lever and quadrants for manual control of airflow and neoprene rubber gaskets, nuts, bolts, screws, flanges etc., as per specifications. | Sqm. | 2.5 | 10500 | 26250 | 9500 | 23750 | 8500 | 21250 | 10500 | 26250 | 9500 | 23750 | 9500 | 23750 | 9500 | 23750 | 9500 | 23750 | 7500 | 18750
230 | 7.3 | Supply,Installation, Testing and Commissioning fixing of powder coated extruded aluminium Supply Exhaust Air Grills as per specifications (zero degree deflection) | Sqm. | 2 | 7500 | 15000 | 7500 | 15000 | 7500 | 15000 | 8700 | 17400 | 7500 | 15000 | 7500 | 15000 | 7800 | 15600 | 7500 | 15000 | 6000 | 12000
231 | 7.8 | Supply,Installation, Testing and Commissioning fixing of powder coated extruded aluminium Continuos Grills as per specifications
232 | 7.8.1 | 150 MM Wide | RM | 20 | 1800 | 36000 | 1450 | 29000 | 1450 | 29000 | 1450 | 29000 | 1450 | 29000 | 1450 | 29000 | 1800 | 36000 | 1450 | 29000 | 1218 | 24360
233 | 7.8.2 | 200 MM Wide | RM | 15 | 2200 | 33000 | 1650 | 24750 | 1650 | 24750 | 1650 | 24750 | 1650 | 24750 | 1650 | 24750 | 2200 | 33000 | 1750 | 26250 | 1470 | 22050
234 | 7.8.3 | Scaffolding for ducting work | Job | 1 | 25000 | 25000 | 2500 | 2500 | 2500 | 2500 | 75000 | 75000 | 45000 | 45000 | 65000 | 65000 | 2500 | 2500 | 2500 | 2500 | 2100 | 2100
235 |  | Sub-Total Part D Rs.
236 | Part E | ELECTRICAL WORKS
237 | 1 | Electrical Work
238 | 1 | Electrical Control Panel
239 |  | Supply, installation, testing and commissioning of panel boards made of 2.0 mm thick steel sheet duly powder coated with voltmeter, ammeter, electronic energy meter, indicating lights, Stop manual Auto selector switch in each, outgoing current operated single phase preventer. The starters should have potential free contacts for connection to Building Automation System. The panel shall include contactors over load relay with built in single phase protection Time delay relay for delayed automatic start of the motor. All panels should have spare NO NC Contacts for BMS applications as required.
240 | 1.1.1 | Panel-P01 (Kitchen Ventilation)
241 |  | (1 x 7.5 KW + 1 x 5.5 KW )
242 |  | INCOMER
243 | -- | 1 No. incoming 40 Amps TP+N MCB
244 | -- | 1 No. Digital Type voltmeter with selector switch with control MCB
245 | -- | 1 No. Digital Type Ammeter 0-80 A with C.T. s and selector switch.
246 | -- | 1 Set of RYB indication lamps with control MCB
247 | -- | 1 No. of 80 Amps Aluminium conductor 25kA bus bar duly sleeved as required.
248 |  | OUTGOING
249 |  | 1 Nos. 32 Amps TPN MCB
250 |  | 1 Nos. 40 Amps TPN MCB
251 |  | 1 No. DOL starter for 5.5 KW Motor
252 |  | 1 No. star delta starter for 7.5 KW Motor
253 |  | 2 Nos. of single phase preventor (current based-MPRD2)
254 |  | 2 Nos. Digital Type Ammeter
255 |  | Each star-delta DOL starter consists of current operated MN type over load relay, contactor, push button, ON OFF indication light | Set | 1 | 55000 | 55000 | 45000 | 45000 | 45000 | 45000 | 85000 | 85000 | 65000 | 65000 | 55000 | 55000 | 45000 | 45000 | 45000 | 45000 | 37000 | 37000
256 | 2 | Cables
257 | 2.1 | Supplying, laying, testing and commissioning of XLPE insulated aluminium conductor armored cables of 1.1 KV grade of following sizes directly on wall structural frame cable trays or racks using approved type of clamps,End terminations with Double Compression type glands on both ends, double earthing with GI strip wire of suitable size and hardware as per specifications.
258 | i. | 3 C x 10 Sq. mm | Mtrs | 0 |  |  |  |  | 0 |  | 960 |  |  |  | 1250 | [5 empty] | 0
259 | ii. | 3 C x 6 Sq. mm | Mtrs | 0 |  |  |  |  | 0 |  | 760 |  |  |  | 850 | [5 empty] | 0
260 | iii. | 3 C x 4 Sq. mm | Mtrs | 50 | 250 | 12500 | 250 | 12500 | 250 | 12500 | 550 | 27500 | 350 | 17500 | 350 | 17500 | 325 | 16250 | 270 | 13500 | 227 | 11350
261 | 3 | Control Transmission Wiring
262 | 3.1 | Providing fixing control cum transmission wiring of 2 core x 1.5 sqmm copper in MS conduits between indoor and out door unit and between indoor units and their remote sensor controller. | RM | 190 | 150 | 28500 | 150 | 28500 | 150 | 28500 | 210 | 39900 | 210 | 39900 | 210 | 39900 | 210 | 39900 | 150 | 28500 | 126 | 23940
263 | 4 | Power Cabling
264 | 4.1 | Indoor Units
265 | 4.1.1 | Providing and fixing flexible power cable of 3 core x 1.5 sqmm copper between Indoor units and their power points | RM | 50 | 150 | 7500 | 150 | 7500 | 150 | 7500 | 190 | 9500 | 150 | 7500 | 150 | 7500 | 200 | 10000 | 175 | 8750 | 147 | 7350
266 | 4.1.2 | Providing and fixing flexible power cable of 3 core x 2.5 sqmm copper between Indoor units and their power points | RM | 10 | 160 | 1600 | 160 | 1600 | 160 | 1600 | 250 | 2500 | 200 | 2000 | 200 | 2000 | 225 | 2250 | 175 | 1750 | 147 | 1470
267 | 5 | Outdoor Units
268 | 5.1.1 | Providing and fixing flexible power cable of 4 core x 10 sqmm copper between Outdoor units and their MCB | RM | 0 |  |  |  |  | 0 |  | 1250 |  |  |  | 950 | [5 empty] | 0
269 | 5.1.2 | Providing and fixing flexible power cable of 4 core x 6 sqmm copper between Outdoor units and their MCB | RM | 80 | 550 | 44000 | 475 | 38000 | 475 | 38000 | 1050 | 84000 | 850 | 68000 | 850 | 68000 | 475 | 38000 | 475 | 38000 | 399 | 31920
270 | 5.1.3 | Providing and fixing flexible power cable of 4 core x 4 sqmm copper between Outdoor units and their MCB | RM | 0 |  |  |  |  | 0 | [5 empty] | 650 | [5 empty] | 0
271 | 6 | Isolator (Weather Proof)
272 | 6.1 | Providing fixing weather proof isolator near each outdoor unit kitchen ventilation units as per specific control drawup.
273 | 6.1.1 | 63 Amp MCCB | Nos | 2 | 12500 | 25000 | 5200 | 10400 | 5200 | 10400 | 9500 | 19000 | 9500 | 19000 | 8500 | 17000 | 5200 | 10400 | 5200 | 10400 | 4367 | 8734
274 | 6.1.2 | 32 Amp MCB | Nos | 1 | 10500 | 10500 | 4200 | 4200 | 4200 | 4200 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4200 | 4200 | 4200 | 4200 | 3528 | 3528
275 | 6.1.3 | 16 Amp MCB | Nos | 1 | 10500 | 10500 | 1500 | 1500 | 1500 | 1500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 1500 | 1500 | 1500 | 1500 | 1260 | 1260
276 | 7 | GI perforated Cable tray
277 |  | Supply,Installation, Testing and Commissioning following size of perforated painted with powder coating M.S. cable trays with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts nuts, painting suspenders etc. as required.
278 | 7.1 | 150 mm width X 50 mm depth X 1.6 mm thickness | RM | 15 | 550 | 8250 | 350 | 5250 | 350 | 5250 | 550 | 8250 | 550 | 8250 | 550 | 8250 | 350 | 5250 | 350 | 5250 | 293 | 4395
279 | 7.2 | 300 mm width X 50 mm depth X 1.6 mm thickness | RM | 15 | 750 | 11250 | 475 | 7125 | 475 | 7125 | 650 | 9750 | 650 | 9750 | 650 | 9750 | 475 | 7125 | 475 | 7125 | 398 | 5970
280 | 7.3 | 450 mm width X 50 mm depth X 2.0 mm thickness | RM | 10 | 850 | 8500 | 525 | 5250 | 525 | 5250 | 850 | 8500 | 850 | 8500 | 850 | 8500 | 525 | 5250 | 525 | 5250 | 439 | 4390
281 | 8 | Earthing
282 |  | Supply,Installation, Testing and Commissioning of the following earthing clamped to wall with suitable clamps saddles and fixing bolts in ground including the cost of digging and back filling as required and complete as required to comply with IS 3043 1987. All copper joints shall be tinned. The rates shall be inclusive of making test joints where ever required
283 | 8.1 | 25 mm x 6 mm GI strip | RM | 25 | 450 | 11250 | 200 | 5000 | 200 | 5000 | 200 | 5000 | 200 | 5000 | 150 | 3750 | 475 | 11875 | 275 | 6875 | 226 | 5650
284 | 8.2 | 8 SWG GI Wire | RM | 25 | 120 | 3000 | 120 | 3000 | 120 | 3000 | 150 | 3750 | 150 | 3750 | 100 | 2500 | 250 | 6250 | 135 | 3375 | 111 | 2775
4 |  | Fire Sprinkler System | NOS | 1 |  | 165800 |  | 145400 |  | 140000 |  | 168250 |  | 149450 |  | 145450 |  | 218750 |  | 176150 |  | 150000
126 | 1 | Providing, Laying, Jointing Testing of Pipes for Sprinkler System - G.I Pipe confirming IS Codes Class `C Heavy Pipe with necessary support anchore fastening from slab.
127 | a. | 25 mm dia | Rft. | 35 | 750 | 26250 | 750 | 26250 | 750 | 26250 | 850 | 29750 | 750 | 26250 | 750 | 26250 | 1200 | 42000 | 1050 | 36750 | 898 | 31430
128 | c. | 40 mm dia | Rft. | 27 | 1050 | 28350 | 1050 | 28350 | 1050 | 28350 | 1050 | 28350 | 1050 | 28350 | 1050 | 28350 | 1400 | 37800 | 1150 | 31050 | 983 | 26541
129 | 2 | Synthetic Enamel Paint.
130 | a. | 25 mm dia | Rft. | 35 | 50 | 1750 | 25 | 875 | 25 | 875 | 50 | 1750 | 50 | 1750 | 50 | 1750 | 300 | 10500 | 150 | 5250 | 129 | 4515
131 | c. | 40 mm dia | Rft. | 27 | 50 | 1350 | 25 | 675 | 25 | 675 | 100 | 2700 | 50 | 1350 | 50 | 1350 | 350 | 9450 | 200 | 5400 | 171 | 4617
132 | 3 | Providing Fixing of Butterfly Valve.
133 | b. | 65 mm dia | No. | 1 | 6500 | 6500 | 6500 | 6500 | 6500 | 6500 | 7250 | 7250 | 6500 | 6500 | 6500 | 6500 | 8500 | 8500 | 7500 | 7500 | 6413 | 6413
134 | 4 | Providing Fixing of Ball Valve.
135 | e. | 65 mm dia | No. | 1 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 6500 | 6500 | 5500 | 5500 | 5500 | 5500 | 7500 | 7500 | 6500 | 6500 | 5558 | 5558
136 | 5 | HEADER FITTING.
137 | a. | Flow Switch | No. | 1 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 8500 | 8500 | 5500 | 5500 | 5500 | 5500 | 8900 | 8900 | 7000 | 7000 | 5985 | 5985
138 | b | Pressure Gauge | No. | 1 | 1850 | 1850 | 1650 | 1650 | 1650 | 1650 | 1650 | 1650 | 1650 | 1650 | 1650 | 1650 | 3950 | 3950 | 2850 | 2850 | 2437 | 2437
139 | c | Air Release Valve | No. | 1 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 2450 | 2450 | 2050 | 2050 | 2050 | 2050 | 3950 | 3950 | 2850 | 2850 | 2437 | 2437
140 | d | 80 mm dia NRV | No. | 1 | 6500 | 6500 | 2850 | 2850 | 2850 | 2850 | 7500 | 7500 | 6500 | 6500 | 4500 | 4500 | 2850 | 2850 | 2850 | 2850 | 2437 | 2437
141 | 6 | Providing Fixing C.P. Brass 68 degree Quartzoid Bulb Sprinklers. Make Tyco viking temp rating standard coverage discharge coefficent k- 6.6 quick response UL listed EN approved.
142 | a. | Pendant Type | No. | 10 | 1650 | 16500 | 1050 | 10500 | 1050 | 10500 | 950 | 9500 | 950 | 9500 | 950 | 9500 | 1900 | 19000 | 1050 | 10500 | 895 | 8950
143 | b. | UP Right Type | No. | 0 |  | 0 |  | 0 | 0 | 0 | 1050 | 0 |  | 0 | 1150 | 0 |  | 0 |  | 0 | 0 | 0
144 | 7 | Providing Fixing C.P. Brass 79 degree(QR) Quartzoid Bulb Sprinklers. Make Tyco viking temp rating standard coverage discharge coefficent k- 6.6 quick response UL listed EN approved for high temperature area in Kitchen temprating shall be 79degre
145 | a. | Pendant Type | No. | 10 | 1850 | 18500 | 1250 | 12500 | 1250 | 12500 | 1150 | 11500 | 1150 | 11500 | 1050 | 10500 | 1850 | 18500 | 1350 | 13500 | 1140 | 11400
146 | 8 | Flexible Sprinkler Drop.
147 | a. | 25mm | No. | 20 | 2250 | 45000 | 2100 | 42000 | 2100 | 42000 | 2450 | 49000 | 2100 | 42000 | 2250 | 45000 | 2100 | 42000 | 2100 | 42000 | 1772 | 35440
148 | 9 | Drain Valve | No. | 1 | 1050 | 1050 | 1050 | 1050 | 1050 | 1050 | 1850 | 1850 | 1050 | 1050 | 1050 | 1050 | 3850 | 3850 | 2150 | 2150 | 1840 | 1840
5 |  | FAS | NOS | 1 |  | 40600 |  | 31525 |  | 30000 |  | 31525 |  | 31525 |  | 30525 |  | 55325 |  | 42125 |  | 37000
149 | 6 | SD (SMOKE DETECTOR ABOVE CEILING) | NOS | 3 | 6200 | 18600 | 4650 | 13950 | 4650 | 13950 | 4650 | 13950 | 4650 | 13950 | 4650 | 13950 | 8000 | 24000 | 6500 | 19500 | 5720 | 17160
150 |  | Providing and fixing electrically operated flow indicating mechanical foam type (ISI marked) An optical smoke detector. Smoke enters through the slits around the side, triggering an electronic horn, which sounds through the large circular opening on the right. The dark circle in the middle is a test button with a built-in LED that flashes to show the detector is working okay.Model Edwards Apollo.
151 | 7 | SD (SMOKE DETECTOR BELOW CEILING) | NOS | 3 | 6000 | 18000 | 4650 | 13950 | 4650 | 13950 | 4650 | 13950 | 4650 | 13950 | 4650 | 13950 | 8150 | 24450 | 6000 | 18000 | 5280 | 15840
152 |  | Providing and fixing electrically operated flow indicating mechanical foam type (ISI marked) An optical smoke detector. Smoke enters through the slits around the side, triggering an electronic horn, which sounds through the large circular opening on the right. The dark circle in the middle is a test button with a built-in LED that flashes to show the detector is working okay. Model Edwards Apollo.
153 |  | Providing and fixing electrically operated flow indicating mechanical foam type (ISI marked) An optical smoke detector. Smoke enters through the slits around the side, triggering an electronic horn, which sounds through the large circular opening on the right. The dark circle in the middle is a test button with a built-in LED that flashes to show the detector is working okay. Model Edwards Apollo. | RMT. | 25 | 160 | 4000 | 145 | 3625 | 145 | 3625 | 145 | 3625 | 145 | 3625 | 145 | 3625 | 275 | 6875 | 185 | 4625 | 160 | 4000

## KFC
[5 empty] | 259900 |  | 218100 |  | 203000 |  | 391400 |  | 227550 |  | 217550 |  | 278750 |  | 238900 |  | 205000
| KFC (Fire Panels & Fire Sprinkler) |  |  | Pioneer Projects (R0) |  | Pioneer Projects (R1) |  | Pioneer Projects (Auction) |  | Anjle (R0) |  | Anjle (R1) |  | Anjle (Auction) |  | Crystal (R0) |  | Crystal (R1) |  | Crystal (Auction)
Sr No. | Item Name | UOM | Qty | Unit Price | Amount | Unit Price | Amount | Unit Price | Amount | Unit Price | Amount | Unit Price | Amount | Unit Price | Amount | Unit Price | Amount | Unit Price | Amount | Unit Price | Amount
1 | Fire Panel | NOS | 1 |  | 110300 |  | 92250 |  | 88000 |  | 233200 |  | 92400 |  | 92400 |  | 112400 |  | 99300 |  | 85000
1 | R1 (RESPONSE INDICATORS)
2 | Providing and fixing electrically operated flow indicating mechanical foam type (ISI marked) Response indicators are connected to automatic fire detectors in order to indicate quickly the source of an alarm signal from detectors which are not easily accessible or visible. They light up as soon as the connected fire detector gives an alarm.(Wiring from switches to panel and stair case pressurization not included) | Nos | 2 | 550 | 1100 | 250 | 500 | 250 | 500 | 250 | 500 | 250 | 500 | 250 | 500 | 350 | 700 | 300 | 600 | 258 | 516
3 | HD (HEAT DETECTOR) INSTALL NEAR HOOD
4 | Providing and fixing electrically operated flow indicating mechanical foam type (ISI marked) A heat detector is a fire alarm device designed to respond when the convected thermal energy of a fire increases the temperature of a heat sensitive element. The thermal mass and conductivity of the element regulate the rate flow of heat into the element. All heat detectors have this thermal lag (Wiring from switches to panel and stair case pressurization not included) (Edwards Apollo) | Nos | 2 | 6000 | 12000 | 5250 | 10500 | 5250 | 10500 | 5050 | 10100 | 5050 | 10100 | 5050 | 10100 | 5500 | 11000 | 5500 | 11000 | 4730 | 9460
5 | MCP (MANUAL CALL POINT)
6 | Providing and fixing electrically operated flow indicating mechanical foam type (ISI marked) Manual call points are used to initiate an alarm signal, and operate by means of a simple button press or when glass is broken revealing a button. They can form part of a manual alarm system or an automatic alarm system.Model Edwards Apollo and FM approved with GI mounting Box | Nos | 1 | 6500 | 6500 | 6500 | 6500 | 6500 | 6500 | 7250 | 7250 | 7250 | 7250 | 7250 | 7250 | 7500 | 7500 | 7000 | 7000 | 6020 | 6020
7 | H (HOOTER)
8 | Providing and fixing electrically operated flow indicating mechanical foam type (ISI marked) Fire Alarm Systems. A fire alarm system is a electrical electronic system which is connected with many type of devices such as main panel, smoke heat detectors, mcp, sounder etc.. to detect the fire event by indiacating audio or visualize signal at the main or individual devices.Model Edwards Apollo with GI mounting Box | Nos | 1 | 6200 | 6200 | 6200 | 6200 | 6200 | 6200 | 145000 | 145000 | 6200 | 6200 | 6200 | 6200 | 7500 | 7500 | 7000 | 7000 | 6020 | 6020
9 | SD (SMOKE DETECTOR ABOVE CEILING)
10 | Providing and fixing electrically operated flow indicating mechanical foam type (ISI marked) An optical smoke detector. Smoke enters through the slits around the side, triggering an electronic horn, which sounds through the large circular opening on the right. The dark circle in the middle is a test button with a built-in LED that flashes to show the detector is working okay.Model Edwards Apollo. | NOS | 4 | 6000 | 24000 | 4850 | 19400 | 4850 | 19400 | 4650 | 18600 | 4650 | 18600 | 4650 | 18600 | 5500 | 22000 | 5000 | 20000 | 4300 | 17200
11 | SD (SMOKE DETECTOR BELOW CEILING)
12 | Providing and fixing electrically operated flow indicating mechanical foam type (ISI marked) An optical smoke detector. Smoke enters through the slits around the side, triggering an electronic horn, which sounds through the large circular opening on the right. The dark circle in the middle is a test button with a built-in LED that flashes to show the detector is working okay. Model Edwards Apollo. | NOS | 6 | 6400 | 38400 | 4850 | 29100 | 4850 | 29100 | 4650 | 27900 | 4650 | 27900 | 4650 | 27900 | 5500 | 33000 | 5000 | 30000 | 4300 | 25800
13 | MSD (MULTI SENSOR DETECTOR BELOW CEILING)
14 | Providing and fixing electrically operated flow indicating mechanical foam type (ISI marked) An optical smoke detector. Smoke enters through the slits around the side, triggering an electronic horn, which sounds through the large circular opening on the right. The dark circle in the middle is a test button with a built-in LED that flashes to show the detector is working okay. Model Edwards Apollo. | NOS | 1 | 6000 | 6000 | 4850 | 4850 | 4850 | 4850 | 4650 | 4650 | 4650 | 4650 | 4650 | 4650 | 5800 | 5800 | 5000 | 5000 | 4300 | 4300
15 | FIRE ALARM SYSTEM LOOPING | RMT. | 60 | 160 | 9600 | 145 | 8700 | 145 | 8700 | 145 | 8700 | 145 | 8700 | 145 | 8700 | 290 | 17400 | 195 | 11700 | 163 | 9780
16 | MONITOR MODULE
17 | Providing and fixing Emonitor module . Model Edwards FMM-1 flash scan type UL listed and FM approved. | NOS | 1 | 6500 | 6500 | 6500 | 6500 | 6500 | 6500 | 10500 | 10500 | 8500 | 8500 | 8500 | 8500 | 7500 | 7500 | 7000 | 7000 | 5904 | 5904
2 | Fire Sprinkler System | NOS | 1 |  | 149600 |  | 125850 |  | 115000 |  | 158200 |  | 135150 |  | 125150 |  | 166350 |  | 139600 |  | 120000
18 | Providing, Laying, Jointing Testing of Pipes for Sprinkler System - G.I Pipe confirming IS Codes Class `C Heavy Pipe with necessary support anchore fastening from slab.
19 | 25 mm dia | Rft. | 25 | 750 | 18750 | 550 | 13750 | 550 | 13750 | 850 | 21250 | 850 | 21250 | 810 | 20250 | 100 | 2500 | 100 | 2500 | 86 | 2150
20 | 32 mm dia | Rft. | 8 | 950 | 7600 | 950 | 7600 | 950 | 7600 | 950 | 7600 | 950 | 7600 | 950 | 7600 | 1200 | 9600 | 1050 | 8400 | 989 | 7912
21 | 40 mm dia | Rft. | 20 | 1050 | 21000 | 1050 | 21000 | 1050 | 21000 | 1050 | 21000 | 1050 | 21000 | 1050 | 21000 | 1300 | 26000 | 1150 | 23000 | 989 | 19780
22 | 50 mm dia | Rft. | 0 |  | 0 |  | 0 | 0 | 0 | 1250 | 0 |  | 0 | 1250 | 0 |  | 0 |  | 0 | 0 | 0
23 | 65mm dia | Rft. | 15 | 1450 | 21750 | 1450 | 21750 | 1450 | 21750 | 1450 | 21750 | 1450 | 21750 | 1450 | 21750 | 1650 | 24750 | 1550 | 23250 | 1333 | 19995
24 | Synthetic Enamel Paint.
25 | 25 mm dia | Rft. | 25 | 50 | 1250 | 25 | 625 | 25 | 625 | 50 | 1250 | 50 | 1250 | 50 | 1250 | 250 | 6250 | 150 | 3750 | 129 | 3225
26 | 32 mm dia | Rft. | 8 | 50 | 400 | 25 | 200 | 25 | 200 | 100 | 800 | 50 | 400 | 50 | 400 | 300 | 2400 | 250 | 2000 | 215 | 1720
27 | 40 mm dia | Rft. | 20 | 50 | 1000 | 25 | 500 | 25 | 500 | 150 | 3000 | 50 | 1000 | 50 | 1000 | 350 | 7000 | 300 | 6000 | 258 | 5160
28 | 65mm dia | Rft. | 15 | 50 | 750 | 25 | 375 | 25 | 375 | 200 | 3000 | 50 | 750 | 50 | 750 | 400 | 6000 | 200 | 3000 | 172 | 2580
29 | Providing Fixing of Butterfly Valve.
30 | 80 mm dia | No. | 1 | 6500 | 6500 | 6000 | 6000 | 6000 | 6000 | 8500 | 8500 | 6000 | 6000 | 7000 | 7000 | 6000 | 6000 | 6000 | 6000 | 5160 | 5160
31 | Providing Fixing of Ball Valve.
32 | 80 mm dia | No. | 1 | 7500 | 7500 | 4000 | 4000 | 4000 | 4000 | 6500 | 6500 | 4000 | 4000 | 2000 | 2000 | 4000 | 4000 | 4000 | 4000 | 3440 | 3440
33 | HEADER FITTING.
34 | Flow Switch | No. | 1 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 9500 | 9500 | 5500 | 5500 | 6200 | 6200 | 6000 | 6000 | 6000 | 6000 | 5160 | 5160
35 | Pressure Gauge | No. | 1 | 1850 | 1850 | 1650 | 1650 | 1650 | 1650 | 1650 | 1650 | 1650 | 1650 | 1650 | 1650 | 8000 | 8000 | 6500 | 6500 | 5590 | 5590
36 | Air Release Valve | No. | 1 | 1200 | 1200 | 800 | 800 | 800 | 800 | 2450 | 2450 | 2450 | 2450 | 1450 | 1450 | 4000 | 4000 | 2500 | 2500 | 2150 | 2150
37 | 80 mm dia NRV | No. | 1 | 6500 | 6500 | 3850 | 3850 | 3850 | 3850 | 7500 | 7500 | 4500 | 4500 | 2000 | 2000 | 3850 | 3850 | 3850 | 3850 | 3311 | 3311
38 | Providing Fixing C.P. Brass 79 degree(QR) Quartzoid Bulb Sprinklers. Make Tyco viking temp rating standard coverage discharge coefficent k- 6.6 quick response UL listed EN approved for high temperature area in Kitchen temprating shall be 79degre
39 | Pendant Type | No. | 12 | 1650 | 19800 | 1250 | 15000 | 1250 | 15000 | 950 | 11400 | 950 | 11400 | 950 | 11400 | 1900 | 22800 | 1050 | 12600 | 903 | 10836
40 | UP Right Type | No. | 0 |  | 0 |  | 0 | 0 | 0 | 1050 | 0 |  | 0 | 1050 | 0 |  | 0 |  | 0 | 0 | 0
41 | Flexible Sprinkler Drop.
43 | 25mm | No. | 12 | 2250 | 27000 | 1850 | 22200 | 1850 | 22200 | 2450 | 29400 | 1950 | 23400 | 2350 | 28200 | 1950 | 23400 | 1950 | 23400 | 1615 | 19380
44 | Drain Valve | No. | 1 | 1250 | 1250 | 1050 | 1050 | 1050 | 1050 | 1650 | 1650 | 1250 | 1250 | 1250 | 1250 | 3800 | 3800 | 2850 | 2850 | 2451 | 2451