## TWC Electrical
[7 empty] | INVENTECH SOLUTIONS (R0) | Vendor Name : INVENTECH SOLUTIONS | INVENTECH SOLUTIONS (R1) | Vendor Name : INVENTECH SOLUTIONS | Arrow Electrical (R1) | Vendor Name : INVENTECH SOLUTIONS | TFS Target
Sr No. | Item Code | Item Name | Item Description | UOM | Qty | Minimum Amount | Unit Price | Amount | Rate | Amount | Rate | Amount | Rate | Amount
1 |  | Electrical Work | Electrical Work | NOS | 1 | 453680 |  | 568755 |  | 457430 |  | 658439 |  | 402630
1 |  | DISTRIBUTION BOARDS - Supply, erection, testing and commissioning of the following sheet steel clad wall recess mounting dust and vermin proof double door type distribution boards constructed from 16 SWG sheet steel IP 42 construction, finished with rust proof duly powder coated in approved shade with hinged gasketed door and housing the following complete with P.V.C. insulated copper busbars rated 200 amp with interconnections, neutral and earth bar assembly per phase, earthing terminals complete as approved by Architects. Note All MCBs in distribuition board for power circuits shall be of C curve | DISTRIBUTION BOARDS - Supply, erection, testing and commissioning of the following sheet steel clad wall recess mounting dust and vermin proof double door type distribution boards constructed from 16 SWG sheet steel IP 42 construction, finished with rust proof duly powder coated in approved shade with hinged gasketed door and housing the following complete with P.V.C. insulated copper busbars rated 200 amp with interconnections, neutral and earth bar assembly per phase, earthing terminals complete as approved by Architects. Note All MCBs in distribuition board for power circuits shall be of C curve
2 |  | Type A - 1-63amp FP MCB with 3 single phase banks each comprising of 63A DP RCCB(100 mA) and 10 nos. 6 or 16 or 20 or 25 amps SP 10 kA MCB(Type C) with thermal magnetic protective releases out goings. (4 way ETPN DB) | Type A - 1-63amp FP MCB with 3 single phase banks each comprising of 63A DP RCCB(100 mA) and 10 nos. 6 or 16 or 20 or 25 amps SP 10 kA MCB(Type C) with thermal magnetic protective releases out goings. (4 way ETPN DB) | Set | 1 | 28500 | 37250 | 37250 | 32250 | 32250 | 28500 | 28500 | 28500 | 28500
3 |  | Type B - 1-20 amp DP MCB + DP RCCB ( 100mA) and 4 nos. 6 or 16 or 20 or 25 amps SP 10 kA MCB(Type D) with thermal magnetic protective releases out goings. (12 way SPN DB) | Type B - 1-20 amp DP MCB + DP RCCB ( 100mA) and 4 nos. 6 or 16 or 20 or 25 amps SP 10 kA MCB(Type D) with thermal magnetic protective releases out goings. (12 way SPN DB) | Set | 1 | 9410 | 9410 | 9410 | 9410 | 9410 | 14200 | 14200 | 9410 | 9410
4 |  | Supply installation testing and commisioning 1.2 kVA online ( 1ph input and 1ph output) UPS with 15 Min power back up complete with in buit Static by pass switch , Mannual external maintenance by pass switch , Rectifiers , Sealed MF batteries etc as required | Supply installation testing and commisioning 1.2 kVA online ( 1ph input and 1ph output) UPS with 15 Min power back up complete with in buit Static by pass switch , Mannual external maintenance by pass switch , Rectifiers , Sealed MF batteries etc as required | No. | 1 | 18000 | 18000 | 18000 | 18000 | 18000 | 75000 | 75000 | 18000 | 18000
5 |  | Supply, laying, testing and commissioning of following sizes of Cu. conductor 1.1 kV grade, armoured, XLPE insulated FRLS LT Cables or Control Cables including necessary cleats, clamps etc. (Cables shall be partly laid in Pipes, O or H cable tray, on wall as required ) | Supply, laying, testing and commissioning of following sizes of Cu. conductor 1.1 kV grade, armoured, XLPE insulated FRLS LT Cables or Control Cables including necessary cleats, clamps etc. (Cables shall be partly laid in Pipes, O or H cable tray, on wall as required )
6 |  | 4C – 16.0 (Cu.) FRLS Armoured XLPE Cable * | 4C – 16.0 (Cu.) FRLS Armoured XLPE Cable * | Mtrs | 60 | 57000 | 1160 | 69600 | 950 | 57000 | 995 | 59700 | 950 | 57000
7 |  | 3C – 4.0 (Cu.) FRLS Armoured XLPE Cable | 3C – 4.0 (Cu.) FRLS Armoured XLPE Cable | Mtrs | 35 | 10500 | 300 | 10500 | 300 | 10500 | 428 | 14980 | 300 | 10500
8 |  | * Approximate and shall be as per point of supply from Airport Panel or Isolator | * Approximate and shall be as per point of supply from Airport Panel or Isolator
9 |  | Supply, erection, testing and commissioning of following sizes of cable end terminations with Single compression gland for 1.1 kV grade, XLPE insulated, Cu Conductor cable | Supply, erection, testing and commissioning of following sizes of cable end terminations with Single compression gland for 1.1 kV grade, XLPE insulated, Cu Conductor cable
10 |  | 4C – 16.0 (Cu.) FRLS Armoured XLPE Cable | 4C – 16.0 (Cu.) FRLS Armoured XLPE Cable | Nos. | 3 | 2235 | 745 | 2235 | 745 | 2235 | 850 | 2550 | 745 | 2235
11 |  | 3C – 4.0 (Cu.) FRLS Armoured XLPE Cable | 3C – 4.0 (Cu.) FRLS Armoured XLPE Cable | Nos. | 3 | 2235 | 745 | 2235 | 745 | 2235 | 350 | 1050 | 745 | 2235
12 |  | Wiring for DB Submains with PVC insulated stranded copper conductor 1100 volt grade wires (FRLS) in surface or concealed MS surface or concealed conduit including cost of providing saddles etc as required for surface conduiting and or or cost of cutting and filling chases as required and making suitable end termination with copper lugs complete as required and as below | Wiring for DB Submains with PVC insulated stranded copper conductor 1100 volt grade wires (FRLS) in surface or concealed MS surface or concealed conduit including cost of providing saddles etc as required for surface conduiting and or or cost of cutting and filling chases as required and making suitable end termination with copper lugs complete as required and as below
13 |  | 2 x 6 sq.mm + 1 No. 4 Sq. mm in 25 mm dia MS Conduit | 2 x 6 sq.mm + 1 No. 4 Sq. mm in 25 mm dia MS Conduit | Mtrs | 100 | 35000 | 350 | 35000 | 350 | 35000 | 412 | 41200 | 350 | 35000
14 |  | 2 x 4 sq.mm + 1 No. 2.5 Sq. mm in 25 mm dia MS Conduit | 2 x 4 sq.mm + 1 No. 2.5 Sq. mm in 25 mm dia MS Conduit | Mtrs | 300 | 62100 | 207 | 62100 | 207 | 62100 | 365 | 109500 | 207 | 62100
15 |  | 2 x 2.5 sq.mm + 1 No. 1.5 Sq. mm in 25 mm dia MS Conduit | 2 x 2.5 sq.mm + 1 No. 1.5 Sq. mm in 25 mm dia MS Conduit | Mtrs | 200 | 29600 | 148 | 29600 | 148 | 29600 | 272 | 54400 | 148 | 29600
16 |  | Supplying and laying of the following earthing clamped to wall with suitable clamps saddles and fixing bolts or in ground including the cost of digging and back filling as required and complete as required to comply with IS 3043 1987. All copper joints shall be tinned. The rates shall be inclusive of making test joints where ever required | Supplying and laying of the following earthing clamped to wall with suitable clamps saddles and fixing bolts or in ground including the cost of digging and back filling as required and complete as required to comply with IS 3043 1987. All copper joints shall be tinned. The rates shall be inclusive of making test joints where ever required
17 |  | 8 SWG Copper Wire | 8 SWG Copper Wire | Mtrs | 35 | 3850 | 140 | 4900 | 110 | 3850 | 110 | 3850 | 110 | 3850
18 |  | 8 SWG GI Wire | 8 SWG GI Wire | Mtrs | 50 | 4500 | 125 | 6250 | 90 | 4500 | 90 | 4500 | 90 | 4500
19 |  | 1 Core 4.0 Sq. Mm FRLS Green Wire | 1 Core 4.0 Sq. Mm FRLS Green Wire | Mtrs | 25 | 1375 | 108 | 2700 | 55 | 1375 | 55 | 1375 | 55 | 1375
20 |  | Wiring for MCB controlled normal primary light points or Wall Point or Floor Point with 1.5 sq. mm PVC insulated stranded copper conductor 1100 Volt grade FRLS wires in 25 mm dia 16 SWG MS conduit in wall or ceiling including cost of cutting and filling chases for recessed conduiting and supports in case of surface conduit including all bends , saddles , Junction boxes etc and including the cost of running 1.5 Sq. mm PVC insulated copper conductor wire for loop earthing etc. complete as required. (Cost of MCB included in the item for per DB). | Wiring for MCB controlled normal primary light points or Wall Point or Floor Point with 1.5 sq. mm PVC insulated stranded copper conductor 1100 Volt grade FRLS wires in 25 mm dia 16 SWG MS conduit in wall or ceiling including cost of cutting and filling chases for recessed conduiting and supports in case of surface conduit including all bends , saddles , Junction boxes etc and including the cost of running 1.5 Sq. mm PVC insulated copper conductor wire for loop earthing etc. complete as required. (Cost of MCB included in the item for per DB). | Pt | 3 | 4500 | 1500 | 4500 | 1500 | 4500 | 4150 | 12450 | 1500 | 4500
21 |  | Wiring for secondary MCB controlled normal light points or Wall Point or Floor Point( Looped from above point) with 1.5 sq. mm PVC insulated stranded copper conductor 1100 Volt grade FRLS wires in 25 mm 16 SWG MS conduit in wall or ceiling including cost of cutting and filling chases for recessed conduiting and supports in case of surface conduit including all bends , saddles , Junction boxes etc and including the cost of running 1.5 Sq mm PVC insulated copper conductor wire for loop earthing etc. complete as required. | Wiring for secondary MCB controlled normal light points or Wall Point or Floor Point( Looped from above point) with 1.5 sq. mm PVC insulated stranded copper conductor 1100 Volt grade FRLS wires in 25 mm 16 SWG MS conduit in wall or ceiling including cost of cutting and filling chases for recessed conduiting and supports in case of surface conduit including all bends , saddles , Junction boxes etc and including the cost of running 1.5 Sq mm PVC insulated copper conductor wire for loop earthing etc. complete as required. | Pt | 3 | 2550 | 850 | 2550 | 850 | 2550 | 2450 | 7350 | 850 | 2550
22 |  | Wiring for MCB controlled Emergency primary light points or Wall Point or Floor Point with 1.5 sq. mm PVC insulated stranded copper conductor 1100 Volt grade FRLS wires in 25 mm dia 16 SWG MS conduit in wall or ceiling including cost of cutting and filling chases for recessed conduiting and supports in case of surface conduit including all bends , saddles , Junction boxes etc and including the cost of running 1.5 Sq. mm PVC insulated copper conductor wire for loop earthing etc. complete as required. (Cost of MCB included in the item for per DB). | Wiring for MCB controlled Emergency primary light points or Wall Point or Floor Point with 1.5 sq. mm PVC insulated stranded copper conductor 1100 Volt grade FRLS wires in 25 mm dia 16 SWG MS conduit in wall or ceiling including cost of cutting and filling chases for recessed conduiting and supports in case of surface conduit including all bends , saddles , Junction boxes etc and including the cost of running 1.5 Sq. mm PVC insulated copper conductor wire for loop earthing etc. complete as required. (Cost of MCB included in the item for per DB). | Pt | 1 | 2250 | 2250 | 2250 | 2250 | 2250 | 4150 | 4150 | 2250 | 2250
23 |  | Wiring for secondary MCB controlled Emergency light points or Wall Point or Floor Point( Looped from above point) with 1.5 sq. mm PVC insulated stranded copper conductor 1100 Volt grade FRLS wires in 25 mm 16 SWG MS conduit in wall or ceiling including cost of cutting and filling chases for recessed conduiting and supports in case of surface conduit including all bends , saddles , Junction boxes etc and including the cost of running 1.5 Sq mm PVC insulated copper conductor wire for loop earthing etc. complete as required. | Wiring for secondary MCB controlled Emergency light points or Wall Point or Floor Point( Looped from above point) with 1.5 sq. mm PVC insulated stranded copper conductor 1100 Volt grade FRLS wires in 25 mm 16 SWG MS conduit in wall or ceiling including cost of cutting and filling chases for recessed conduiting and supports in case of surface conduit including all bends , saddles , Junction boxes etc and including the cost of running 1.5 Sq mm PVC insulated copper conductor wire for loop earthing etc. complete as required. | Pt | 1 | 1200 | 1200 | 1200 | 1200 | 1200 | 2450 | 2450 | 1200 | 1200
24 |  | Wiring for a 5 pin 240 volt 6 amp single phase and neutral switch socket outlet with 2.5 sq. mm PVC insulated stranded copper conductor 1100 Volt grade wires (FRLS) in 25mm dia 16 SWG MS conduit in wall or ceiling including cost of providing circuit wiring with 2.5 sq mm PVC insulated stranded copper conductor 1100 volt grade wires and including cost of cutting and filling chases for recessed conduiting and supports in case of surface conduit including all bends , saddles , Junction boxes etc and providing and fixing of a combined 5 pin 240 volt 6 amp socket outlet with safety shutters and 6 amp 240 volt single pole grid plate mounted switch with moulded cover plate in recessed GI box and including earthing of the 3rd pin with 1.5 sq mm 1100 volt grade PVC insulated stranded copper conductor wires complete as requied( Switch and socket shall be as approved by the architect or Client) | Wiring for a 5 pin 240 volt 6 amp single phase and neutral switch socket outlet with 2.5 sq. mm PVC insulated stranded copper conductor 1100 Volt grade wires (FRLS) in 25mm dia 16 SWG MS conduit in wall or ceiling including cost of providing circuit wiring with 2.5 sq mm PVC insulated stranded copper conductor 1100 volt grade wires and including cost of cutting and filling chases for recessed conduiting and supports in case of surface conduit including all bends , saddles , Junction boxes etc and providing and fixing of a combined 5 pin 240 volt 6 amp socket outlet with safety shutters and 6 amp 240 volt single pole grid plate mounted switch with moulded cover plate in recessed GI box and including earthing of the 3rd pin with 1.5 sq mm 1100 volt grade PVC insulated stranded copper conductor wires complete as requied( Switch and socket shall be as approved by the architect or Client) | Pt. | 2 | 2400 | 1200 | 2400 | 1200 | 2400 | 5710 | 11420 | 1200 | 2400
25 |  | Wiring same as in Item 12 above looped from an adjacent 6 amp switch socket outlet as required and providing and fixing of a modular type 5 pin 240 Volt 6 amp shuttered socket outlet and a modular type 6 amp 240 Volt single pole switch in a recessed GI boxes with internal wiring and moulded front plates complete as required. ( Switch and socket shall be as approved by the architect or Client) | Wiring same as in Item 12 above looped from an adjacent 6 amp switch socket outlet as required and providing and fixing of a modular type 5 pin 240 Volt 6 amp shuttered socket outlet and a modular type 6 amp 240 Volt single pole switch in a recessed GI boxes with internal wiring and moulded front plates complete as required. ( Switch and socket shall be as approved by the architect or Client) | Pt. | 2 | 2400 | 1200 | 2400 | 1200 | 2400 | 3362 | 6724 | 1200 | 2400
26 |  | Wiring for 6 pin 240 volt 16 amp single phase and neutral switch socket outlets (1 outlet wired on 1 circuit) with 2.5 sq. mm PVC insulated stranded copper conductor 1100 volt grade wires (FRLS) in 25mm dia 16 SWG MS conduit in wall or Ceiling including the cost of cutting and filling chases for recessed conduiting and supports in case of surface conduit including all bends , saddles , Junction boxes etc and including providing and fixing 6 pin 240 volt 16 amp socket outlet with safety shutters and 16 amp 240 volt single pole grid plate mounted modular type switch with moulded cover plate in recessed GI box and including earthing of the 3rd pin with 1.5 sq mm 1100 volt grade PVC insulated stranded copper conductor wires and complete as requied( Switch and socket shall be as approved by the architect or Client) | Wiring for 6 pin 240 volt 16 amp single phase and neutral switch socket outlets (1 outlet wired on 1 circuit) with 2.5 sq. mm PVC insulated stranded copper conductor 1100 volt grade wires (FRLS) in 25mm dia 16 SWG MS conduit in wall or Ceiling including the cost of cutting and filling chases for recessed conduiting and supports in case of surface conduit including all bends , saddles , Junction boxes etc and including providing and fixing 6 pin 240 volt 16 amp socket outlet with safety shutters and 16 amp 240 volt single pole grid plate mounted modular type switch with moulded cover plate in recessed GI box and including earthing of the 3rd pin with 1.5 sq mm 1100 volt grade PVC insulated stranded copper conductor wires and complete as requied( Switch and socket shall be as approved by the architect or Client) | Pt. | 3 | 9150 | 3050 | 9150 | 3050 | 9150 | 6100 | 18300 | 3050 | 9150
27 |  | Wiring for 6 pin 240 volt 16 amp single phase and neutral switch socket outlets (1 outlet wired on 1 circuit) with 4.0 sq. mm PVC insulated stranded copper conductor 1100 volt grade wires (FRLS) in 25mm dia 16 SWG MS conduit in wall or Ceiling including the cost of cutting and filling chases for recessed conduiting and supports in case of surface conduit including all bends , saddles , Junction boxes etc and including providing and fixing 6 pin 240 volt 16 amp socket outlet with safety shutters and 16 amp 240 volt single pole grid plate mounted modular type switch with moulded cover plate in recessed GI box and including earthing of the 3rd pin with 2.5 sq mm 1100 volt grade PVC insulated stranded copper conductor wires and complete as requied( Switch and socket shall be as approved by the architect or Client) | Wiring for 6 pin 240 volt 16 amp single phase and neutral switch socket outlets (1 outlet wired on 1 circuit) with 4.0 sq. mm PVC insulated stranded copper conductor 1100 volt grade wires (FRLS) in 25mm dia 16 SWG MS conduit in wall or Ceiling including the cost of cutting and filling chases for recessed conduiting and supports in case of surface conduit including all bends , saddles , Junction boxes etc and including providing and fixing 6 pin 240 volt 16 amp socket outlet with safety shutters and 16 amp 240 volt single pole grid plate mounted modular type switch with moulded cover plate in recessed GI box and including earthing of the 3rd pin with 2.5 sq mm 1100 volt grade PVC insulated stranded copper conductor wires and complete as requied( Switch and socket shall be as approved by the architect or Client) | Pt. | 9 | 36000 | 4000 | 36000 | 4000 | 36000 | 6310 | 56790 | 4000 | 36000
28 |  | Wiring for 6 pin 240 volt 16 amp single phase and neutral switch socket outlets (2 outlets wired on 1 circuit) with PVC insulated stranded copper conductor 1100 volt grade wires (FRLS), 4.0 sq mm upto the first outlet and 2.5 sq mm from first to the second outlet in 25mm dia 16 SWG MS conduit in wall or Ceiling including cost of providing saddles etc as required for surface conduiting and or or cost of cutting and filling chases and including providing and fixing of two sets of 6 pin 240 volt 16 amp socket outlet with safety shutters and 16 amp 240 volt single pole grid plate mounted switches with moulded cover plate in a recessed GI box including earthing of the 3rd pin with 2.5 sq mm 1100 volt grade PVC insulated stranded copper conductor wire complete as required. (Switch or Socket Shall be as per approved sample by Architect) | Wiring for 6 pin 240 volt 16 amp single phase and neutral switch socket outlets (2 outlets wired on 1 circuit) with PVC insulated stranded copper conductor 1100 volt grade wires (FRLS), 4.0 sq mm upto the first outlet and 2.5 sq mm from first to the second outlet in 25mm dia 16 SWG MS conduit in wall or Ceiling including cost of providing saddles etc as required for surface conduiting and or or cost of cutting and filling chases and including providing and fixing of two sets of 6 pin 240 volt 16 amp socket outlet with safety shutters and 16 amp 240 volt single pole grid plate mounted switches with moulded cover plate in a recessed GI box including earthing of the 3rd pin with 2.5 sq mm 1100 volt grade PVC insulated stranded copper conductor wire complete as required. (Switch or Socket Shall be as per approved sample by Architect) | Pt. | 3 | 12000 | 4000 | 12000 | 4000 | 12000 | 6620 | 19860 | 4000 | 12000
29 |  | Wiring for primary switch board consisting of 3 Nos. 5 pin 240 volt 6 amp single phase and neutral switch socket outlets with 3 Nos. 6A switch with PVC insulated stranded copper conductor 1100 volt grade wires (FRLS), 2.5 sq FRLS copper wire mm in 25mm dia 16 SWG MS conduit in wall or Ceiling including cost of providing saddles etc as required for surface conduiting and or or cost of cutting and filling chases and including providing and fixing prewired switch board each consisting of 3 Nos. 5 pin 240 volt 6 amp single phase and neutral switch socket outlets with 3 Nos. 6A modular switch , safety shutters in a recessed or surface GI box including earthing of the 3rd pin with 1.5 sq mm 1100 volt grade PVC insulated stranded copper conductor wire complete as required. (Switch or Socket Shall be as per approved sample by Architect) Note- Conduits shall be 16 SWG MS on surface and FRLS PVC for wall concealed | Wiring for primary switch board consisting of 3 Nos. 5 pin 240 volt 6 amp single phase and neutral switch socket outlets with 3 Nos. 6A switch with PVC insulated stranded copper conductor 1100 volt grade wires (FRLS), 2.5 sq FRLS copper wire mm in 25mm dia 16 SWG MS conduit in wall or Ceiling including cost of providing saddles etc as required for surface conduiting and or or cost of cutting and filling chases and including providing and fixing prewired switch board each consisting of 3 Nos. 5 pin 240 volt 6 amp single phase and neutral switch socket outlets with 3 Nos. 6A modular switch , safety shutters in a recessed or surface GI box including earthing of the 3rd pin with 1.5 sq mm 1100 volt grade PVC insulated stranded copper conductor wire complete as required. (Switch or Socket Shall be as per approved sample by Architect) Note- Conduits shall be 16 SWG MS on surface and FRLS PVC for wall concealed | Pt. | 2 | 8100 | 4050 | 8100 | 4050 | 8100 | 8655 | 17310 |  | 0
30 |  | Supply installation testing and fixing 3 pin 20A , 240V , single Phase metal Clad industrial socket outlet with 20A DP MCB and complete in all respects( Wiring Excluded from scope of this item) | Supply installation testing and fixing 3 pin 20A , 240V , single Phase metal Clad industrial socket outlet with 20A DP MCB and complete in all respects( Wiring Excluded from scope of this item) | Nos. | 4 | 28400 | 12000 | 48000 | 7100 | 28400 | 2850 | 11400 | 2850 | 11400
31 |  | Supply installation testing and fixing 3 pin 25A or 32A , 240V , single Phase metal Clad industrial socket outlet with 25A or 32A DP MCB and complete in all respects( Wiring Excluded from scope of this item) | Supply installation testing and fixing 3 pin 25A or 32A , 240V , single Phase metal Clad industrial socket outlet with 25A or 32A DP MCB and complete in all respects( Wiring Excluded from scope of this item) | Nos. | 5 | 44000 | 15000 | 75000 | 8800 | 44000 | 4500 | 22500 | 4500 | 22500
32 |  | Supply , fixing and Laying 2.0mm Thick FRLS PVC conduits on surface or concealed complete with PVC junction boxes, cover plates, PVC bends, PVC saddles, base and other accessories all made in PVC with GI screws as required to complete the job. . | Supply , fixing and Laying 2.0mm Thick FRLS PVC conduits on surface or concealed complete with PVC junction boxes, cover plates, PVC bends, PVC saddles, base and other accessories all made in PVC with GI screws as required to complete the job. .
33 |  | 25 mm dia FRLS PVC conduit | 25 mm dia FRLS PVC conduit | Mtrs | 35 | 7350 | 210 | 7350 | 210 | 7350 | 120 | 4200 | 120 | 4200
34 |  | 20 mm dia FRLS PVC conduit | 20 mm dia FRLS PVC conduit | Mtrs | 25 | 3750 | 190 | 4750 | 150 | 3750 | 98 | 2450 | 98 | 2450
35 |  | Supply and installation of flush mounted (Enhanced Category 6T 568 A or B) outlets with 2 mm thick GI box complete including cutting, chases, fixing of GI boxes and making good. The plastic shall be high impact, flame-retardant, UL rate thermoplastic. Dust cover or blank shall be provided to protect unused faceplate openings. Termination caps and plastic cover shall be provided to protect jack wiring. | Supply and installation of flush mounted (Enhanced Category 6T 568 A or B) outlets with 2 mm thick GI box complete including cutting, chases, fixing of GI boxes and making good. The plastic shall be high impact, flame-retardant, UL rate thermoplastic. Dust cover or blank shall be provided to protect unused faceplate openings. Termination caps and plastic cover shall be provided to protect jack wiring.
36 |  | Single outlet face plate with RJ-45 Jack with information outlet | Single outlet face plate with RJ-45 Jack with information outlet | Nos. | 6 | 3000 | 500 | 3000 | 500 | 3000 | 850 | 5100 | 500 | 3000
37 |  | Duplex outlet face plate with RJ-45 Jack with information outlet | Duplex outlet face plate with RJ-45 Jack with information outlet | Nos. | 3 | 1800 | 600 | 1800 | 600 | 1800 | 1460 | 4380 | 600 | 1800
38 |  | Supply,installtion testing and commisioning of Cat-6A UTP cables in existing Conduit complete as required for Telephone and Data System | Supply,installtion testing and commisioning of Cat-6A UTP cables in existing Conduit complete as required for Telephone and Data System | Mtrs | 100 | 5100 | 51 | 5100 | 51 | 5100 | 120 | 12000 | 51 | 5100
39 |  | Supplying,installation and commisioning of CAT-6A patch cords 2 mtrs. | Supplying,installation and commisioning of CAT-6A patch cords 2 mtrs. | Nos | 5 | 1250 | 250 | 1250 | 250 | 1250 | 450 | 2250 | 250 | 1250
40 |  | Supplying,installation and commisioning of CAT-6A patch cords 1 mtr. | Supplying,installation and commisioning of CAT-6A patch cords 1 mtr. | Nos | 5 | 1125 | 225 | 1125 | 225 | 1125 | 250 | 1250 | 225 | 1125
41 |  | Installation of following light fixtures including connections and complete in all respects | Installation of following light fixtures including connections and complete in all respects
42 |  | Recessed Downlighter | Recessed Downlighter | No. | 4 | 1000 | 1800 | 7200 | 250 | 1000 | 450 | 1800 | 250 | 1000
43 |  | 2x28W LED Tube | 2x28W LED Tube | No. | 2 | 500 | 700 | 1400 | 250 | 500 | 250 | 500 | 250 | 500
44 |  | LED Strip Light ( Per Meter) | LED Strip Light ( Per Meter) | Mtrs | 15 | 1350 | 850 | 12750 | 90 | 1350 | 90 | 1350 | 90 | 1350
45 |  | Signage light point | Signage light point | No. | 1 | 200 | 200 | 200 | 200 | 200 | 450 | 450 | 200 | 200
46 |  | Suspended cylindrical spot light 300 k | Suspended cylindrical spot light 300 k | nos | 6 | 1500 | 3500 | 21000 | 250 | 1500 | 450 | 2700 | 250 | 1500
47 |  | 3 phase meter with box | 3 phase meter with box | nos | 1 | 8500 | 8500 | 8500 | 8500 | 8500 | 18500 | 18500 | 8500 | 8500
L1