## Summary
Outlet- Dwarka Central Kitchen HVAC, FAS & Fire Sprinklers
Budget- 13,00,000
RFQ No: R2171 COST COMPARISON REPORT | Comp. Date : 16/11/2024
| Mahamaya Engineering |  |  | Pioneer Projects |  |  | ANJLE MEP PROJECT
Rounds | R0 | R1 | Auction | R0 | R1 | Auction | R0 | R1 | Auction
HVAC high side | 1695900 | 1695900 | 1211000 | 1755500 | 1570500 | 1115000 | 2854500 | 1814500 | 1544500
Hvac - low side | 2189750 | 1783850 | 1040100 | 1306670 | 1260995 | 1100000 | 1705490 | 1641990 | 1441990
Fire Sprinkler | 1765810 | 1548520 | 875000 | 1107300 | 985725 | 985725 | 1284820 | 1169870 | 895870
Total | 5651460 | 5028270 | 3126100 | 4169470 | 3817220 | 3200725 | 5844810 | 4626360 | 3882360
Suppliers Invited
PIONEER PROJECT SOLUTION | FL Group
ANJLE MEP PROJECT | Inventech Solutions
Mahamaya Engineering | Yashvas Interiors
Crystal Aircool
M & A Interiors
MVP INTERIORS
Rudra Ineriors
TRIDENT DESIGN AND CONTRACT
PAVILION INTERIORS
FL Group

## BOQ Price Bid
[6 empty] | 5651460 |  | 5028270 |  | 3126100 |  | 4169470 |  | 3817220 |  | 3200725 |  | 5844810 |  | 4626360 |  | 3882360
|  | RFQ No: R2171 COST COMPARISON REPORT | Comp. Date : 15/11/2024 | Comp. Date : 15/11/2024 | Mahamaya Engineering | [5 empty] | PIONEER PROJECT | [5 empty] | ANJLE MEP
Sr No. | Item Code | Item Description | UOM | Qty | Unit Price | Amount | Unit Price | Amount | Unit Price | Amount | Unit Price | Amount | Unit Price | Amount | Unit Price | Amount | Unit Price | Amount | Unit Price | Amount | Unit Price | Amount
1 |  | High side | NOS | 1 |  | 1695900 |  | 1695900 |  | 1211000 |  | 1755500 |  | 1570500 |  | 1115000 |  | 2854500 |  | 1814500 |  | 1544500
1 | A | SPLIT UNITS Supply , Installation, Testing and Commissioning of split units, each comprising of an outdoor and a single indoor unit as shown on the drawings and as per the specifications. Enclosures shall be factory fabricated and painted to a smooth finish. Oudoor unit shall consist of hermatically sealed semi- hermatic scroll rotary compressor s, air cooled condenser with fan. Indoor unit shall consist of fan section with dynamically balanced centrifugal fan s driven by FHP TEFC squirrel cage induction motor, multirows deep DX- copper cooling coil with aluminium fins, thermostatic expansion valve, synthetic fibre filters, insulated drain pan, safety controls, safety controls, thermostat all complete in a unit. The quoted price shall be inclusive of full charge of refrigerant gas, vibration isolation arrangement. Refrigerant Shall be R-32 R410A R407C Three phase ductable split units with Scroll compressor Unit should be suitable to handle total 35-40RM inter unit referigerant piping inlcuding 12-15RM vertical length. 8.5TR nominal capacity, split unit with single ductable type indoor unit and factory fitted electrical arrangement corded remote. | No | 1 | 178500 | 178500 | 178500 | 178500 | 175000 | 175000 | 165000 | 165000 | 165000 | 165000 | 165000 | 165000 | 245000 | 245000 | 215000 | 215000 | 215000 | 215000
2 | B | Single phase Non-ductable split units with Rotary compressor (Three Star Rating) (Units should be suitable to handle piping length upto 24-25 RM) 1.5TR nominal capacity, split unit with single Wall Mounted type indoor unit and cordless control . Price shall be inclusive of copper power cabling from indoor to outdoor unit as required. | No | 2 | 55000 | 110000 | 55000 | 110000 | 40000 | 80000 | 40000 | 80000 | 40000 | 80000 | 40000 | 80000 | 46500 | 93000 | 43500 | 87000 | 43500 | 87000
3 |  | SECTION B KITCHEN VENTILATION SYSTEM
4 |  | DOUBLE SKIN AIR COOLING MACHINES - With Fresh Air Intake Section (AIR WASHERS) Supply , Installation, Testing and Commissioning of double skin type evaporative air cooling machines (packaged type) each comprising of following as per the specifications Casing of air washer shall be in double skin construction. Inner skin shall be constructed out of24 gauge plain GS sheet outer skin in 24 gauge pre-plasticized GS sheet sandwitched between 50mm thick injected PU foam insulation of density not less than 40 Kg CuM and complete with marine light,limit switch inspection doors including control wiringas required. Air washer shall have access for all parts. Fan section complete with backward curved DIDW type centrifugal fan s, EFF1, IE3, IP-55, rated TEFC squirrel cageinduction motor suitable to operate on 415+10%V, 50Hz,3 phase AC power supply and belt drive package.Centrifugal fans shall be coated with epoxy paint as specified. Fan outlet velocity shall not be more than 2000 FPM (10.16 MPS).All fans should be AMCA certified. AirWasher shall be provided with Intake Section withF A openings as per approved shop drawing. Air washer wet section shall be complete with 300mm thick cellulose based paper fills, drift eliminators,water distribution system complete with FRP spray headers, strainer of fine mesh brass screen, globe valve,float valve, quick fill, over flow drainconnections, GI medium class piping and 3 1 phasemonobloc pumps of 1HP 1.5HP 2HP motor rating as required according to the capacity of air cooling machines. Inner skin of wet section including fills mounting frame shall be constructed out of stainless steel SS- 304 A grade of appropriate thickness .Sump shall be made out of 1.25mm thick SS-304 A grade stainless steel .Velocity across the paper fills not to exceed 500 FPM. Filter section complete with 50mm thick aluminiumwire mesh viscous metallic filters. Velocity across the filters shall not exceed 500 FPM. Airwasher should be provided with adequate space between eliminator fan to avoid water carryover.The Evaporative Air Cooling Machines (EAC) shall be of following duty parameters M c No Capacity S.P Motor Area to (Cfm) (mmWG) Rating be fed (HP)EAC-1 1x22500 58-60 1x15.0 Kitchen | No | 1 | 550000 | 550000 | 550000 | 550000 | 370000 | 370000 | 650000 | 650000 | 590000 | 590000 | 590000 | 590000 | 1050000 | 1050000 | 650000 | 650000 | 650000 | 650000
5 | 1.2 | SCRUBBER (For Kitchen Exhaust) WET TYPE SCRUBBER Supply , Installation , Testing and Commissioning of wet type scrubber (packaged type) comprising of following as per the specifications Fan section complete with backward curved DIDW type centrifugal fan s, TEFC squirrel cage inductionmotor suitable to operate on 415+10%V, 50Hz,3 phase AC power supply and belt drive package.Casing of wet type scrubber shall be constructedout of 16 gauge GS sheet complete with inspectiondoors as required. Centrifugal fans shall be coatedwith epoxy paint as specified. Fan outlet velocity shall not be more than 2000 FPM (10.16 MPS). Wet section complete with double bank spray header in GI construction and nozzles, louvers PVC mist eliminators mist collection tray made out of 16G GSS,strainer of fine mesh brass screen, globe valve,float valve, quick fill, over flow drainconnections, GI medium class piping and 3 phasemonobloc pump of 1.5HP motor rating as required according to the capacity of scrubber machines. Wet section including sump will be made of1.25mm thick SS-304 A grade stainless steel . In addition to the above, scrubber shall be provided with adequate vibration isolation padsand fire retardent flexible canvass connections madeout of canvass sleeve.The Scrubber Machines (EAC) shall be of following duty parameters M c No Capacity S.P Motor Area to (Cfm) (mmWG) Rating be fed (HP)WS-1 28000 68-70 20.0 Kitchen Area | No | 1 | 666000 | 666000 | 666000 | 666000 | 461000 | 461000 | 850000 | 850000 | 725000 | 725000 | 725000 | 725000 | 1450000 | 1450000 | 850000 | 850000 | 850000 | 850000
6 |  | INLINE FANS (Single Phase) Supply, Installation, Testing Commissioning of circular rectangular inline fans for exhaust air complete with sheet metal casing, direct driven centrifugal fan, motor with proper protection and inspection door. Fan shall be suitable for operation on 220+6 % volts, 50 Hz,1phase AC power supply. Fan shall be installed as shown in the drawings and will be of following characteristics All single phase inline fans shall be provided with factory fitted speed regulators. All Fans Should be complete with Plug Top necessary power cable. Fan Capacity S.P Area to No. (Cfm) (mmWG) to be exhausted IF-1(Circular) 300 14-15 Pantry | No | 1 | 41400 | 41400 | 41400 | 41400 | 15000 | 15000 | 10500 | 10500 | 10500 | 10500 | 10500 | 10500 | 16500 | 16500 | 12500 | 12500 | 12500 | 12500
7 | C | AIR CURTAIN Supply , Installation and Testing of air curtains with noiseless, statically dynamically balanced aluminium blowers, cleanable type pre-filters, motor powder coated aluminium enclosure as per the specifications. Unit shall be complete with Plug Top necessary power cable.
8 | a. | 2.1 M long air curtain | No | 1 | 55000 | 55000 | 55000 | 55000 | 40000 | 40000 | 45000 | 45000 | 45000 | 45000 | 45000 | 45000 | 55000 | 55000 | 45000 | 45000 | 45000 | 45000
9 | b. | 1.5 M long air curtain | No | 2 | 47500 | 95000 | 47500 | 95000 | 35000 | 70000 | 35000 | 70000 | 35000 | 70000 | 35000 | 70000 | 48500 | 97000 | 40500 | 81000 | 40500 | 81000
2 |  | Low side | NOS | 1 |  | 2189750 |  | 1783850 |  | 1040100 |  | 1306670 |  | 1260995 |  | 1100000 |  | 1705490 |  | 1641990 |  | 1441990
10 |  | REFRIGERANT PIPING Supply, Installation,Testing Commissioning of copper refrigerant piping complete with copper fittings charge of regrigerant gas for the above split units. Piping associated with split units to be insulated with 19mm thick closed cell elastomeric insulation with Class O in tubing form as required. Piping shall be laid over duly painted slotted angle trays fixed with GI clamps. Quoted Price shall be inclusive of UV protection paint for all exposed pipes of approved make. Price shall be inclusive of copper power cabling from indoor to outdoor unit as required. Referigerant piping shall be epoxy coated to prevent erosion.
11 | a. | Pair of hard drawn copper refrigerant piping for the above split units with scroll compressor. | RM | 25 | 2650 | 66250 | 2350 | 58750 | 1800 | 45000 | 1850 | 46250 | 1850 | 46250 | 1850 | 46250 | 2450 | 61250 | 1850 | 46250 | 1850 | 46250
12 | b. | Pair of Soft refrigerant piping for non ductable split units with rotary compressor. | RM | 55 | 2350 | 129250 | 2000 | 110000 | 900 | 49500 | 1250 | 68750 | 1250 | 68750 | 1250 | 68750 | 1450 | 79750 | 1450 | 79750 | 1450 | 79750
13 | 1 | MS FRAME FOR ODUs Supply and Erection of MS base frame duly applied with red-oxide primer followed by black enamel paint for mounting of outdoor units. | Kg | 55 | 400 | 22000 | 350 | 19250 | 140 | 7700 | 150 | 8250 | 150 | 8250 | 150 | 8250 | 250 | 13750 | 210 | 11550 | 210 | 11550
14 | 2 | PIPING CONDENSATE DRAIN PIPING -cPVC Supply, Installation, Testing and Commissioning of cPVC pipes cut to required lengths and installed for condensate drain. Quoted price shall be inclusive of supply and fixing in position the necessary fittings like elbows, tees reducers etc. and supporting arrangement in accordance with the approved shop drawings and specifications. Pipes shall be insulated with 9mm thick closed cell elastomeric insulation with class O fire retardant properties in tubing form . Pipes shall be of following sizes
15 | a. | 50mm dia | RM | 5 | 610 | 3050 | 610 | 3050 | 350 | 1750 | 220 | 1100 | 220 | 1100 | 220 | 1100 | 750 | 3750 | 650 | 3250 | 650 | 3250
16 | b. | 40mm dia | RM | 10 | 550 | 5500 | 550 | 5500 | 320 | 3200 | 180 | 1800 | 180 | 1800 | 180 | 1800 | 550 | 5500 | 450 | 4500 | 450 | 4500
17 | c. | 32mm dia | RM | 2 | 550 | 1100 | 550 | 1100 | 300 | 600 | 160 | 320 | 160 | 320 | 160 | 320 | 450 | 900 | 350 | 700 | 350 | 700
18 | d. | 25mm dia | RM | 5 | 380 | 1900 | 380 | 1900 | 280 | 1400 | 140 | 700 | 140 | 700 | 140 | 700 | 350 | 1750 | 250 | 1250 | 250 | 1250
19 | 3 | DUCTWORK AIR TERMINALS FACTORY FABRICATED DUCTING Supply , Installation and Testing of factory fabricated GSS ducting complete with vanes, splitter dampers, fire retardant gaskets hanging arrangement including fully threaded GI rods and GI C channels, GI C channels etc. as approved by clients consultants in accordance with the approved shop drawings and specifications. Quoted price shall be inclusive of necessary scaffolding charges towards installation of supply exhaust air ducts outside or within building wherever required. Quoted price should also include necessary charges towards duct supporets including MS angle channel arrangement as required for ducts being installed outside or within building wherever required. Spacing between duct supports should not exceed 2m. All duct support to be provided with check nuts (lock nuts). While selecting the duct supports vendor shall ensure vibration free installation.Quoted price shall be inclusive of smoke test using smoke bombs.
20 | a. | 1mm to 899mm -- 26G GSS with TDC Joints | SqM | 5 | 1850 | 9250 | 1250 | 6250 | 800 | 4000 | 1050 | 5250 | 1050 | 5250 | 1050 | 5250 | 1150 | 5750 | 1150 | 5750 | 1150 | 5750
21 | b. | 900mm to 1200mm -- 24G GSS with TDC Joints | SqM | 10 | 1850 | 18500 | 1480 | 14800 | 1100 | 11000 | 1150 | 11500 | 1150 | 11500 | 1150 | 11500 | 1250 | 12500 | 1250 | 12500 | 1250 | 12500
22 | c. | 1201mm to 1800mm - 22G GSS with TDC Joints | SqM | 5 | 2250 | 11250 | 1560 | 7800 | 1280 | 6400 | 1250 | 6250 | 1250 | 6250 | 1250 | 6250 | 1450 | 7250 | 1450 | 7250 | 1450 | 7250
23 | 3.2 | SITE FABRICATED DUCTING Supply, Fabrication, Installation and Testing of sheet metal ducts complete with vanes, splitter dampers, hanging arrangement including check nuts in accordance with the approved shop drawings and specifications
24 |  | a. 0.63mm (24 gauge) GSS | SqM | 10 | 1850 | 18500 | 1450 | 14500 | 996 | 9960 | 1050 | 10500 | 1050 | 10500 | 1050 | 10500 | 1150 | 11500 | 1150 | 11500 | 1150 | 11500
25 |  | b. 0.8 mm (22 gauge) GSS | SqM | 5 | 2250 | 11250 | 1580 | 7900 | 1230 | 6150 | 1150 | 5750 | 1150 | 5750 | 1150 | 5750 | 1350 | 6750 | 1350 | 6750 | 1350 | 6750
26 | 3.3 | FLEXIBLE CANVASS CONNECTIONS Supply, Installation, Testing of 125mm deep antivibration flexible joints at the outlet of air handling units ductable split units inline fans. Flexible connections shall be constructed using imported fire retardant fabric with extruded aluminium frame flange on both sides of approved make. | RM | 4 | 3500 | 14000 | 2500 | 10000 | 1000 | 4000 | 1000 | 4000 | 1000 | 4000 | 1000 | 4000 | 2450 | 9800 | 2250 | 9000 | 2250 | 9000
27 | 3.4 | LINEAR GRILLES Supply, Installation , Testing and Balancing of one way blow linear supply cum return air grilles complete with fixed core as per approved shop drawings and specifications. The grilles shall be of approved colour shade. Powder coated aluminium grilles of extruded sections with integral flanges on both sides ends as required complete with corner pieces. i. 100 150 200 250 mm High grilles | SqM | 1 | 7500 | 7500 | 7500 | 7500 | 7500 | 7500 | 6500 | 6500 | 6500 | 6500 | 6500 | 6500 | 8650 | 8650 | 7250 | 7250 | 7250 | 7250
28 | 3.5 | DOUBLE LOUVERED GRILLES Supply, Installation ,Testing and Balancing of double louvered supply air grilles as per approved shop drawings and specifications complete with key operated aluminium volume control dampers. a. Powder coated extruded aluminium grilles. | SQM | 0.5 | 14500 | 7250 | 12500 | 6250 | 9800 | 4900 | 9500 | 4750 | 9500 | 4750 | 9500 | 4750 | 10500 | 5250 | 10500 | 5250 | 10500 | 5250
29 | 3.6 | AIR TRANSFER GRILLES Supply, Installation and Testing of extruded aluminium powder coated air transfer grilles to be provided at the door of toilets pantry. | SQM | 0.2 | 14500 | 2900 | 9500 | 1900 | 9500 | 1900 | 7500 | 1500 | 7500 | 1500 | 7500 | 1500 | 11500 | 2300 | 11500 | 2300 | 11500 | 2300
30 | 3.7 | Supply, Installation and Testing of GI box type volume control dampers as per the specifications and shop drawings.- For Rectangular Duct | SqM | 0.5 | 14500 | 7250 | 10500 | 5250 | 10500 | 5250 | 8500 | 4250 | 7850 | 3925 | 7850 | 3925 | 7850 | 3925 | 7850 | 3925 | 7850 | 3925
31 | 3.8 | Supply, Installation and Testing of GI multi blade type louver dampers as per the specifications and shop drawings. | SqM | 1 | 14500 | 14500 | 8800 | 8800 | 8800 | 8800 | 8500 | 8500 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250
32 | 4.1 | INSULATION ACOUSTIC LINING OF DUCTS Using Open Cell Nitrile Rubber Supply and Application of internal acoustic lining of supply air ducting using open cell nitrile rubber insulation with density within 140-180 Kg m3 as per the approved shop drawings and specifications. Insulation material shall be bonded with the ducts using metal screw and washers to facilitate grip to the GI sheet. Adhesive used shall be Low VOC type. 10mm thick lining | SqM | 5 | 2650 | 13250 | 1350 | 6750 | 600 | 3000 | 850 | 4250 | 850 | 4250 | 850 | 4250 | 1450 | 7250 | 1250 | 6250 | 1250 | 6250
33 | 4.2 | INSULATION ACOUSTIC LINING OF DUCTS Using Fibre Glass Supply and Application of internal acoustic lining of supply return air ducting using resin bonded fibre glass insulation of density not less than 32Kg CuM as per the approved shop drawings and specifications. Quoted price shall be inclusive of GSS channel, metal screws, washers, fibre glass tissue, perforated sheet etc. as required for complete installation. a. 25mm thick lining | SqM | 10 | 3300 | 33000 | 1050 | 10500 | 600 | 6000 | 650 | 6500 | 650 | 6500 | 650 | 6500 | 1050 | 10500 | 850 | 8500 | 850 | 8500
34 | 5 | THERMAL INSULATION OF DUCTS (Using Factory Laminated aluminium foil faced,Class O Closed Cell Elastomeric insulation) Supply and Application of internal external thermal insulation of supply return air ducting using closed cell elastomeric insulation with class O fire retardant properties as per the specifications and drawings.Adhesive used shall be Low VOC type. a. 13mm thick insulation | SQM | 30 | 1450 | 43500 | 750 | 22500 | 480 | 14400 | 450 | 13500 | 450 | 13500 | 450 | 13500 | 850 | 25500 | 750 | 22500 | 750 | 22500
35 | 7 | DUCTWORK AIR TERMINALS - INCLUDING IN SECTION A FACTORY FABRICATED DUCTING Supply, Installation and Testing of factory fabricated GSS ducting complete with vanes,splitter dampers, fire retardant gaskets, hanging arrangement including fully threaded GI rods and GI C channels rolled steel wires or Gripple Wire Rope Hangers Supports complete with end fixing, GI C channels etc. as approved by clients consultants in accordance with the approved shop drawings and specifications. Quoted price shall be inclusive of necessary scaffolding charges towards installation of supply exhaust air ducts outside or within building wherever required. Spacing between duct supports should not exceed 2m in both cases i.e GI rods with GI C channels Gripple Wire Rope Hanger support . In case of Gripple Wire Rope Hanger support for duct sizes above 1800mm, MS angles duly painted with black enamel paint should be used along with neoprene pad in between the duct MS angle. All duct supports shall be provided with check nuts (lock nuts). While selecting the duct supports vendor shall ensurevibration free installation.Quoted price shall be inclusive of smoke test using smoke bombs. For Air-Cooling ducts
36 | a. | 1mm to 899mm -- 24G GSS with TDC Joints | SqM | 50 | 1950 | 97500 | 1250 | 62500 | 800 | 40000 | 1150 | 57500 | 1150 | 57500 | 1150 | 57500 | 1250 | 62500 | 1250 | 62500 | 1250 | 62500
37 | b. | 900mm to 1500mm -- 22G GSS with TDC Joints | SqM | 50 | 2150 | 107500 | 1480 | 74000 | 900 | 45000 | 1350 | 67500 | 1350 | 67500 | 1350 | 67500 | 1450 | 72500 | 1450 | 72500 | 1450 | 72500
38 | c. | 1501mm to 2100mm - 20G GSS with TDC Joints | SqM | 10 | 2450 | 24500 | 1560 | 15600 | 1200 | 12000 | 1550 | 15500 | 1550 | 15500 | 1550 | 15500 | 1650 | 16500 | 1650 | 16500 | 1650 | 16500
39 | 7.1 | SITE FABRICATED DUCTING Supply, Fabrication, Installation and Testing of sheet metal ducts complete with vanes, splitter dampers, hanging arrangement including check nuts in accordance with the approved shop drawings and specifications.
40 | a. | a. 0.63mm (24 gauge) GSS | SqM | 15 | 1950 | 29250 | 1450 | 21750 | 1040 | 15600 | 1150 | 17250 | 1150 | 17250 | 1150 | 17250 | 1150 | 17250 | 1150 | 17250 | 1150 | 17250
41 | b. | b. 0.8 mm (22 gauge) GSS | SqM | 5 | 2150 | 10750 | 1580 | 7900 | 1180 | 5900 | 1250 | 6250 | 1250 | 6250 | 1250 | 6250 | 1358 | 6790 | 1358 | 6790 | 1358 | 6790
42 | c. | c. 1.0mm (20 gauge) GSS | SqM | 5 | 2450 | 12250 | 1850 | 9250 | 1310 | 6550 | 1450 | 7250 | 1450 | 7250 | 1450 | 7250 | 1550 | 7750 | 1550 | 7750 | 1550 | 7750
43 | 7.2 | For Kitchen Exhaust Supply, fabrication, Installation and testing of MS ductingfor kitchen exhaust contructed out of 2mm thick MS sheet using MS angle iron flanges in line with good engineering practice. Entire ducting shall be applied with minimum two coats of red oxide primer. Duct shall be provided with oil trap as required | SqM | 140 | 3500 | 490000 | 3500 | 490000 | 2600 | 364000 | 2850 | 399000 | 2850 | 399000 | 2850 | 399000 | 3650 | 511000 | 3250 | 455000 | 3250 | 455000
44 | 7.3 | FLEXIBLE CANVASS CONNECTIONS Supply, Installation, Testing of 125mm deep antivibration flexible joints at the outlet of air handling units ductable split units inline fans. Flexible connections shall be constructed using imported fire retardant fabric with extruded aluminium frame flange on both sides of approved make. | RM | 8.5 | 1800 | 15300 | 2500 | 21250 | 1000 | 8500 | 1000 | 8500 | 1000 | 8500 | 1000 | 8500 | 2450 | 20825 | 2250 | 19125 | 2250 | 19125
45 | 7.4 | LINEAR GRILLES Supply, Installation , Testing and Balancing of one way blow linear supply cum return air grilles complete with fixed core as per approved shop drawings and specifications. The grilles shall be of approved colour shade. Powder coated aluminium grilles of extruded sections with integral flanges on both sides ends as required complete with corner pieces. i. 100 150 200 250 mm High grilles | SqM | 8 | 14500 | 116000 | 7500 | 60000 | 5500 | 44000 | 6500 | 52000 | 6500 | 52000 | 6500 | 52000 | 8650 | 69200 | 6500 | 52000 | 6500 | 52000
46 | 8 | AIR TRANSFER GRILLES Supply, Installation and Testing of GI box type volume control dampers as per the specifications and shop drawings. | SQM | 3.5 | 14500 | 50750 | 10500 | 36750 | 5500 | 19250 | 8500 | 29750 | 8500 | 29750 | 8500 | 29750 | 10500 | 36750 | 10500 | 36750 | 10500 | 36750
47 | 9 | Supply, Installation and Testing of Aluminium multi bladetype louver dampers as per the specifications and shop drawings. | SqM | 6 | 14500 | 87000 | 7000 | 42000 | 4200 | 25200 | 8500 | 51000 | 4650 | 27900 | 4650 | 27900 | 4650 | 27900 | 4650 | 27900 | 4650 | 27900
48 | 10 | Supply, Installation and Testing of fresh air powdered coated anodised extruded aluminium louvers to be installed outside for suction ( airwashers), as per approved shop drawings and specifications. Sample of louvers to be got approved from consultants and Clients prior to procurement. | SqM | 1 | 14500 | 14500 | 12500 | 12500 | 5500 | 5500 | 10500 | 10500 | 10500 | 10500 | 10500 | 10500 | 12500 | 12500 | 10500 | 10500 | 10500 | 10500
49 | 11 | Supply, Installation and Testing of Bird Screens with GI wire mesh to be installed at the suction of fresh air discharge of Exhaust air as per the specifications and shop drawings.Sample of bird screen to be got approved from consultants and Clients prior to procurement. | SqM | 1 | 7500 | 7500 | 7500 | 7500 | 4500 | 4500 | 10500 | 10500 | 6500 | 6500 | 6500 | 6500 | 6500 | 6500 | 6500 | 6500 | 6500 | 6500
50 | 12 | INSULATION THERMAL INSULATION OF DUCTS-(FOR AIR SCRUBBER DUCT) (Using Factory Laminated fibre glass insulation) Supply and Application of external thermal insulation of supply return air ducting using aluminium foil faced fibre glass insulation of density not less than 24Kg CuM and aluminium foil thickness of 22 microns as per the specifications and drawings. Quoted price shall be inclusive of Low VOC adhesive as required, aluminium tape straps. 50mm thick insulation | SqM | 140 | 2350 | 329000 | 1890 | 264600 | 480 | 67200 | 650 | 91000 | 650 | 91000 | 650 | 91000 | 1050 | 147000 | 750 | 105000 | 750 | 105000
51 | 13 | THERMAL INSULATION OF DUCTS-(FOR AIR SCRUBBER DUCT) - EXPOSED (Using Factory Laminated fibre glass insulation) Supply and Application of external thermal insulation of supply return air ducting using aluminium foil faced fibre glass insulation of density not less than 24Kg CuM and aluminium foil thickness of 22 microns as per the specifications and drawings. Quoted price shall be inclusive of Low VOC adhesive as required, aluminium tape straps. Insulation shall be covered necessary glass cloth UV protection paint. 50mm thick insulation | SqM | 15 | 2650 | 39750 | 1890 | 28350 | 600 | 9000 | 850 | 12750 | 850 | 12750 | 850 | 12750 | 1050 | 15750 | 850 | 12750 | 850 | 12750
52 | a. | THERMAL INSULATION OF DUCTS - Air Washer (Using aluminium foil faced Class O Fire Retardant Properties Closed Cell Elastomeric insulation) Supply and Application of external thermal insulation of supply return air ducting using factory laminated aluminium foil faced closed cell elastomeric nitrile rubber insulation with class O fire retardant properties as per the specifications and drawings. aluminium foil face shall provide protection from mechanical impact, and Scratches etc. Both insulation aluminium foil layer should have built in antimicrobial protection. Expose insulation shall be covered with necessary glass cloth UV protection paint. Adhesive - AC Duct King Eco Fresh 25mm thick insulation - For AC Duct in Kitchen | SqM | 135 | 2350 | 317250 | 1050 | 141750 | 430 | 58050 | 850 | 114750 | 850 | 114750 | 850 | 114750 | 950 | 128250 | 950 | 128250 | 950 | 128250
53 | 14 | KVF PANEL -1 (Location Kitchen ) - 13.8KW For 9700Cfm Air Washers Pump, 12100Cfm SISW Fan ESP Incoming 63 Amps ,TP MCCB with electronic release earth fault relay, door interlock and front drive rotor kit-- 1set(0-500) V digital Voltmeter with built in Selectorswitch -- 1setDigital Ammeter with built in selector switch- 1setCurrent Transformers - 1setLED type RYB phase indication lights- 1setBusbar100 Amps TPN aluminium busbar havingsuitable fault level, with PVC heat shrunk sleeves on SMC DMC supports. | No | 1 | 0 | 0 | 105000 | 105000 | 69340 | 69340 | 85000 | 85000 | 85000 | 85000 | 85000 | 85000 | 215000 | 215000 | 175000 | 175000 | 175000 | 175000
54 | 15 | CABLING Supply, laying, affecting connections andarmoured PVC insulated aluminium copperconductor cables. Cables shall be inclusive ofall clamps, saddles, screws, cable identificationtags, cable terminal joints including terminallugs, insulating tapes, affecting terminal connections to the equipment as per the specifications and as required. Quoted priceshall be inclusive of perforated duly painted2mm thick MS trays to be installed inside and8SWG copper earth wire for all equipment.EQUIPMENT
55 | a. | 3 C x 10 Sqmm cable (Copper) | RM | 10 | 0 | 0 | 850 | 8500 | 650 | 6500 | 650 | 6500 | 650 | 6500 | 650 | 6500 | 1250 | 12500 | 1250 | 12500 | 1250 | 12500
56 | b. | 3 C x 6 Sqmm cable (Copper) | RM | 20 | 0 | 0 | 850 | 17000 | 650 | 13000 | 650 | 13000 | 650 | 13000 | 650 | 13000 | 650 | 13000 | 650 | 13000 | 650 | 13000
57 | c. | 3 C x 2.5 Sqmm cable (Copper) | RM | 5 | 0 | 0 | 300 | 1500 | 170 | 850 | 150 | 750 | 150 | 750 | 150 | 750 | 250 | 1250 | 250 | 1250 | 250 | 1250
58 | d. | 3 C x 2.5 Sqmm cable( Copper Control cabling) | RM | 5 | 0 | 0 | 300 | 1500 | 170 | 850 | 150 | 750 | 150 | 750 | 150 | 750 | 250 | 1250 | 250 | 1250 | 250 | 1250
59 | e | 3 C x 1.5 Sqmm cable(Copper Control cabling) | RM | 10 | 0 | 0 | 300 | 3000 | 170 | 1700 | 150 | 1500 | 150 | 1500 | 150 | 1500 | 170 | 1700 | 170 | 1700 | 170 | 1700
60 | 16 | Supply and fixing of 1.1 KV grade rubbermat 914.4 mm wide 6mm thick to withstand 1.1 KV dielectric strength in front of each panel. | RM | 2 | 0 | 0 | 1200 | 2400 | 600 | 1200 | 1500 | 3000 | 500 | 1000 | 500 | 1000 | 500 | 1000 | 500 | 1000 | 500 | 1000
61 | 17 | Supply, Installation Testing of TPN isolator in weather proof enclosure near fans | No | 2 | 0 | 0 | 9500 | 19000 | 7000 | 14000 | 12500 | 25000 | 6500 | 13000 | 6500 | 13000 | 6500 | 13000 | 6500 | 13000 | 6500 | 13000
3 |  | Fire Sprinkler System | NOS | 1 |  | 1765810 |  | 1548520 |  | 875000 |  | 1107300 |  | 985725 |  | 985725 |  | 1284820 |  | 1169870 |  | 895870
62 | 1 | Providing, laying, jointing and testing of following sizes of pipes conforming to IS-1239 with all accessories like all fittings (upto 50mm dia threaded M.S.forged fittings and above 50 mm dia MS fittings with welded joints shall be used)fittings including tees, elbows, reducers, flanges, rubber gaskets, nuts bolts, washer. And fixing the pipe on floor wall ceiling with suitable size clamps, hangers, structural steel supports as per specification. And PVC pipe sleeve to be provided wherever the pipes are crossing the walls floors and sealing the sleeves as per consultants requirements including cutting holes and chases in brick, R.C.C work and making good the same to original conditions complete in all respects.Arrows showing direction of flow to be marked(with paint of approved colour) on each pipe at locations as decided at site.
63 | (a) | For Fire fighting sprinkler System - M.S. `C Heavy class pipe
64 |  | a)25 mm dia(4.04mm thickness) screwed joint | RM | 90 | 2150 | 193500 | 690 | 62100 | 430 | 38700 | 550 | 49500 | 550 | 49500 | 550 | 49500 | 750 | 67500 | 720 | 64800 | 720 | 64800
65 |  | b)32 mm dia(4.05mm thickness)screwed joint | RM | 10 | 2350 | 23500 | 870 | 8700 | 550 | 5500 | 750 | 7500 | 750 | 7500 | 750 | 7500 | 950 | 9500 | 850 | 8500 | 850 | 8500
66 |  | c) 40 mm dia(4.05mm thickness)screwed joint | RM | 20 | 2559 | 51180 | 980 | 19600 | 650 | 13000 | 850 | 17000 | 850 | 17000 | 850 | 17000 | 1050 | 21000 | 950 | 19000 | 950 | 19000
67 |  | d) 50 mm dia(4.5mm thickness)screwed joint | RM | 15 | 2750 | 41250 | 1250 | 18750 | 750 | 11250 | 1050 | 15750 | 1050 | 15750 | 1050 | 15750 | 1250 | 18750 | 1150 | 17250 | 1150 | 17250
68 |  | e) 65 mm dia(4.5mm thickness) | RM | 20 | 2950 | 59000 | 1450 | 29000 | 900 | 18000 | 1250 | 25000 | 1150 | 23000 | 1150 | 23000 | 1450 | 29000 | 1450 | 29000 | 1450 | 29000
69 |  | f) 80 mm dia(4.85mm thickness) | RM | 100 | 3100 | 310000 | 1670 | 167000 | 1300 | 130000 | 1450 | 145000 | 1350 | 135000 | 1350 | 135000 | 1650 | 165000 | 1650 | 165000 | 1650 | 165000
70 |  | g)100 mm dia(5.4mm thickness) | RM | 10 | 3300 | 33000 | 1900 | 19000 | 1530 | 15300 | 1650 | 16500 | 1550 | 15500 | 1550 | 15500 | 2050 | 20500 | 2050 | 20500 | 2050 | 20500
71 | 2 | Providing two coats of synthetic enamel paint of approved shade over a coat of primer. Including painting of legends both direction arrow as per the approval of the architects consultants.
72 |  | a)25 mm dia | RM | 90 | 40 | 3600 | 40 | 3600 | 1 | 90 | 50 | 4500 | 25 | 2250 | 25 | 2250 | 100 | 9000 | 50 | 4500 | 50 | 4500
73 |  | b)32 mm dia | RM | 10 | 40 | 400 | 40 | 400 | 1 | 10 | 50 | 500 | 25 | 250 | 25 | 250 | 100 | 1000 | 50 | 500 | 50 | 500
74 |  | c) 40 mm dia | RM | 20 | 40 | 800 | 40 | 800 | 1 | 20 | 50 | 1000 | 25 | 500 | 25 | 500 | 100 | 2000 | 50 | 1000 | 50 | 1000
75 |  | d) 50 mm dia | RM | 15 | 40 | 600 | 40 | 600 | 1 | 15 | 50 | 750 | 25 | 375 | 25 | 375 | 100 | 1500 | 50 | 750 | 50 | 750
76 |  | e) 65 mm dia | RM | 20 | 40 | 800 | 40 | 800 | 1 | 20 | 50 | 1000 | 25 | 500 | 25 | 500 | 100 | 2000 | 50 | 1000 | 50 | 1000
77 |  | f) 80 mm dia | RM | 100 | 40 | 4000 | 40 | 4000 | 1 | 100 | 50 | 5000 | 25 | 2500 | 25 | 2500 | 100 | 10000 | 50 | 5000 | 50 | 5000
78 |  | g)100 mm dia | RM | 10 | 40 | 400 | 40 | 400 | 1 | 10 | 50 | 500 | 25 | 250 | 25 | 250 | 100 | 1000 | 50 | 500 | 50 | 500
79 | 3 | Providing and fixing gun metal ball valve suitable for pressure 15 Kg Cm2 and confirming to IS 778 of the following size including providing necessary union flange.
80 |  | a) 25 mm dia | NO. | 1 | 3300 | 3300 | 2500 | 2500 | 1850 | 1850 | 2050 | 2050 | 1550 | 1550 | 1550 | 1550 | 1850 | 1850 | 1850 | 1850 | 1850 | 1850
81 |  | b) 50 mm dia | NO. | 1 | 5500 | 5500 | 4500 | 4500 | 3500 | 3500 | 3500 | 3500 | 2850 | 2850 | 2850 | 2850 | 6250 | 6250 | 6250 | 6250 | 6250 | 6250
82 | 4 | Providing fixing of butterfly valve suitable for pressure 15 Kg Sqcm. with flanges, nut bolts gaskets complete required.
83 |  | a) 65 mm dia | NO. | 1 | 9500 | 9500 | 7800 | 7800 | 5500 | 5500 | 5500 | 5500 | 4500 | 4500 | 4500 | 4500 | 8500 | 8500 | 8500 | 8500 | 8500 | 8500
84 |  | b) 80 mm dia | NOS | 3 | 16500 | 49500 | 10500 | 31500 | 5500 | 16500 | 6500 | 19500 | 5500 | 16500 | 5500 | 16500 | 10500 | 31500 | 10500 | 31500 | 10500 | 31500
85 |  | c) 100 mm dia | NOS | 2 | 18500 | 37000 | 14500 | 29000 | 6500 | 13000 | 8500 | 17000 | 6500 | 13000 | 6500 | 13000 | 12500 | 25000 | 12500 | 25000 | 12500 | 25000
86 | 5 | Providing and fixing of C.I. wafer type check valve suitable for pressure 15 Kg Sqcm. with flanges, Nut, bolts washers, painting etc. complete as required.
87 |  | a) 80 mm dia | NOS. | 1 | 8800 | 8800 | 8800 | 8800 | 6500 | 6500 | 8500 | 8500 | 8500 | 8500 | 8500 | 8500 | 8500 | 8500 | 8500 | 8500 | 8500 | 8500
88 | 6 | Providing and fixing C.I.`Y strainer with bronze perforated sheet basket tested to a pressure of 15 Kg sqcm including rubber gasket, flanges, nuts, bolts and washers, complete as required.
89 |  | b) 100 mm dia | NO. | 1 | 21000 | 21000 | 15500 | 15500 | 9500 | 9500 | 10500 | 10500 | 8500 | 8500 | 8500 | 8500 | 9500 | 9500 | 9500 | 9500 | 9500 | 9500
90 | 7 | Providing fixing gun metal fire hydrant valve with 80 mm N.B. flanged inlet, brass spindal, one no. 63 mm dia female instantaneous outlet type. G.M. coupling,blank cap, chain. Conforming to IS 5290. Including tapping from wet riser complete as required. | NOS | 1 | 17000 | 17000 | 14500 | 14500 | 8500 | 8500 | 12500 | 12500 | 8500 | 8500 | 8500 | 8500 | 8500 | 8500 | 8500 | 8500 | 8500 | 8500
91 | 8 | Providing fixing swinging type First Aid hose reel in red colour with 36 mts long and 20 mm dia dia heavy duty rubber water hose, 20 mm dia globe valve stop cock, terminating with G.M. coupling nozzle of 5mm outlet with shut off valve confirming to IS 8090 - 1976 complete with drum and brackets for fixing on wall, bolts nuts conforming to IS 884-1969 complete as required. | NOS | 1 | 23000 | 23000 | 18500 | 18500 | 10500 | 10500 | 10500 | 10500 | 9500 | 9500 | 9500 | 9500 | 12500 | 12500 | 12500 | 12500 | 12500 | 12500
92 | 9 | Providing and Fixing Hose pipe, 63 mm dia and 15 mts long, duly reinforced, rubber lined suitable for brusting pressure not less than 22 Kg Sqcm. conforming to IS 636-1988 type A with gun metal heavy duty instantaneous type coupling ( Pair male female parts) conforming to IS 903. Complete as required (two nos. for each hydrant) | NOS | 2 | 18500 | 37000 | 18500 | 37000 | 6500 | 13000 | 6500 | 13000 | 5500 | 11000 | 5500 | 11000 | 8460 | 16920 | 8460 | 16920 | 8460 | 16920
93 | 10 | Providing and Fixing 63 mm dia instantaneous pattern branch short gunmetal pipe, 16 mm dia nozzle conforming to IS 903, suitable for inter connection to hose pipe coupling complete as required. | NOS | 1 | 15000 | 15000 | 6500 | 6500 | 2500 | 2500 | 2500 | 2500 | 2200 | 2200 | 2200 | 2200 | 2050 | 2050 | 2050 | 2050 | 2050 | 2050
94 | 11 | Providing and fixing standard firemans axe with heavy rubber handle. | NOS | 1 | 7000 | 7000 | 3500 | 3500 | 1000 | 1000 | 850 | 850 | 550 | 550 | 550 | 550 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500
95 | 12 | Providing and fixing inlet breaching having C.I. body Two way gun metal 63 mm dia instantaneous inlets conforming to IS 903 fitted with non return valves, 25 mm dia gun metal drain cock, blank cap, brass chains and 100 mm dia flanges with all accessories suitable for local fire tender complete as required. | NO | 1 | 24500 | 24500 | 16900 | 16900 | 10500 | 10500 | 12500 | 12500 | 12500 | 12500 | 12500 | 12500 | 10500 | 10500 | 10500 | 10500 | 10500 | 10500
96 | 13 | Providing and fixing 4 mm thick glass door of size 2.1 m x 1.2 m with anodized aluminium frame of size 0.10 x 0.05 M with centre opening for fire hose cabinet. Suitably marked on the outside with the letters FIRE HOSE including locking arrangement. All aluminium work to be in Red P.O. colour. | NOS | 1 | 33000 | 33000 | 25490 | 25490 | 16500 | 16500 | 16500 | 16500 | 14500 | 14500 | 14500 | 14500 | 20500 | 20500 | 20500 | 20500 | 20500 | 20500
97 | 14 | Providing and fixing ISI Marked of approved make Fire Extinguishers complete with all accessories as per manufacturer s specifications.
98 |  | a) CO2 gas nozzle type - 4.5kg capacity (IS 15683). | NOS | 10 | 8000 | 80000 | 8000 | 80000 | 6590 | 65900 | 5600 | 56000 | 4800 | 48000 | 4800 | 48000 | 8250 | 82500 | 5600 | 56000 | 5600 | 56000
99 |  | b) Mechanical Foam gas cartridge type. 6 lts capacity (IS 15683). | NOS | 6 | 15000 | 90000 | 10500 | 63000 | 8000 | 48000 | 5200 | 31200 | 3200 | 19200 | 3200 | 19200 | 4850 | 29100 | 4850 | 29100 | 4850 | 29100
100 |  | c) ABC dry powder stored pressure type 9 kg capacity (IS 15683). | NOS | 10 | 18500 | 185000 | 12000 | 120000 | 8000 | 80000 | 4800 | 48000 | 4800 | 48000 | 4800 | 48000 | 7650 | 76500 | 4850 | 48500 | 4850 | 48500
101 | 15 | Supplying, installing, testing and commissioning of HDPE water storage tank including holes for inlet, outlet, overflow level indicator drain and vent points, manhole cover suitable supporting structure complete.
102 |  | a) Capacity 5000 Lts. | NOS | 4 | 25000 | 100000 | 65000 | 260000 | 30000 | 120000 | 55000 | 220000 | 50000 | 200000 | 50000 | 200000 | 25000 | 100000 | 25000 | 100000 | 25000 | 100000
103 | 16 | Approval of fire (NOC) system from local fire authority at initial various other stages of works, including preperation of report integration with Fire alarm system and preparation of drawings as per local fire authority. Contractor shall include cost of all liasion works which are not explicity mentioned above but are mendatory to have fire authority approved. | No | 1 | 50000 | 50000 | 50000 | 50000 | 5000 | 5000 | 100000 | 100000 | 80000 | 80000 | 80000 | 80000 | 150000 | 150000 | 150000 | 150000 | 150000 | 150000
104 | 17 | Providing fixing C.P.brass quartzoid bulb sprinklers of size 15mm dia to be operated at 68Deg.C complete.Make of rosette plate- Veekay Sainath fire Safeworld approved equal.
105 |  | a) Pendant type with heavy duty adjustable SS rosette plate | NOS. | 44 | 320 | 14080 | 320 | 14080 | 80 | 3520 | 850 | 37400 | 650 | 28600 | 650 | 28600 | 1050 | 46200 | 1050 | 46200 | 1050 | 46200
106 |  | b) Side wall extended throw type with heavy duty adjustable SS rosette plate | NOS. | 2 | 350 | 700 | 350 | 700 | 200 | 400 | 1050 | 2100 | 850 | 1700 | 850 | 1700 | 1250 | 2500 | 1250 | 2500 | 1250 | 2500
107 | 18 | Providing Fixing of installation control valve with turbine type automatic Alarm Gong to be connected with control valve, drain test valve as per manufacturer s specifications complete.
108 |  | a) 80 mm dia | NO | 1 | 9900 | 9900 | 17000 | 17000 | 9900 | 9900 | 52000 | 52000 | 50000 | 50000 | 50000 | 50000 | 16500 | 16500 | 16500 | 16500 | 16500 | 16500
109 | 19 | Providing, jointing and testing of sprinklers through flexible connections(internal diameter 25mm outlet connection15mm dia.) as per requirement at site.Make-SeungJin-Korea.The flexible connectors shall be supported through false ceiling through clamps or as directed at site.The flexible connector shall be suitable for working pressure12 kg sqcm . | NOS | 44 | 4000 | 176000 | 4000 | 176000 | 1550 | 68200 | 1550 | 68200 | 1550 | 68200 | 1550 | 68200 | 2050 | 90200 | 2050 | 90200 | 2050 | 90200
110 | 20 | Providing installing MS 24 gauge fire buckets ( capacity of each bucket = 9 lts) filled with sand including MS stand for hanging the buckets.All MS items shall be painted with two coats of primer two coats of paint of approved colour.
111 |  | Set of four buckets with stand | NOS | 2 | 8500 | 17000 | 5500 | 11000 | 1500 | 3000 | 1500 | 3000 | 1500 | 3000 | 1500 | 3000 | 2500 | 5000 | 2500 | 5000 | 2500 | 5000
112 | 21 | Supply, installation, testing and commissioning of Down comer pump comprising of the following Suitable cement concrete foundation with plaster, Antivibration arrangement of cushy foot mounting. | NO | 1 | 30000 | 30000 | 200000 | 200000 | 120215 | 120215 | 65000 | 65000 | 55000 | 55000 | 55000 | 55000 | 165000 | 165000 | 125000 | 125000 | 125000 | 125000

## Technical Score Detail
|  | RFQ No: R2171 COST COMPARISON REPORT | RFQ No: R2171 COST COMPARISON REPORT | RFQ No: R2171 COST COMPARISON REPORT | Comp. Date : 15/11/2024 | Comp. Date : 15/11/2024 | Comp. Date : 15/11/2024 | Vendor Name : PIONEER PROJECT SOLUTION |  | Vendor Name : Mahamaya Engineering |  | Vendor Name : ANJLE MEP PROJECTS PVT LTD
|  | RFQ No: R2171 COST COMPARISON REPORT | RFQ No: R2171 COST COMPARISON REPORT | RFQ No: R2171 COST COMPARISON REPORT | RFQ #: R2171 | RFQ #: R2171 | RFQ #: R2171 | Contact Name : Mohd Ashraf |  | Contact Name : Yash Katoch |  | Contact Name : Priyanka/Premkant Rajpoot
|  | RFQ No: R2171 COST COMPARISON REPORT | RFQ No: R2171 COST COMPARISON REPORT | RFQ No: R2171 COST COMPARISON REPORT | RFQ Date : 07/11/2024 16:13:53 | RFQ Date : 07/11/2024 16:13:53 | RFQ Date : 07/11/2024 16:13:53 | Vendor City : |  | Vendor City : delhi |  | Vendor City :
|  | RFQ No: R2171 COST COMPARISON REPORT | RFQ No: R2171 COST COMPARISON REPORT | RFQ No: R2171 COST COMPARISON REPORT | BCD Date : 14/11/2024 23:58:00 | BCD Date : 14/11/2024 23:58:00 | BCD Date : 14/11/2024 23:58:00 | Telephone # : |  | Telephone # : 9810360460 |  | Telephone # :
|  | RFQ No: R2171 COST COMPARISON REPORT | RFQ No: R2171 COST COMPARISON REPORT | RFQ No: R2171 COST COMPARISON REPORT |  |  |  | Mobile # : |  | Mobile # : 9810360460 |  | Mobile # :
PR Number : TFSPL-2425-00911,TFSPL-2425-00912 | PR Number : TFSPL-2425-00911,TFSPL-2425-00912 | PR Number : TFSPL-2425-00911,TFSPL-2425-00912 | PR Number : TFSPL-2425-00911,TFSPL-2425-00912 | PR Number : TFSPL-2425-00911,TFSPL-2425-00912 | PR Number : TFSPL-2425-00911,TFSPL-2425-00912 | PR Number : TFSPL-2425-00911,TFSPL-2425-00912 | PR Number : TFSPL-2425-00911,TFSPL-2425-00912 | Email : projectspioneer@gmail.com |  | Email : mahamaya.engineering1@gmail.com |  | Email : anjlemepprojects@gmail.com
Package / RFQ Name : PR for HVAC & Fire Sprinkler for DEL DWARKA BASE KITCHEN - T1... | Package / RFQ Name : PR for HVAC & Fire Sprinkler for DEL DWARKA BASE KITCHEN - T1... | Package / RFQ Name : PR for HVAC & Fire Sprinkler for DEL DWARKA BASE KITCHEN - T1... | Package / RFQ Name : PR for HVAC & Fire Sprinkler for DEL DWARKA BASE KITCHEN - T1... | Package / RFQ Name : PR for HVAC & Fire Sprinkler for DEL DWARKA BASE KITCHEN - T1... | Package / RFQ Name : PR for HVAC & Fire Sprinkler for DEL DWARKA BASE KITCHEN - T1... | Package / RFQ Name : PR for HVAC & Fire Sprinkler for DEL DWARKA BASE KITCHEN - T1... | Package / RFQ Name : PR for HVAC & Fire Sprinkler for DEL DWARKA BASE KITCHEN - T1... | Round # : 2 (RFQ) |  | Round # : 2 (RFQ) |  | Round # : 2 (RFQ)
Buyer : Pushpak Mahesh Shewale | Buyer : Pushpak Mahesh Shewale | Buyer : Pushpak Mahesh Shewale | Buyer : Pushpak Mahesh Shewale | Buyer : Pushpak Mahesh Shewale | Buyer : Pushpak Mahesh Shewale | Buyer : Pushpak Mahesh Shewale | Buyer : Pushpak Mahesh Shewale | Quotation Date : |  | Quotation Date : |  | Quotation Date :
Comp. # : 2 | Comp. # : 2 | Comp. # : 2 | Comp. # : 2 | Comp. # : 2 | Currency :INR | Currency :INR | Currency :INR | Quotation Validity Date : |  | Quotation Validity Date : |  | Quotation Validity Date :
Comp. # : 2 | Comp. # : 2 | Comp. # : 2 | Comp. # : 2 | Comp. # : 2 | BUDGET PRICE : | .00 |  | Quote Currency : |  | Quote Currency : |  | Quote Currency :
# | Item Code | Item Description | Last PO Details | Unit | Qty | Last PO Unit Rate | Last PO Total Value | Score | Justification | Score | Justification | Score | Justification
1 |  | High side |  | NOS | 1.000 | 0.00 | 0.00
2 | A | SPLIT UNITS Supply , Installation, Testing and Commissioning of split units, each comprising of an outdoor and a single indoor unit as shown on the drawings and as per the specifications. Enclosures shall be factory fabricated and painted to a smooth finish. Oudoor unit shall consist of hermatically sealed semi- hermatic scroll rotary compressor s, air cooled condenser with fan. Indoor unit shall consist of fan section with dynamically balanced centrifugal fan s driven by FHP TEFC squirrel cage induction motor, multirows deep DX- copper cooling coil with aluminium fins, thermostatic expansion valve, synthetic fibre filters, insulated drain pan, safety controls, safety controls, thermostat all complete in a unit. The quoted price shall be inclusive of full charge of refrigerant gas, vibration isolation arrangement. Refrigerant Shall be R-32 R410A R407C Three phase ductable split units with Scroll compressor Unit should be suitable to handle total 35-40RM inter unit referigerant piping inlcuding 12-15RM vertical length. 8.5TR nominal capacity, split unit with single ductable type indoor unit and factory fitted electrical arrangement corded remote. |  | No | 1.000 | 0.00 | 0.00
3 | B | Single phase Non-ductable split units with Rotary compressor (Three Star Rating) (Units should be suitable to handle piping length upto 24-25 RM) 1.5TR nominal capacity, split unit with single Wall Mounted type indoor unit and cordless control . Price shall be inclusive of copper power cabling from indoor to outdoor unit as required. |  | No | 2.000 | 0.00 | 0.00
4 |  | SECTION B KITCHEN VENTILATION SYSTEM |  |  | 0.000 | 0.00 | 0.00
5 |  | DOUBLE SKIN AIR COOLING MACHINES - With Fresh Air Intake Section (AIR WASHERS) Supply , Installation, Testing and Commissioning of double skin type evaporative air cooling machines (packaged type) each comprising of following as per the specifications Casing of air washer shall be in double skin construction. Inner skin shall be constructed out of24 gauge plain GS sheet outer skin in 24 gauge pre-plasticized GS sheet sandwitched between 50mm thick injected PU foam insulation of density not less than 40 Kg CuM and complete with marine light,limit switch inspection doors including control wiringas required. Air washer shall have access for all parts. Fan section complete with backward curved DIDW type centrifugal fan s, EFF1, IE3, IP-55, rated TEFC squirrel cageinduction motor suitable to operate on 415+10%V, 50Hz,3 phase AC power supply and belt drive package.Centrifugal fans shall be coated with epoxy paint as specified. Fan outlet velocity shall not be more than 2000 FPM (10.16 MPS).All fans should be AMCA certified. AirWasher shall be provided with Intake Section withF A openings as per approved shop drawing. Air washer wet section shall be complete with 300mm thick cellulose based paper fills, drift eliminators,water distribution system complete with FRP spray headers, strainer of fine mesh brass screen, globe valve,float valve, quick fill, over flow drainconnections, GI medium class piping and 3 1 phasemonobloc pumps of 1HP 1.5HP 2HP motor rating as required according to the capacity of air cooling machines. Inner skin of wet section including fills mounting frame shall be constructed out of stainless steel SS- 304 A grade of appropriate thickness .Sump shall be made out of 1.25mm thick SS-304 A grade stainless steel .Velocity across the paper fills not to exceed 500 FPM. Filter section complete with 50mm thick aluminiumwire mesh viscous metallic filters. Velocity across the filters shall not exceed 500 FPM. Airwasher should be provided with adequate space between eliminator fan to avoid water carryover.The Evaporative Air Cooling Machines (EAC) shall be of following duty parameters M c No Capacity S.P Motor Area to (Cfm) (mmWG) Rating be fed (HP)EAC-1 1x22500 58-60 1x15.0 Kitchen |  | No | 1.000 | 0.00 | 0.00
6 | 1.2 | SCRUBBER (For Kitchen Exhaust) WET TYPE SCRUBBER Supply , Installation , Testing and Commissioning of wet type scrubber (packaged type) comprising of following as per the specifications Fan section complete with backward curved DIDW type centrifugal fan s, TEFC squirrel cage inductionmotor suitable to operate on 415+10%V, 50Hz,3 phase AC power supply and belt drive package.Casing of wet type scrubber shall be constructedout of 16 gauge GS sheet complete with inspectiondoors as required. Centrifugal fans shall be coatedwith epoxy paint as specified. Fan outlet velocity shall not be more than 2000 FPM (10.16 MPS). Wet section complete with double bank spray header in GI construction and nozzles, louvers PVC mist eliminators mist collection tray made out of 16G GSS,strainer of fine mesh brass screen, globe valve,float valve, quick fill, over flow drainconnections, GI medium class piping and 3 phasemonobloc pump of 1.5HP motor rating as required according to the capacity of scrubber machines. Wet section including sump will be made of1.25mm thick SS-304 A grade stainless steel . In addition to the above, scrubber shall be provided with adequate vibration isolation padsand fire retardent flexible canvass connections madeout of canvass sleeve.The Scrubber Machines (EAC) shall be of following duty parameters M c No Capacity S.P Motor Area to (Cfm) (mmWG) Rating be fed (HP)WS-1 28000 68-70 20.0 Kitchen Area |  | No | 1.000 | 0.00 | 0.00
7 |  | INLINE FANS (Single Phase) Supply, Installation, Testing Commissioning of circular rectangular inline fans for exhaust air complete with sheet metal casing, direct driven centrifugal fan, motor with proper protection and inspection door. Fan shall be suitable for operation on 220+6 % volts, 50 Hz,1phase AC power supply. Fan shall be installed as shown in the drawings and will be of following characteristics All single phase inline fans shall be provided with factory fitted speed regulators. All Fans Should be complete with Plug Top necessary power cable. Fan Capacity S.P Area to No. (Cfm) (mmWG) to be exhausted IF-1(Circular) 300 14-15 Pantry |  | No | 1.000 | 0.00 | 0.00
8 |  | Low side |  | NOS | 1.000 | 0.00 | 0.00
9 |  | REFRIGERANT PIPING Supply, Installation,Testing Commissioning of copper refrigerant piping complete with copper fittings charge of regrigerant gas for the above split units. Piping associated with split units to be insulated with 19mm thick closed cell elastomeric insulation with Class O in tubing form as required. Piping shall be laid over duly painted slotted angle trays fixed with GI clamps. Quoted Price shall be inclusive of UV protection paint for all exposed pipes of approved make. Price shall be inclusive of copper power cabling from indoor to outdoor unit as required. Referigerant piping shall be epoxy coated to prevent erosion. |  |  | 0.000 | 0.00 | 0.00
10 | a. | Pair of hard drawn copper refrigerant piping for the above split units with scroll compressor. |  | RM | 25.000 | 0.00 | 0.00
11 | b. | Pair of Soft refrigerant piping for non ductable split units with rotary compressor. |  | RM | 55.000 | 0.00 | 0.00
12 | 1 | MS FRAME FOR ODUs Supply and Erection of MS base frame duly applied with red-oxide primer followed by black enamel paint for mounting of outdoor units. |  | Kg | 55.000 | 0.00 | 0.00
13 | 2 | PIPING CONDENSATE DRAIN PIPING -cPVC Supply, Installation, Testing and Commissioning of cPVC pipes cut to required lengths and installed for condensate drain. Quoted price shall be inclusive of supply and fixing in position the necessary fittings like elbows, tees reducers etc. and supporting arrangement in accordance with the approved shop drawings and specifications. Pipes shall be insulated with 9mm thick closed cell elastomeric insulation with class O fire retardant properties in tubing form . Pipes shall be of following sizes |  |  | 0.000 | 0.00 | 0.00
14 | a. | 50mm dia |  | RM | 5.000 | 0.00 | 0.00
15 | b. | 40mm dia |  | RM | 10.000 | 0.00 | 0.00
16 | c. | 32mm dia |  | RM | 2.000 | 0.00 | 0.00
17 | d. | 25mm dia |  | RM | 5.000 | 0.00 | 0.00
18 | 3 | DUCTWORK AIR TERMINALS FACTORY FABRICATED DUCTING Supply , Installation and Testing of factory fabricated GSS ducting complete with vanes, splitter dampers, fire retardant gaskets hanging arrangement including fully threaded GI rods and GI C channels, GI C channels etc. as approved by clients consultants in accordance with the approved shop drawings and specifications. Quoted price shall be inclusive of necessary scaffolding charges towards installation of supply exhaust air ducts outside or within building wherever required. Quoted price should also include necessary charges towards duct supporets including MS angle channel arrangement as required for ducts being installed outside or within building wherever required. Spacing between duct supports should not exceed 2m. All duct support to be provided with check nuts (lock nuts). While selecting the duct supports vendor shall ensure vibration free installation.Quoted price shall be inclusive of smoke test using smoke bombs. |  |  | 0.000 | 0.00 | 0.00
19 | a. | 1mm to 899mm -- 26G GSS with TDC Joints |  | SqM | 5.000 | 0.00 | 0.00
20 | b. | 900mm to 1200mm -- 24G GSS with TDC Joints |  | SqM | 10.000 | 0.00 | 0.00
21 | c. | 1201mm to 1800mm - 22G GSS with TDC Joints |  | SqM | 5.000 | 0.00 | 0.00
22 | 3.2 | SITE FABRICATED DUCTING Supply, Fabrication, Installation and Testing of sheet metal ducts complete with vanes, splitter dampers, hanging arrangement including check nuts in accordance with the approved shop drawings and specifications |  |  | 0.000 | 0.00 | 0.00
23 |  | a. 0.63mm (24 gauge) GSS |  | SqM | 10.000 | 0.00 | 0.00
24 |  | b. 0.8 mm (22 gauge) GSS |  | SqM | 5.000 | 0.00 | 0.00
25 | 3.3 | FLEXIBLE CANVASS CONNECTIONS Supply, Installation, Testing of 125mm deep antivibration flexible joints at the outlet of air handling units ductable split units inline fans. Flexible connections shall be constructed using imported fire retardant fabric with extruded aluminium frame flange on both sides of approved make. |  | RM | 4.000 | 0.00 | 0.00
26 | 3.4 | LINEAR GRILLES Supply, Installation , Testing and Balancing of one way blow linear supply cum return air grilles complete with fixed core as per approved shop drawings and specifications. The grilles shall be of approved colour shade. Powder coated aluminium grilles of extruded sections with integral flanges on both sides ends as required complete with corner pieces. i. 100 150 200 250 mm High grilles |  | SqM | 1.000 | 0.00 | 0.00
27 | 3.5 | DOUBLE LOUVERED GRILLES Supply, Installation ,Testing and Balancing of double louvered supply air grilles as per approved shop drawings and specifications complete with key operated aluminium volume control dampers. a. Powder coated extruded aluminium grilles. |  | SQM | 0.500 | 0.00 | 0.00
28 | 3.6 | AIR TRANSFER GRILLES Supply, Installation and Testing of extruded aluminium powder coated air transfer grilles to be provided at the door of toilets pantry. |  | SQM | 0.200 | 0.00 | 0.00
29 | 3.7 | Supply, Installation and Testing of GI box type volume control dampers as per the specifications and shop drawings.- For Rectangular Duct |  | SqM | 0.500 | 0.00 | 0.00
30 | 3.8 | Supply, Installation and Testing of GI multi blade type louver dampers as per the specifications and shop drawings. |  | SqM | 1.000 | 0.00 | 0.00
31 | 4.1 | INSULATION ACOUSTIC LINING OF DUCTS Using Open Cell Nitrile Rubber Supply and Application of internal acoustic lining of supply air ducting using open cell nitrile rubber insulation with density within 140-180 Kg m3 as per the approved shop drawings and specifications. Insulation material shall be bonded with the ducts using metal screw and washers to facilitate grip to the GI sheet. Adhesive used shall be Low VOC type. 10mm thick lining |  | SqM | 5.000 | 0.00 | 0.00
32 | 4.2 | INSULATION ACOUSTIC LINING OF DUCTS Using Fibre Glass Supply and Application of internal acoustic lining of supply return air ducting using resin bonded fibre glass insulation of density not less than 32Kg CuM as per the approved shop drawings and specifications. Quoted price shall be inclusive of GSS channel, metal screws, washers, fibre glass tissue, perforated sheet etc. as required for complete installation. a. 25mm thick lining |  | SqM | 10.000 | 0.00 | 0.00
33 | 5 | THERMAL INSULATION OF DUCTS (Using Factory Laminated aluminium foil faced,Class O Closed Cell Elastomeric insulation) Supply and Application of internal external thermal insulation of supply return air ducting using closed cell elastomeric insulation with class O fire retardant properties as per the specifications and drawings.Adhesive used shall be Low VOC type. a. 13mm thick insulation |  | SQM | 30.000 | 0.00 | 0.00
34 | 6 | AIR CURTAIN Supply , Installation and Testing of air curtains with noiseless, statically dynamically balanced aluminium blowers, cleanable type pre-filters, motor powder coated aluminium enclosure as per the specifications. Unit shall be complete with Plug Top necessary power cable. |  |  | 0.000 | 0.00 | 0.00
35 | b. | 2.1 M long air curtain |  | No | 1.000 | 0.00 | 0.00
36 | c. | 1.5 M long air curtain |  | No | 2.000 | 0.00 | 0.00
37 | 7 | DUCTWORK AIR TERMINALS - INCLUDING IN SECTION A FACTORY FABRICATED DUCTING Supply, Installation and Testing of factory fabricated GSS ducting complete with vanes,splitter dampers, fire retardant gaskets, hanging arrangement including fully threaded GI rods and GI C channels rolled steel wires or Gripple Wire Rope Hangers Supports complete with end fixing, GI C channels etc. as approved by clients consultants in accordance with the approved shop drawings and specifications. Quoted price shall be inclusive of necessary scaffolding charges towards installation of supply exhaust air ducts outside or within building wherever required. Spacing between duct supports should not exceed 2m in both cases i.e GI rods with GI C channels Gripple Wire Rope Hanger support . In case of Gripple Wire Rope Hanger support for duct sizes above 1800mm, MS angles duly painted with black enamel paint should be used along with neoprene pad in between the duct MS angle. All duct supports shall be provided with check nuts (lock nuts). While selecting the duct supports vendor shall ensurevibration free installation.Quoted price shall be inclusive of smoke test using smoke bombs. For Air-Cooling ducts |  |  | 0.000 | 0.00 | 0.00
38 | a. | 1mm to 899mm -- 24G GSS with TDC Joints |  | SqM | 50.000 | 0.00 | 0.00
39 | b. | 900mm to 1500mm -- 22G GSS with TDC Joints |  | SqM | 50.000 | 0.00 | 0.00
40 | c. | 1501mm to 2100mm - 20G GSS with TDC Joints |  | SqM | 10.000 | 0.00 | 0.00
41 | 7.1 | SITE FABRICATED DUCTING Supply, Fabrication, Installation and Testing of sheet metal ducts complete with vanes, splitter dampers, hanging arrangement including check nuts in accordance with the approved shop drawings and specifications. |  |  | 0.000 | 0.00 | 0.00
42 | a. | a. 0.63mm (24 gauge) GSS |  | SqM | 15.000 | 0.00 | 0.00
43 | b. | b. 0.8 mm (22 gauge) GSS |  | SqM | 5.000 | 0.00 | 0.00
44 | c. | c. 1.0mm (20 gauge) GSS |  | SqM | 5.000 | 0.00 | 0.00
45 | 7.2 | For Kitchen Exhaust Supply, fabrication, Installation and testing of MS ductingfor kitchen exhaust contructed out of 2mm thick MS sheet using MS angle iron flanges in line with good engineering practice. Entire ducting shall be applied with minimum two coats of red oxide primer. Duct shall be provided with oil trap as required |  | SqM | 140.000 | 0.00 | 0.00
46 | 7.3 | FLEXIBLE CANVASS CONNECTIONS Supply, Installation, Testing of 125mm deep antivibration flexible joints at the outlet of air handling units ductable split units inline fans. Flexible connections shall be constructed using imported fire retardant fabric with extruded aluminium frame flange on both sides of approved make. |  | RM | 8.500 | 0.00 | 0.00
47 | 7.4 | LINEAR GRILLES Supply, Installation , Testing and Balancing of one way blow linear supply cum return air grilles complete with fixed core as per approved shop drawings and specifications. The grilles shall be of approved colour shade. Powder coated aluminium grilles of extruded sections with integral flanges on both sides ends as required complete with corner pieces. i. 100 150 200 250 mm High grilles |  | SqM | 8.000 | 0.00 | 0.00
48 | 8 | AIR TRANSFER GRILLES Supply, Installation and Testing of GI box type volume control dampers as per the specifications and shop drawings. |  | SQM | 3.500 | 0.00 | 0.00
49 | 9 | Supply, Installation and Testing of Aluminium multi bladetype louver dampers as per the specifications and shop drawings. |  | SqM | 6.000 | 0.00 | 0.00
50 | 10 | Supply, Installation and Testing of fresh air powdered coated anodised extruded aluminium louvers to be installed outside for suction ( airwashers), as per approved shop drawings and specifications. Sample of louvers to be got approved from consultants and Clients prior to procurement. |  | SqM | 1.000 | 0.00 | 0.00
51 | 11 | Supply, Installation and Testing of Bird Screens with GI wire mesh to be installed at the suction of fresh air discharge of Exhaust air as per the specifications and shop drawings.Sample of bird screen to be got approved from consultants and Clients prior to procurement. |  | SqM | 1.000 | 0.00 | 0.00
52 | 12 | INSULATION THERMAL INSULATION OF DUCTS-(FOR AIR SCRUBBER DUCT) (Using Factory Laminated fibre glass insulation) Supply and Application of external thermal insulation of supply return air ducting using aluminium foil faced fibre glass insulation of density not less than 24Kg CuM and aluminium foil thickness of 22 microns as per the specifications and drawings. Quoted price shall be inclusive of Low VOC adhesive as required, aluminium tape straps. 50mm thick insulation |  | SqM | 140.000 | 0.00 | 0.00
53 | 13 | THERMAL INSULATION OF DUCTS-(FOR AIR SCRUBBER DUCT) - EXPOSED (Using Factory Laminated fibre glass insulation) Supply and Application of external thermal insulation of supply return air ducting using aluminium foil faced fibre glass insulation of density not less than 24Kg CuM and aluminium foil thickness of 22 microns as per the specifications and drawings. Quoted price shall be inclusive of Low VOC adhesive as required, aluminium tape straps. Insulation shall be covered necessary glass cloth UV protection paint. 50mm thick insulation |  | SqM | 15.000 | 0.00 | 0.00
54 | a. | THERMAL INSULATION OF DUCTS - Air Washer (Using aluminium foil faced Class O Fire Retardant Properties Closed Cell Elastomeric insulation) Supply and Application of external thermal insulation of supply return air ducting using factory laminated aluminium foil faced closed cell elastomeric nitrile rubber insulation with class O fire retardant properties as per the specifications and drawings. aluminium foil face shall provide protection from mechanical impact, and Scratches etc. Both insulation aluminium foil layer should have built in antimicrobial protection. Expose insulation shall be covered with necessary glass cloth UV protection paint. Adhesive - AC Duct King Eco Fresh 25mm thick insulation - For AC Duct in Kitchen |  | SqM | 135.000 | 0.00 | 0.00
55 | 14 | KVF PANEL -1 (Location Kitchen ) - 13.8KW For 9700Cfm Air Washers Pump, 12100Cfm SISW Fan ESP Incoming 63 Amps ,TP MCCB with electronic release earth fault relay, door interlock and front drive rotor kit-- 1set(0-500) V digital Voltmeter with built in Selectorswitch -- 1setDigital Ammeter with built in selector switch- 1setCurrent Transformers - 1setLED type RYB phase indication lights- 1setBusbar100 Amps TPN aluminium busbar havingsuitable fault level, with PVC heat shrunk sleeves on SMC DMC supports. |  | No | 1.000 | 0.00 | 0.00
56 | 15 | CABLING Supply, laying, affecting connections andarmoured PVC insulated aluminium copperconductor cables. Cables shall be inclusive ofall clamps, saddles, screws, cable identificationtags, cable terminal joints including terminallugs, insulating tapes, affecting terminal connections to the equipment as per the specifications and as required. Quoted priceshall be inclusive of perforated duly painted2mm thick MS trays to be installed inside and8SWG copper earth wire for all equipment.EQUIPMENT |  |  | 0.000 | 0.00 | 0.00
57 | a. | 3 C x 10 Sqmm cable (Copper) |  | RM | 10.000 | 0.00 | 0.00
58 | b. | 3 C x 6 Sqmm cable (Copper) |  | RM | 20.000 | 0.00 | 0.00
59 | c. | 3 C x 2.5 Sqmm cable (Copper) |  | RM | 5.000 | 0.00 | 0.00
60 | d. | 3 C x 2.5 Sqmm cable( Copper Control cabling) |  | RM | 5.000 | 0.00 | 0.00
61 | e | 3 C x 1.5 Sqmm cable(Copper Control cabling) |  | RM | 10.000 | 0.00 | 0.00
62 | 16 | Supply and fixing of 1.1 KV grade rubbermat 914.4 mm wide 6mm thick to withstand 1.1 KV dielectric strength in front of each panel. |  | RM | 2.000 | 0.00 | 0.00
63 | 17 | Supply, Installation Testing of TPN isolator in weather proof enclosure near fans |  | No | 2.000 | 0.00 | 0.00
64 |  | Fire Sprinkler System |  | NOS | 1.000 | 0.00 | 0.00
65 | 1 | Providing, laying, jointing and testing of following sizes of pipes conforming to IS-1239 with all accessories like all fittings (upto 50mm dia threaded M.S.forged fittings and above 50 mm dia MS fittings with welded joints shall be used)fittings including tees, elbows, reducers, flanges, rubber gaskets, nuts bolts, washer. And fixing the pipe on floor wall ceiling with suitable size clamps, hangers, structural steel supports as per specification. And PVC pipe sleeve to be provided wherever the pipes are crossing the walls floors and sealing the sleeves as per consultants requirements including cutting holes and chases in brick, R.C.C work and making good the same to original conditions complete in all respects.Arrows showing direction of flow to be marked(with paint of approved colour) on each pipe at locations as decided at site. |  |  | 0.000 | 0.00 | 0.00
66 | (a) | For Fire fighting sprinkler System - M.S. `C Heavy class pipe |  |  | 0.000 | 0.00 | 0.00
67 |  | a)25 mm dia(4.04mm thickness) screwed joint |  | RM | 90.000 | 0.00 | 0.00
68 |  | b)32 mm dia(4.05mm thickness)screwed joint |  | RM | 10.000 | 0.00 | 0.00
69 |  | c) 40 mm dia(4.05mm thickness)screwed joint |  | RM | 20.000 | 0.00 | 0.00
70 |  | d) 50 mm dia(4.5mm thickness)screwed joint |  | RM | 15.000 | 0.00 | 0.00
71 |  | e) 65 mm dia(4.5mm thickness) |  | RM | 20.000 | 0.00 | 0.00
72 |  | f) 80 mm dia(4.85mm thickness) |  | RM | 100.000 | 0.00 | 0.00
73 |  | g)100 mm dia(5.4mm thickness) |  | RM | 10.000 | 0.00 | 0.00
74 | 2 | Providing two coats of synthetic enamel paint of approved shade over a coat of primer. Including painting of legends both direction arrow as per the approval of the architects consultants. |  |  | 0.000 | 0.00 | 0.00
75 |  | a)25 mm dia |  | RM | 90.000 | 0.00 | 0.00
76 |  | b)32 mm dia |  | RM | 10.000 | 0.00 | 0.00
77 |  | c) 40 mm dia |  | RM | 20.000 | 0.00 | 0.00
78 |  | d) 50 mm dia |  | RM | 15.000 | 0.00 | 0.00
79 |  | e) 65 mm dia |  | RM | 20.000 | 0.00 | 0.00
80 |  | f) 80 mm dia |  | RM | 100.000 | 0.00 | 0.00
81 |  | g)100 mm dia |  | RM | 10.000 | 0.00 | 0.00
82 | 3 | Providing and fixing gun metal ball valve suitable for pressure 15 Kg Cm2 and confirming to IS 778 of the following size including providing necessary union flange. |  |  | 0.000 | 0.00 | 0.00
83 |  | a) 25 mm dia |  | NO. | 1.000 | 0.00 | 0.00
84 |  | b) 50 mm dia |  | NO. | 1.000 | 0.00 | 0.00
85 | 4 | Providing fixing of butterfly valve suitable for pressure 15 Kg Sqcm. with flanges, nut bolts gaskets complete required. |  |  | 0.000 | 0.00 | 0.00
86 |  | a) 65 mm dia |  | NO. | 1.000 | 0.00 | 0.00
87 |  | b) 80 mm dia |  | NOS | 3.000 | 0.00 | 0.00
88 |  | c) 100 mm dia |  | NOS | 2.000 | 0.00 | 0.00
89 | 5 | Providing and fixing of C.I. wafer type check valve suitable for pressure 15 Kg Sqcm. with flanges, Nut, bolts washers, painting etc. complete as required. |  |  | 0.000 | 0.00 | 0.00
90 |  | a) 80 mm dia |  | NOS. | 1.000 | 0.00 | 0.00
91 | 6 | Providing and fixing C.I.`Y strainer with bronze perforated sheet basket tested to a pressure of 15 Kg sqcm including rubber gasket, flanges, nuts, bolts and washers, complete as required. |  |  | 0.000 | 0.00 | 0.00
92 |  | b) 100 mm dia |  | NO. | 1.000 | 0.00 | 0.00
93 | 7 | Providing fixing gun metal fire hydrant valve with 80 mm N.B. flanged inlet, brass spindal, one no. 63 mm dia female instantaneous outlet type. G.M. coupling,blank cap, chain. Conforming to IS 5290. Including tapping from wet riser complete as required. |  | NOS | 1.000 | 0.00 | 0.00
94 | 8 | Providing fixing swinging type First Aid hose reel in red colour with 36 mts long and 20 mm dia dia heavy duty rubber water hose, 20 mm dia globe valve stop cock, terminating with G.M. coupling nozzle of 5mm outlet with shut off valve confirming to IS 8090 - 1976 complete with drum and brackets for fixing on wall, bolts nuts conforming to IS 884-1969 complete as required. |  | NOS | 1.000 | 0.00 | 0.00
95 | 9 | Providing and Fixing Hose pipe, 63 mm dia and 15 mts long, duly reinforced, rubber lined suitable for brusting pressure not less than 22 Kg Sqcm. conforming to IS 636-1988 type A with gun metal heavy duty instantaneous type coupling ( Pair male female parts) conforming to IS 903. Complete as required (two nos. for each hydrant) |  | NOS | 2.000 | 0.00 | 0.00
96 | 10 | Providing and Fixing 63 mm dia instantaneous pattern branch short gunmetal pipe, 16 mm dia nozzle conforming to IS 903, suitable for inter connection to hose pipe coupling complete as required. |  | NOS | 1.000 | 0.00 | 0.00
97 | 11 | Providing and fixing standard firemans axe with heavy rubber handle. |  | NOS | 1.000 | 0.00 | 0.00
98 | 12 | Providing and fixing inlet breaching having C.I. body Two way gun metal 63 mm dia instantaneous inlets conforming to IS 903 fitted with non return valves, 25 mm dia gun metal drain cock, blank cap, brass chains and 100 mm dia flanges with all accessories suitable for local fire tender complete as required. |  | NO | 1.000 | 0.00 | 0.00
99 | 13 | Providing and fixing 4 mm thick glass door of size 2.1 m x 1.2 m with anodized aluminium frame of size 0.10 x 0.05 M with centre opening for fire hose cabinet. Suitably marked on the outside with the letters FIRE HOSE including locking arrangement. All aluminium work to be in Red P.O. colour. |  | NOS | 1.000 | 0.00 | 0.00
100 | 14 | Providing and fixing ISI Marked of approved make Fire Extinguishers complete with all accessories as per manufacturer s specifications. |  |  | 0.000 | 0.00 | 0.00
101 |  | a) CO2 gas nozzle type - 4.5kg capacity (IS 15683). |  | NOS | 10.000 | 0.00 | 0.00
102 |  | b) Mechanical Foam gas cartridge type. 6 lts capacity (IS 15683). |  | NOS | 6.000 | 0.00 | 0.00
103 |  | c) ABC dry powder stored pressure type 9 kg capacity (IS 15683). |  | NOS | 10.000 | 0.00 | 0.00
104 | 15 | Supplying, installing, testing and commissioning of HDPE water storage tank including holes for inlet, outlet, overflow level indicator drain and vent points, manhole cover suitable supporting structure complete. |  |  | 0.000 | 0.00 | 0.00
105 |  | a) Capacity 5000 Lts. |  | NOS | 4.000 | 0.00 | 0.00
106 | 16 | Approval of fire (NOC) system from local fire authority at initial various other stages of works, including preperation of report integration with Fire alarm system and preparation of drawings as per local fire authority. Contractor shall include cost of all liasion works which are not explicity mentioned above but are mendatory to have fire authority approved. |  | No | 1.000 | 0.00 | 0.00
107 | 17 | Providing fixing C.P.brass quartzoid bulb sprinklers of size 15mm dia to be operated at 68Deg.C complete.Make of rosette plate- Veekay Sainath fire Safeworld approved equal. |  |  | 0.000 | 0.00 | 0.00
108 |  | a) Pendant type with heavy duty adjustable SS rosette plate |  | NOS. | 44.000 | 0.00 | 0.00
109 |  | b) Side wall extended throw type with heavy duty adjustable SS rosette plate |  | NOS. | 2.000 | 0.00 | 0.00
110 | 18 | Providing Fixing of installation control valve with turbine type automatic Alarm Gong to be connected with control valve, drain test valve as per manufacturer s specifications complete. |  |  | 0.000 | 0.00 | 0.00
111 |  | a) 80 mm dia |  | NO | 1.000 | 0.00 | 0.00
112 | 19 | Providing, jointing and testing of sprinklers through flexible connections(internal diameter 25mm outlet connection15mm dia.) as per requirement at site.Make-SeungJin-Korea.The flexible connectors shall be supported through false ceiling through clamps or as directed at site.The flexible connector shall be suitable for working pressure12 kg sqcm . |  | NOS | 44.000 | 0.00 | 0.00
113 | 20 | Providing installing MS 24 gauge fire buckets ( capacity of each bucket = 9 lts) filled with sand including MS stand for hanging the buckets.All MS items shall be painted with two coats of primer two coats of paint of approved colour. |  |  | 0.000 | 0.00 | 0.00
114 |  | Set of four buckets with stand |  | NOS | 2.000 | 0.00 | 0.00
115 | 21 | Supply, installation, testing and commissioning of Down comer pump comprising of the following Suitable cement concrete foundation with plaster, Antivibration arrangement of cushy foot mounting. |  | NO | 1.000 | 0.00 | 0.00