## Price Comparison
|  | RFQ No: R0040 COST COMPARISON REPORT | RFQ No: R0040 COST COMPARISON REPORT | RFQ No: R0040 COST COMPARISON REPORT | Comp. Date : 15/01/2024 | Comp. Date : 15/01/2024 | Comp. Date : 15/01/2024 | Vendor Name : PIONEER PROJECT SOLUTION (RV232414136) | [10 empty] | Vendor Name : ANJLE MEP PROJECTS PVT LTD (RV232413533) | [10 empty] | Vendor Name : Pikture Perfect Design Studio Pvt. Ltd (RV232413816)
|  | RFQ No: R0040 COST COMPARISON REPORT | RFQ No: R0040 COST COMPARISON REPORT | RFQ No: R0040 COST COMPARISON REPORT | RFQ #: R0040 | RFQ #: R0040 | RFQ #: R0040 | Contact Name : Mohd Ashraf | [10 empty] | Contact Name : Priyanka/Premkant Rajpoot | [10 empty] | Contact Name : Gangadhar Sharma
|  | RFQ No: R0040 COST COMPARISON REPORT | RFQ No: R0040 COST COMPARISON REPORT | RFQ No: R0040 COST COMPARISON REPORT | RFQ Date : 13/01/2024 15:17:25 | RFQ Date : 13/01/2024 15:17:25 | RFQ Date : 13/01/2024 15:17:25 | Vendor City : | [10 empty] | Vendor City : | [10 empty] | Vendor City :
|  | RFQ No: R0040 COST COMPARISON REPORT | RFQ No: R0040 COST COMPARISON REPORT | RFQ No: R0040 COST COMPARISON REPORT | BCD Date : | BCD Date : | BCD Date : | Telephone # : | [10 empty] | Telephone # : | [10 empty] | Telephone # :
|  | RFQ No: R0040 COST COMPARISON REPORT | RFQ No: R0040 COST COMPARISON REPORT | RFQ No: R0040 COST COMPARISON REPORT |  |  |  | Mobile # : | [10 empty] | Mobile # : | [10 empty] | Mobile # :
PR Number : TFSPL-2324-00102 | PR Number : TFSPL-2324-00102 | PR Number : TFSPL-2324-00102 | PR Number : TFSPL-2324-00102 | PR Number : TFSPL-2324-00102 | PR Number : TFSPL-2324-00102 | PR Number : TFSPL-2324-00102 | PR Number : TFSPL-2324-00102 | Email : projectspioneer@gmail.com | [10 empty] | Email : anjlemepprojects@gmail.com | [10 empty] | Email : piktureperfectdesignstudio@gmail.com
Package / RFQ Name : TFAS / RFQ / TFSPL-2324-00102 | Package / RFQ Name : TFAS / RFQ / TFSPL-2324-00102 | Package / RFQ Name : TFAS / RFQ / TFSPL-2324-00102 | Package / RFQ Name : TFAS / RFQ / TFSPL-2324-00102 | Package / RFQ Name : TFAS / RFQ / TFSPL-2324-00102 | Package / RFQ Name : TFAS / RFQ / TFSPL-2324-00102 | Package / RFQ Name : TFAS / RFQ / TFSPL-2324-00102 | Package / RFQ Name : TFAS / RFQ / TFSPL-2324-00102 | Round # : 1 (RFQ) |  |  |  |  | Round # : 2 (Auction) | [5 empty] | Round # : 1 (RFQ) |  |  |  |  | Round # : 2 (Auction) | [5 empty] | Round # : 1 (RFQ) |  |  |  |  | Round # : 2 (Auction)
Buyer : Jogeswar Sahu / Technical : / Approver : | Buyer : Jogeswar Sahu / Technical : / Approver : | Buyer : Jogeswar Sahu / Technical : / Approver : | Buyer : Jogeswar Sahu / Technical : / Approver : | Buyer : Jogeswar Sahu / Technical : / Approver : | Buyer : Jogeswar Sahu / Technical : / Approver : | Buyer : Jogeswar Sahu / Technical : / Approver : | Buyer : Jogeswar Sahu / Technical : / Approver : | Quotation Date : |  | Quotation Validity Date : |  |  | Quotation Date : |  |  | Quotation Validity Date : |  |  | Quotation Date : |  | Quotation Validity Date : |  |  | Quotation Date : |  |  | Quotation Validity Date : |  |  | Quotation Date : |  | Quotation Validity Date : |  |  | Quotation Date : |  |  | Quotation Validity Date :
Comp. # : 2 | Comp. # : 2 | Comp. # : 2 | Comp. # : 2 | Comp. # : 2 | Currency :INR | Currency :INR | Currency :INR | Buyer Remark : |  |  |  |  | Buyer Remark : . | [5 empty] | Buyer Remark : |  |  |  |  | Buyer Remark : | [5 empty] | Buyer Remark : |  |  |  |  | Buyer Remark :
Comp. # : 2 | Comp. # : 2 | Comp. # : 2 | Comp. # : 2 | Comp. # : 2 | BUDGET PRICE : | .00 |  | Quote Currency : INR |  |  |  |  | Quote Currency : INR | [5 empty] | Quote Currency : INR |  |  |  |  | Quote Currency : INR | [5 empty] | Quote Currency : INR |  |  |  |  | Quote Currency : INR
# | Item Code | Item Description | Unit | Qty | Last PO Details | Lowest Unit Rate | Lowest Vendor | Price | Disc % | GST % | Unit Price | Total | Price | Disc % | GST % | Technical | Unit Price | Total | Price | Disc % | GST % | Unit Price | Total | Price | Disc % | GST % | Technical | Unit Price | Total | Price | Disc % | GST % | Unit Price | Total | Price | Disc % | GST % | Technical | Unit Price | Total
1 |  | HVAC low side | NOS | 1.00 |  | 391700.00 | PIONEER PROJECT SOLUTION | 402770.00 | 0.00 | 18.00 | 402,770.00 | 402,770.00 | 402770.00 | 0.00 | 0.00 |  | 391,700.00 | 391,700.00 | 477550.00 | 0.00 | 18.00 | 477,550.00 | 477,550.00 | 477550.00 | 0.00 | 0.00 |  | 477,550.00 | 477,550.00 | 897125.00 | 0.00 | 18.00 | 897,125.00 | 897,125.00 | 897125.00 | 0.00 | 0.00 |  | 897,125.00 | 897,125.00
2 |  | HVAC High Side | NOS | 1.00 |  | 405000.00 | PIONEER PROJECT SOLUTION | 470000.00 | 0.00 | 18.00 | 470,000.00 | 470,000.00 | 470000.00 | 0.00 | 0.00 |  | 405,000.00 | 405,000.00 | 635500.00 | 0.00 | 18.00 | 635,500.00 | 635,500.00 | 635500.00 | 0.00 | 0.00 |  | 635,500.00 | 635,500.00 | 459000.00 | 0.00 | 28.00 | 459,000.00 | 459,000.00 | 459000.00 | 0.00 | 0.00 |  | 459,000.00 | 459,000.00
Item Total | [8 empty] | .00 | 157,098.60 |  | 872,770.00 |  | .00 | .00 |  |  | 796,700.00 |  | .00 | 200,349.00 |  | 1,113,050.00 |  | .00 | .00 |  |  | 1,113,050.00 |  | .00 | 290,002.50 |  | 1,356,125.00 |  | .00 | .00 |  |  | 1,356,125.00
Discount Total Value | [7 empty] | Grand Dis. Amt | .00 |  |  | .00 | Grand Dis. Amt | .00 |  |  |  | .00 | Grand Dis. Amt | .00 |  |  | .00 | Grand Dis. Amt | .00 |  |  |  | .00 | Grand Dis. Amt | .00 |  |  | .00 | Grand Dis. Amt | .00 |  |  |  | .00
GST Total Amount | [11 empty] | 157,098.60 | [5 empty] | .00 |  |  |  |  | 200,349.00 | [5 empty] | .00 |  |  |  |  | 161,482.50 | [5 empty] | .00
Net Landed Cost | [10 empty] | INR | 1,029,868.60 |  |  |  |  | INR | 796,700.00 |  |  |  | INR | 1,313,399.00 |  |  |  |  | INR | 1,113,050.00 |  |  |  | INR | 1,517,607.50 |  |  |  |  | INR | 1,356,125.00
Vendor Status | [7 empty] | Round # : 1 (RFQ) | Round # : 1 (RFQ) | Round # : 2 (Auction) | Round # : 2 (Auction)
Sr No. | Vendor Code | Vendor Name | [5 empty] | Status | Remarks | Status | Remarks
1 | T051606 | SM Infra | [5 empty] | Participate |  | Participate
2 | RV232414136 | PIONEER PROJECT SOLUTION | [5 empty] | Participate |  | Participate
3 | RV232413816 | Pikture Perfect Design Studio Pvt. Ltd | [5 empty] | Participate |  | Participate
4 | RV232413533 | ANJLE MEP PROJECTS PVT LTD | [5 empty] | Participate |  | Participate

## BOQ Price Bid
|  | RFQ No: R0040 COST COMPARISON REPORT | RFQ No: R0040 COST COMPARISON REPORT | Comp. Date : 15/01/2024 | Comp. Date : 15/01/2024 | Comp. Date : 15/01/2024 | Vendor Name : PIONEER PROJECT SOLUTION | Vendor Name : PIONEER PROJECT SOLUTION | Vendor Name : ANJLE MEP PROJECTS PVT LTD | Vendor Name : ANJLE MEP PROJECTS PVT LTD | Vendor Name : Pikture Perfect Design Studio Pvt. Ltd | Vendor Name : Pikture Perfect Design Studio Pvt. Ltd
|  | RFQ No: R0040 COST COMPARISON REPORT | RFQ No: R0040 COST COMPARISON REPORT | RFQ #: R0040 | RFQ #: R0040 | RFQ #: R0040 | Contact Name : Mohd Ashraf | Contact Name : Mohd Ashraf | Contact Name : Priyanka/Premkant Rajpoot | Contact Name : Priyanka/Premkant Rajpoot | Contact Name : Gangadhar Sharma | Contact Name : Gangadhar Sharma
|  | RFQ No: R0040 COST COMPARISON REPORT | RFQ No: R0040 COST COMPARISON REPORT | RFQ Date : 13/01/2024 15:17:25 | RFQ Date : 13/01/2024 15:17:25 | RFQ Date : 13/01/2024 15:17:25 | Vendor City : | Vendor City : | Vendor City : | Vendor City : | Vendor City : | Vendor City :
|  | RFQ No: R0040 COST COMPARISON REPORT | RFQ No: R0040 COST COMPARISON REPORT | BCD Date : | BCD Date : | BCD Date : | Telephone # : | Telephone # : | Telephone # : | Telephone # : | Telephone # : | Telephone # :
|  | RFQ No: R0040 COST COMPARISON REPORT | RFQ No: R0040 COST COMPARISON REPORT |  |  |  | Mobile # : | Mobile # : | Mobile # : | Mobile # : | Mobile # : | Mobile # :
PR Number : TFSPL-2324-00102 | PR Number : TFSPL-2324-00102 | PR Number : TFSPL-2324-00102 | PR Number : TFSPL-2324-00102 | PR Number : TFSPL-2324-00102 | PR Number : TFSPL-2324-00102 | PR Number : TFSPL-2324-00102 | Email : projectspioneer@gmail.com | Email : projectspioneer@gmail.com | Email : anjlemepprojects@gmail.com | Email : anjlemepprojects@gmail.com | Email : piktureperfectdesignstudio@gmail.com | Email : piktureperfectdesignstudio@gmail.com
Package / RFQ Name : TFAS / RFQ / TFSPL-2324-00102 | Package / RFQ Name : TFAS / RFQ / TFSPL-2324-00102 | Package / RFQ Name : TFAS / RFQ / TFSPL-2324-00102 | Package / RFQ Name : TFAS / RFQ / TFSPL-2324-00102 | Package / RFQ Name : TFAS / RFQ / TFSPL-2324-00102 | Package / RFQ Name : TFAS / RFQ / TFSPL-2324-00102 | Package / RFQ Name : TFAS / RFQ / TFSPL-2324-00102 | Round # : 2 (Auction) | Round # : 2 (Auction) | Round # : 2 (Auction) | Round # : 2 (Auction) | Round # : 2 (Auction) | Round # : 2 (Auction)
Buyer : Jogeswar Sahu | Buyer : Jogeswar Sahu | Buyer : Jogeswar Sahu | Buyer : Jogeswar Sahu | Buyer : Jogeswar Sahu | Buyer : Jogeswar Sahu | Buyer : Jogeswar Sahu | Techanical Score : | Techanical Score : | Techanical Score : | Techanical Score : | Techanical Score : | Techanical Score :
Comp. # : 2 | Comp. # : 2 | Comp. # : 2 | Comp. # : 2 | Currency :INR | Currency :INR | Currency :INR | Quotation Date : | Quotation Date : | Quotation Date : | Quotation Date : | Quotation Date : | Quotation Date :
Comp. # : 2 | Comp. # : 2 | Comp. # : 2 | Comp. # : 2 | BUDGET PRICE :.00 | BUDGET PRICE :.00 | BUDGET PRICE :.00 | Quotation Validity Date : | Quotation Validity Date : | Quotation Validity Date : | Quotation Validity Date : | Quotation Validity Date : | Quotation Validity Date :
Sr No. | Item Code | Item Name | Item Description | UOM | Qty | Minimum Amount | Unit Price | Amount | Unit Price | Amount | Unit Price | Amount
1 |  | HVAC low side | BOQ for HVAC for Delhi T1 Taco Bell-Low Side | NOS | 1.000 |  |  | 402,770.00 |  | 477,550.00 |  | 897,125.00
1 | 1.1 | Chilled Water pipe | Chilled Water pipe
2 |  | Supply, installation, testing commissioning of chilled water pipes in MS class C construction complete with fittings, bends, elbows, unions supports, vibration isolators,sleeves as per specifications and drawings | Supply, installation, testing commissioning of chilled water pipes in MS class C construction complete with fittings, bends, elbows, unions supports, vibration isolators,sleeves as per specifications and drawings
3 | a | 100 mm dia. | 100 mm dia. | Rmt | 0.000 | .00 | 0.00 | .00 | 0.00 | .00 | 0.00 | .00
4 | b | 80 mm dia. | 80 mm dia. | Rmt | 0.000 | .00 | 0.00 | .00 | 0.00 | .00 | 0.00 | .00
5 | c | 65 mm dia. | 65 mm dia. | Rmt | 0.000 | .00 | 0.00 | .00 | 0.00 | .00 | 0.00 | .00
6 | d | 50 mm dia. | 50 mm dia. | Rmt | 0.000 | .00 | 1450.00 | .00 | 0.00 | .00 | 0.00 | .00
7 | e | 40 mm dia. | 40 mm dia. | Rmt | 0.000 | .00 | 0.00 | .00 | 0.00 | .00 | 0.00 | .00
8 | f | 32 mm dia. | 32 mm dia. | Rmt | 10.000 | 10,500.00 | 1050.00 | 10,500.00 | 1250.00 | 12,500.00 | 2150.00 | 21,500.00
9 | g | 25 mm dia. | 25 mm dia. | Rmt | 0.000 | .00 | 0.00 | .00 | 0.00 | .00 | 0.00 | .00
10 | 2.2 | Chilled Water pipe Insulation | Chilled Water pipe Insulation
11 |  | Providing and fixing insulation of 25 18 mm nitrile foam insullation with class O fire retardant propertiesby applying adhesive as per specifications and drawings. | Providing and fixing insulation of 25 18 mm nitrile foam insullation with class O fire retardant propertiesby applying adhesive as per specifications and drawings.
12 | a | 100 mm dia. | 100 mm dia. | Rmt | 0.000 | .00 | 0.00 | .00 | 0.00 | .00 | 0.00 | .00
13 | b | 80 mm dia. | 80 mm dia. | Rmt | 0.000 | .00 | 0.00 | .00 | 0.00 | .00 | 0.00 | .00
14 | c | 65 mm dia. | 65 mm dia. | Rmt | 0.000 | .00 | 0.00 | .00 | 0.00 | .00 | 0.00 | .00
15 | d | 50 mm dia. | 50 mm dia. | Rmt | 0.000 | .00 | 750.00 | .00 | 0.00 | .00 | 0.00 | .00
16 | e | 40 mm dia. | 40 mm dia. | Rmt | 0.000 | .00 | 0.00 | .00 | 0.00 | .00 | 0.00 | .00
17 | f | 32 mm dia. | 32 mm dia. | Rmt | 10.000 | 5,500.00 | 550.00 | 5,500.00 | 750.00 | 7,500.00 | 550.00 | 5,500.00
18 | g | 25 mm dia. | 25 mm dia. | Rmt | 0.000 | .00 | 0.00 | .00 | 0.00 | .00 | 0.00 | .00
19 | 3 | Butter Fly Valve | Butter Fly Valve
20 |  | Supply, installation, testing commissioning of following sizes of Butterfly valve with lug type construction, bolts, supports etc. The valves should be insulated by 18 mm nitrile foam by applying adhesive as per specifications. Valves should be sui | Supply, installation, testing commissioning of following sizes of Butterfly valve with lug type construction, bolts, supports etc. The valves should be insulated by 18 mm nitrile foam by applying adhesive as per specifications. Valves should be sui
21 | a | 80 mm dia. | 80 mm dia. | Nos. | 0.000 | .00 | 0.00 | .00 | 0.00 | .00 | 0.00 | .00
22 | b | 65 mm dia. | 65 mm dia. | Nos. | 0.000 | .00 | 0.00 | .00 | 0.00 | .00 | 0.00 | .00
23 | c | 50 mm dia. | 50 mm dia. | Nos. | 0.000 | .00 | 5500.00 | .00 | 0.00 | .00 | 0.00 | .00
24 | d | 40 mm dia. | 40 mm dia. | Nos. | 0.000 | .00 | 0.00 | .00 | 0.00 | .00 | 0.00 | .00
25 | e | 32 mm dia. | 32 mm dia. | Nos. | 0.000 | .00 | 0.00 | .00 | 0.00 | .00 | 0.00 | .00
26 | f | 25 mm dia. | 25 mm dia. | Nos. | 0.000 | .00 | 0.00 | .00 | 0.00 | .00 | 0.00 | .00
27 | 4 | Ball Valve | Ball Valve
28 |  | Supply, installation, testing commissioning of following sizes of Ball valve with lug type construction, bolts, supports etc. The valves should be insulated by 18 mm nitril foam by applying adhesive as per specifications. Valves should be suitabl | Supply, installation, testing commissioning of following sizes of Ball valve with lug type construction, bolts, supports etc. The valves should be insulated by 18 mm nitril foam by applying adhesive as per specifications. Valves should be suitabl
29 | e | 32 mm dia. | 32 mm dia. | Nos. | 2.000 | 4,600.00 | 4500.00 | 9,000.00 | 4250.00 | 8,500.00 | 2300.00 | 4,600.00
30 | f | 25 mm dia. | 25 mm dia. | Nos. | 0.000 | .00 | 0.00 | .00 | 0.00 | .00 | 0.00 | .00
31 | 5 | Balancing Valve | Balancing Valve
32 |  | Supply, installation, testing commissioning of following sizes of balancing valve with matching flanges, bolts, supports etc. The valves should be insulated by 18 mm nitril foam by applying adhesive as per specifications. Valves should be suitabl | Supply, installation, testing commissioning of following sizes of balancing valve with matching flanges, bolts, supports etc. The valves should be insulated by 18 mm nitril foam by applying adhesive as per specifications. Valves should be suitabl
33 | a | 80 mm dia. | 80 mm dia. | Nos. | 0.000 | .00 | 0.00 | .00 | 0.00 | .00 | 0.00 | .00
34 | b | 65 mm dia. | 65 mm dia. | Nos. | 0.000 | .00 | 0.00 | .00 | 0.00 | .00 | 0.00 | .00
35 | c | 50 mm dia. | 50 mm dia. | Nos. | 0.000 | .00 | 8500.00 | .00 | 0.00 | .00 | 0.00 | .00
36 | d | 40 mm dia. | 40 mm dia. | Nos. | 0.000 | .00 | 0.00 | .00 | 0.00 | .00 | 0.00 | .00
37 | e | 32 mm dia. | 32 mm dia. | Nos. | 1.000 | 6,500.00 | 6500.00 | 6,500.00 | 12500.00 | 12,500.00 | 48500.00 | 48,500.00
38 | f | 25 mm dia. | 25 mm dia. | Nos. | 0.000 | .00 | 0.00 | .00 | 0.00 | .00 | 0.00 | .00
39 | 6 | Two Way valve OR Three Way Valve | Two Way valve OR Three Way Valve
40 |  | Supply, installation, testing commissioning of following sizes of Two way Valve with matching flanges, bolts, supports etc. The valves should be insulated by making 24 G aluminium sheet box and filling loose TF thermocole applied as per specifications. | Supply, installation, testing commissioning of following sizes of Two way Valve with matching flanges, bolts, supports etc. The valves should be insulated by making 24 G aluminium sheet box and filling loose TF thermocole applied as per specifications.
41 | a | 80 mm dia. | 80 mm dia. | Nos. | 0.000 | .00 | 0.00 | .00 | 0.00 | .00 | 0.00 | .00
42 | b | 65 mm dia. | 65 mm dia. | Nos. | 0.000 | .00 | 0.00 | .00 | 0.00 | .00 | 0.00 | .00
43 | c | 50 mm dia. | 50 mm dia. | Nos. | 0.000 | .00 | 40500.00 | .00 | 0.00 | .00 | 0.00 | .00
44 | d | 40 mm dia. | 40 mm dia. | Nos. | 0.000 | .00 | 0.00 | .00 | 0.00 | .00 | 0.00 | .00
45 | e | 32 mm dia. | 32 mm dia. | Nos. | 1.000 | 16,500.00 | 30500.00 | 30,500.00 | 46500.00 | 46,500.00 | 16500.00 | 16,500.00
46 | f | 25 mm dia. | 25 mm dia. | Nos. | 0.000 | .00 | 0.00 | .00 | 0.00 | .00 | 0.00 | .00
47 | 7 | Y Stainer | Y Stainer
48 |  | Supply, installation, testing commissioning of following sizes of Y Stainer with matching flanges, bolts, supports etc. The valves should be insulated by making 24 G aluminium sheet box and filling loose TF thermocole applied as per specifications. | Supply, installation, testing commissioning of following sizes of Y Stainer with matching flanges, bolts, supports etc. The valves should be insulated by making 24 G aluminium sheet box and filling loose TF thermocole applied as per specifications.
49 | a | 80 mm dia. | 80 mm dia. | Nos. | 0.000 | .00 | 0.00 | .00 | 0.00 | .00 | 0.00 | .00
50 | b | 65 mm dia. | 65 mm dia. | Nos. | 0.000 | .00 | 0.00 | .00 | 0.00 | .00 | 0.00 | .00
51 | c | 50 mm dia. | 50 mm dia. | Nos. | 0.000 | .00 | 5500.00 | .00 | 0.00 | .00 | 0.00 | .00
52 | d | 40 mm dia. | 40 mm dia. | Nos. | 0.000 | .00 | 0.00 | .00 | 0.00 | .00 | 0.00 | .00
53 | e | 32 mm dia. | 32 mm dia. | Nos. | 1.000 | 3,200.00 | 4500.00 | 4,500.00 | 3850.00 | 3,850.00 | 3200.00 | 3,200.00
54 | f | 25 mm dia. | 25 mm dia. | Nos. | 0.000 | .00 | 0.00 | .00 | 0.00 | .00 | 0.00 | .00
55 | 8 | Auto Air vent valve | Auto Air vent valve
56 |  | Supply, installation, testing commissioning of following sizes of Auto Air Vent Valve | Supply, installation, testing commissioning of following sizes of Auto Air Vent Valve
57 | a | 3/4 Ball valves for vent / Purge in each risers common headers | 3/4 Ball valves for vent / Purge in each risers common headers | Nos. | 1.000 | 1,850.00 | 2200.00 | 2,200.00 | 2450.00 | 2,450.00 | 1850.00 | 1,850.00
58 | 9 | Pressure Guage/Thermometer | Pressure Guage/Thermometer
59 |  | Supply, installation, testing commissioning of following guages as per drawing | Supply, installation, testing commissioning of following guages as per drawing
60 | a | Pressure gauge with gauge cock, thermowell | Pressure gauge with gauge cock, thermowell | Nos. | 1.000 | 1,650.00 | 2250.00 | 2,250.00 | 1650.00 | 1,650.00 | 3950.00 | 3,950.00
61 | b | Thermometers (Mercury filled V form type) | Thermometers (Mercury filled V form type) | Nos. | 1.000 | 1,450.00 | 1450.00 | 1,450.00 | 2450.00 | 2,450.00 | 2200.00 | 2,200.00
62 | 10 | Drain Valves | Drain Valves
63 | a | 25mm dia | 25mm dia | Nos. | 2.000 | 3,300.00 | 1650.00 | 3,300.00 | 2150.00 | 4,300.00 | 2350.00 | 4,700.00
64 | b | 40mm dia | 40mm dia | Nos. | 0.000 | .00 | 0.00 | .00 | 0.00 | .00 | 0.00 | .00
65 | 11 | Drain Piping; | Drain Piping;
66 |  | Supply, installation, testing commissioning of following sizes insulated CPVC drain pipes from AHU drain pans to nearest floor drain and from CHW pump glands to the nearest drain complete with interconnection, flanges, elbows, tees, nuts, P-trap etc. Th | Supply, installation, testing commissioning of following sizes insulated CPVC drain pipes from AHU drain pans to nearest floor drain and from CHW pump glands to the nearest drain complete with interconnection, flanges, elbows, tees, nuts, P-trap etc. Th
67 | a | 65mm dia. | 65mm dia. | Rmt | 0.000 | .00 | 0.00 | .00 | 0.00 | .00 | 0.00 | .00
68 | b | 50mm dia. | 50mm dia. | Rmt | 2.000 | 560.00 | 280.00 | 560.00 | 750.00 | 1,500.00 | 950.00 | 1,900.00
69 | c | 40mm dia. | 40mm dia. | Rmt | 8.000 | 1,760.00 | 220.00 | 1,760.00 | 650.00 | 5,200.00 | 750.00 | 6,000.00
70 | d | 32mm dia. | 32mm dia. | Rmt | 0.000 | .00 | 0.00 | .00 | 0.00 | .00 | 0.00 | .00
71 | e | 25mm dia. | 25mm dia. | Rmt | 0.000 | .00 | 0.00 | .00 | 0.00 | .00 | 0.00 | .00
72 | 12 | AIR DISTRIBUTION SYSTEM | AIR DISTRIBUTION SYSTEM
73 | 12.1 | GI sheet metal rectangular duct | GI sheet metal rectangular duct
74 |  | Supply, Fabrication, Installation, Testing Commissioning of following gauges of ducting complete with splitters, supports, dampers, and turning vanes as per specification and HVAC lay out. Aproved Makes JINDAL, TATA, SAIL, Equivalent. All exposed ducts | Supply, Fabrication, Installation, Testing Commissioning of following gauges of ducting complete with splitters, supports, dampers, and turning vanes as per specification and HVAC lay out. Aproved Makes JINDAL, TATA, SAIL, Equivalent. All exposed ducts
75 | a | 24 gauge ducting - 0.63 mm thickness (upto - 750mm) | 24 gauge ducting - 0.63 mm thickness (upto - 750mm) | Sq. mt | 55.000 | 68,750.00 | 1250.00 | 68,750.00 | 1350.00 | 74,250.00 | 1250.00 | 68,750.00
76 | b | 22 gauge ducting - 0.80 mm thickness (751 - 1500) | 22 gauge ducting - 0.80 mm thickness (751 - 1500) | Sq. mt | 45.000 | 65,250.00 | 1450.00 | 65,250.00 | 1450.00 | 65,250.00 | 1550.00 | 69,750.00
77 | c | 20 gauge ducting - 1.00 mm thickness (1501 - 2250) | 20 gauge ducting - 1.00 mm thickness (1501 - 2250) | Sq. mt | 5.000 | 8,250.00 | 1650.00 | 8,250.00 | 1650.00 | 8,250.00 | 1850.00 | 9,250.00
78 | d | 18 gauge ducting - 1.20 mm thickness (2251-2500 plenum) | 18 gauge ducting - 1.20 mm thickness (2251-2500 plenum) | Sq. mt | 0.000 | .00 | 0.00 | .00 | 0.00 | .00 | 0.00 | .00
79 | 12.2 | GI sheet metal elpitical duct | GI sheet metal elpitical duct
80 |  | Supply, Fabrication, Installation, Testing Commissioning of following gauges of ducting complete with splitters, supports, dampers, and turning vanes as per specification and HVAC lay out. Aproved Makes JINDAL, TATA, SAIL, Equivalent. All exposed ducts | Supply, Fabrication, Installation, Testing Commissioning of following gauges of ducting complete with splitters, supports, dampers, and turning vanes as per specification and HVAC lay out. Aproved Makes JINDAL, TATA, SAIL, Equivalent. All exposed ducts
81 | a | 24 gauge ducting - 0.63 mm thickness (upto - 750mm) | 24 gauge ducting - 0.63 mm thickness (upto - 750mm) | Sq. mt | 0.000 | .00 | 0.00 | .00 | 0.00 | .00 | 0.00 | .00
82 | b | 22 gauge ducting - 0.80 mm thickness (751 - 1500) | 22 gauge ducting - 0.80 mm thickness (751 - 1500) | Sq. mt | 0.000 | .00 | 0.00 | .00 | 0.00 | .00 | 0.00 | .00
83 | c | 20 gauge ducting - 1.00 mm thickness (1501 - 2250) | 20 gauge ducting - 1.00 mm thickness (1501 - 2250) | Sq. mt | 0.000 | .00 | 0.00 | .00 | 0.00 | .00 | 0.00 | .00
84 | d | 18 gauge ducting - 1.20 mm thickness (2251-2500 plenum) | 18 gauge ducting - 1.20 mm thickness (2251-2500 plenum) | Sq. mt | 0.000 | .00 | 0.00 | .00 | 0.00 | .00 | 0.00 | .00
85 | 12.3 | MS sheet metal rectangular duct | MS sheet metal rectangular duct
86 |  | Supply, Fabrication, Installation, Testing Commissioning of following gauges of ducting complete with splitters, supports, dampers, and turning vanes as per specification and HVAC lay out. Aproved Makes JINDAL, TATA, SAIL, Equivalent. All exposed ducts | Supply, Fabrication, Installation, Testing Commissioning of following gauges of ducting complete with splitters, supports, dampers, and turning vanes as per specification and HVAC lay out. Aproved Makes JINDAL, TATA, SAIL, Equivalent. All exposed ducts
87 | a | 16 gauge MS ducting - | 16 gauge MS ducting - | Sq. mt | 0.000 | .00 | 0.00 | .00 | 0.00 | .00 | 0.00 | .00
88 | 14 | Accoustic Insulation | Accoustic Insulation
89 |  | Accoustic lining of duct work with following thicknesss closed cell nitrile rubber- Makes A Flex, K Flex. | Accoustic lining of duct work with following thicknesss closed cell nitrile rubber- Makes A Flex, K Flex.
90 |  | 15mm Thick | 15mm Thick | Sq. mt | 0.000 | .00 | 0.00 | .00 | 0.00 | .00 | 0.00 | .00
91 |  | 25mm Thick | 25mm Thick | Sq. mt | 7.000 | 10,150.00 | 1550.00 | 10,850.00 | 1450.00 | 10,150.00 | 1850.00 | 12,950.00
92 | 15 | Thermal insulation Nitrile rubber Insulation ( Supply air ) | Thermal insulation Nitrile rubber Insulation ( Supply air )
93 |  | Providing and fixing nitrile rubber insulation with class O fire retardant properties by applying adhesive outside the ducts complete as per specifications and drawings.Make-K Flex, A Flex - Insulation exposed to ambient shall be covered with glass clot | Providing and fixing nitrile rubber insulation with class O fire retardant properties by applying adhesive outside the ducts complete as per specifications and drawings.Make-K Flex, A Flex - Insulation exposed to ambient shall be covered with glass clot
94 | a | 25 mm thick | 25 mm thick | Sq. mt | 0.000 | .00 | 0.00 | .00 | 0.00 | .00 | 0.00 | .00
95 | b | 19 mm thick | 19 mm thick | Sq. mt | 0.000 | .00 | 750.00 | .00 | 0.00 | .00 | 0.00 | .00
96 | c | 13 mm thick | 13 mm thick | Sq. mt | 48.000 | 31,200.00 | 650.00 | 31,200.00 | 850.00 | 40,800.00 | 1650.00 | 79,200.00
97 | d | 9mm thick | 9mm thick | Sq. mt | 0.000 | .00 | 0.00 | .00 | 0.00 | .00 | 0.00 | .00
98 | e | 6mm thick | 6mm thick | Sq. mt | 0.000 | .00 | 0.00 | .00 | 0.00 | .00 | 0.00 | .00
99 | 16 | Thermal Exhaust Duct Insulation ( Only in BOH ) | Thermal Exhaust Duct Insulation ( Only in BOH )
100 |  | Exhaust Air Duct insulation with 1325mm thick heatlon insulation within store. No insulation for duct outside store. Insulation exposed to ambient shall be covered with glass cloth UV protection paint. | Exhaust Air Duct insulation with 1325mm thick heatlon insulation within store. No insulation for duct outside store. Insulation exposed to ambient shall be covered with glass cloth UV protection paint. | Sq. mt | 42.000 | 44,100.00 | 1050.00 | 44,100.00 | 1250.00 | 52,500.00 | 1550.00 | 65,100.00
101 | 17 | Thermal insulation- (Out side Building for Air washer) | Thermal insulation- (Out side Building for Air washer)
102 |  | Providing and fixing of 9mm thick nitrial rubber by applying adhesive inside the ducts c. (9mm thick) | Providing and fixing of 9mm thick nitrial rubber by applying adhesive inside the ducts c. (9mm thick) | Sq. mt | 0.000 | .00 | 0.00 | .00 | 0.00 | .00 | 0.00 | .00
103 | 18 | Under Deck Insulation | Under Deck Insulation
104 | a | Under deck insulation for exporsed concrete slab using 19mm thick nitrile rubber insulation with class O fire retardant properties as per the specifications and drawings. Adhesive used shall be Low VOC type. Insulation to be mechanically fasteed using | Under deck insulation for exporsed concrete slab using 19mm thick nitrile rubber insulation with class O fire retardant properties as per the specifications and drawings. Adhesive used shall be Low VOC type. Insulation to be mechanically fasteed using | Sq. mt | 0.000 | .00 | 0.00 | .00 | 0.00 | .00 | 0.00 | .00
105 | 19 | Continous / Linear Grilles | Continous / Linear Grilles
106 |  | Extruded Aluminium Powder Coated Continous / Linear Grilles Of Required Airflow Angles with required damper at collar , with four side flanges as per requirements. (Make - AIRVISION/COSMOS) - Quoted Mahadi | Extruded Aluminium Powder Coated Continous / Linear Grilles Of Required Airflow Angles with required damper at collar , with four side flanges as per requirements. (Make - AIRVISION/COSMOS) - Quoted Mahadi
107 | a | 4 Width | 4 Width | Rmt | 0.000 | .00 | 0.00 | .00 | 0.00 | .00 | 0.00 | .00
108 | b | 6 Width | 6 Width | Rmt | 5.000 | 7,250.00 | 2200.00 | 11,000.00 | 1450.00 | 7,250.00 | 2850.00 | 14,250.00
109 | c | 8 Width | 8 Width | Rmt | 0.000 | .00 | 0.00 | .00 | 0.00 | .00 | 0.00 | .00
110 | d | 10 Width | 10 Width | Rmt | 0.000 | .00 | 0.00 | .00 | 0.00 | .00 | 0.00 | .00
111 | g | Rount double louvered grill with damper for elipitical duct | Rount double louvered grill with damper for elipitical duct
112 |  | 24 X6 | 24 X6 | Nos | 0.000 | .00 | 0.00 | .00 | 0.00 | .00 | 0.00 | .00
113 |  | 22 X4 | 22 X4 | Nos | 0.000 | .00 | 0.00 | .00 | 0.00 | .00 | 0.00 | .00
114 |  | 18 X6 | 18 X6 | Nos | 0.000 | .00 | 0.00 | .00 | 0.00 | .00 | 0.00 | .00
115 |  | 48 X4 | 48 X4 | Nos | 0.000 | .00 | 0.00 | .00 | 0.00 | .00 | 0.00 | .00
116 | 20 | Supply Air Square Grille | Supply Air Square Grille
117 |  | Supply, installation of aluminium extruded powdercoated supply air square grilles with four side flanges (0 degree deflection), with aluminium powder coated, multiple flape type with dampers.(Kitchen Area) | Supply, installation of aluminium extruded powdercoated supply air square grilles with four side flanges (0 degree deflection), with aluminium powder coated, multiple flape type with dampers.(Kitchen Area)
118 | a | Neck Size - 18 x 18 (Outer Size - 24 x 24 ) | Neck Size - 18 x 18 (Outer Size - 24 x 24 ) | Nos. | 0.000 | .00 | 0.00 | .00 | 0.00 | .00 | 0.00 | .00
119 | b | Neck Size - 15 x 15 (Outer Size - 24 x 24 ) | Neck Size - 15 x 15 (Outer Size - 24 x 24 ) | Nos. | 0.000 | .00 | 0.00 | .00 | 0.00 | .00 | 0.00 | .00
120 | c | Neck Size - 12 x 12 (Outer Size - 24 x 24 ) | Neck Size - 12 x 12 (Outer Size - 24 x 24 ) | Nos. | 0.000 | .00 | 0.00 | .00 | 0.00 | .00 | 0.00 | .00
121 | d | Neck Size - 9 x 9 (Outer Size - 24 x 24 ) Double deflection grille | Neck Size - 9 x 9 (Outer Size - 24 x 24 ) Double deflection grille | Nos. | 0.000 | .00 | 0.00 | .00 | 0.00 | .00 | 0.00 | .00
122 | 21 | Return Air Square Grille | Return Air Square Grille
123 |  | Return air square grills without damper shall be four side flanges with active sizes as given below. | Return air square grills without damper shall be four side flanges with active sizes as given below.
124 | a | Outer Size - 24 x 24 | Outer Size - 24 x 24 | Nos. | 4.000 | 8,000.00 | 2000.00 | 8,000.00 | 2650.00 | 10,600.00 | 9500.00 | 38,000.00
125 | b | Outer Size - 12 x 12 | Outer Size - 12 x 12 | Nos. | 0.000 | .00 | 0.00 | .00 | 0.00 | .00 | 0.00 | .00
126 | c | Outer Size - 36 x 14 | Outer Size - 36 x 14 | Nos. | 0.000 | .00 | 0.00 | .00 | 0.00 | .00 | 0.00 | .00
127 | d | 16 x 16 | 16 x 16 | Nos. | 0.000 | .00 | 0.00 | .00 | 0.00 | .00 | 0.00 | .00
128 | e | 8 x 8 | 8 x 8 | Nos. | 0.000 | .00 | 0.00 | .00 | 0.00 | .00 | 0.00 | .00
129 | f | 6 x 6 | 6 x 6 | Nos. | 0.000 | .00 | 0.00 | .00 | 0.00 | .00 | 0.00 | .00
130 | 22 | Supply Air Diffuser (Diffuser to be mounted on collar with damper) | Supply Air Diffuser (Diffuser to be mounted on collar with damper)
131 |  | Supply, installation of aluminium extruded powdercoated four way square diffuser with damper. Make-AIRVISION/COSMOS | Supply, installation of aluminium extruded powdercoated four way square diffuser with damper. Make-AIRVISION/COSMOS
132 | a | Neck Size - 18 x 18 (Outer Size - 24 x 24 ) | Neck Size - 18 x 18 (Outer Size - 24 x 24 ) | Nos. | 12.000 | 12,600.00 | 1050.00 | 12,600.00 | 2850.00 | 34,200.00 | 12500.00 | 150,000.00
133 | b | Neck Size - 15 x 15 (Outer Size - 24 x 24 ) | Neck Size - 15 x 15 (Outer Size - 24 x 24 ) | Nos. | 0.000 | .00 | 0.00 | .00 | 0.00 | .00 | 0.00 | .00
134 | 23 | Supply Return Air Diffuser (Diffuser to be mounted on collar with damper) | Supply Return Air Diffuser (Diffuser to be mounted on collar with damper)
135 |  | Supply, installation of aluminium extruded powdercoated four way square diffuser without damper. Make-AIRVISION/COSMOS | Supply, installation of aluminium extruded powdercoated four way square diffuser without damper. Make-AIRVISION/COSMOS
136 | a | Outer Size - 24 x 24 | Outer Size - 24 x 24 | Nos. | 11.000 | 22,000.00 | 2000.00 | 22,000.00 | 2450.00 | 26,950.00 | 9500.00 | 104,500.00
137 | b | Outer Size - 12 x 12 | Outer Size - 12 x 12 | Nos. | 0.000 | .00 | 0.00 | .00 | 0.00 | .00 | 0.00 | .00
138 | c | Outer Size - 8 x 8 | Outer Size - 8 x 8 | Nos. | 0.000 | .00 | 0.00 | .00 | 0.00 | .00 | 0.00 | .00
139 | 24 | Canvass Connection | Canvass Connection
140 | a | Installation of Double Canvass connection for all air outlet / inlet, Fire retardant type with GI flanges for Units. | Installation of Double Canvass connection for all air outlet / inlet, Fire retardant type with GI flanges for Units. | Nos. | 3.000 | 7,950.00 | 3000.00 | 9,000.00 | 2650.00 | 7,950.00 | 4500.00 | 13,500.00
141 | b | Installation of Double Canvass connection for Inline Toilet Exhaust Fan. | Installation of Double Canvass connection for Inline Toilet Exhaust Fan. | Nos. | 0.000 | .00 | 0.00 | .00 | 0.00 | .00 | 0.00 | .00
142 | 25 | Volume Control Damper | Volume Control Damper
143 |  | Supply Installation of volume control damper on AHU mouth y piece. | Supply Installation of volume control damper on AHU mouth y piece. | Sq. mt | 2.000 | 16,500.00 | 8500.00 | 17,000.00 | 8250.00 | 16,500.00 | 8750.00 | 17,500.00
144 | 26 | Collar Damper | Collar Damper
145 | a | Supply Installation of Collar Damper on AHU mouth y piece. | Supply Installation of Collar Damper on AHU mouth y piece. | Sq.mt | 1.000 | 4,250.00 | 5500.00 | 5,500.00 | 4250.00 | 4,250.00 | 11500.00 | 11,500.00
146 | 27 | Flexible Duct | Flexible Duct
147 |  | Supply, installation, testing commissioning of Flexible Ducts of following sizes comprising of inner as well as outer skin constructed out of aluminium | Supply, installation, testing commissioning of Flexible Ducts of following sizes comprising of inner as well as outer skin constructed out of aluminium
148 | a | 250 mm Dia | 250 mm Dia | Rmt | 0.000 | .00 | 0.00 | .00 | 0.00 | .00 | 0.00 | .00
149 | b | 200 mm Dia | 200 mm Dia | Rmt | 0.000 | .00 | 0.00 | .00 | 0.00 | .00 | 0.00 | .00
150 | c | 150 mm Dia | 150 mm Dia | Rmt | 0.000 | .00 | 0.00 | .00 | 0.00 | .00 | 0.00 | .00
151 | 28 | Gas | Gas
152 | a | R22 | R22 | KG | 0.000 | .00 | 0.00 | .00 | 0.00 | .00 | 0.00 | .00
153 | b | R32/R407C/R410A | R32/R407C/R410A | KG | 0.000 | .00 | 0.00 | .00 | 0.00 | .00 | 0.00 | .00
154 | 29 | Misc. item | Misc. item
155 | a | Hood Installation | Hood Installation | Nos | 0.000 | .00 | 0.00 | .00 | 0.00 | .00 | 0.00 | .00
156 | b | Scaffolding | Scaffolding | sqft | 0.000 | .00 | 0.00 | .00 | 0.00 | .00 | 0.00 | .00
157 | c | Catwalk | Catwalk | kg | 0.000 | .00 | 0.00 | .00 | 0.00 | .00 | 0.00 | .00
158 | d | DOL Starter Panel upto 7.5 HP with Cabling | DOL Starter Panel upto 7.5 HP with Cabling | Nos | 0.000 | .00 | 0.00 | .00 | 0.00 | .00 | 0.00 | .00
159 | e | Star delta panel above 7.5 HP | Star delta panel above 7.5 HP | Nos | 0.000 | .00 | 0.00 | .00 | 0.00 | .00 | 0.00 | .00
160 | f | Cable Tray 300mm width | Cable Tray 300mm width | Rmt | 15.000 | 9,750.00 | 750.00 | 11,250.00 | 650.00 | 9,750.00 | 1050.00 | 15,750.00
161 | 30 | Supply, Installation, Testing and Commissioning of motorised fire dampers suitable for at least 120 minutes fire rating as per the specifications and approved shop drawings. Quoted price shall be inclusive of copper control wiring as required. | Supply, Installation, Testing and Commissioning of motorised fire dampers suitable for at least 120 minutes fire rating as per the specifications and approved shop drawings. Quoted price shall be inclusive of copper control wiring as required.
162 | a. | Bare Fire Dampers | Bare Fire Dampers | SqM | 0.000 | .00 | 0.00 | .00 | 0.00 | .00 | 0.00 | .00
163 | b. | Spring return action type actuator complete with | Spring return action type actuator complete with
164 |  | control panel and temperature sensor. Torque not less | control panel and temperature sensor. Torque not less | No | 0.000 | .00 | 0.00 | .00 | 0.00 | .00 | 0.00 | .00
165 |  | than 16NM | than 16NM
166 |  | Sub total | Sub total
167 |  | GST extra as applicable | GST extra as applicable
168 |  | All the chasing works in wall supporting the HVAC system shall be in HVAC contractor scope only. | All the chasing works in wall supporting the HVAC system shall be in HVAC contractor scope only.
169 |  | Chilled Water Piping - | Chilled Water Piping -
170 |  | Chilled water piping shall be confirming to IS 1239 Part I class ‘C’ heavy and fitting shall be conforming to ASTM A-105,3000lbs socket weld end (up to 50mm) 1S 1239 Part-II HEAVY/ASTM A-234 WPB, Gr.B butt weld fitting ( above 50nb pipe size) | Chilled water piping shall be confirming to IS 1239 Part I class ‘C’ heavy and fitting shall be conforming to ASTM A-105,3000lbs socket weld end (up to 50mm) 1S 1239 Part-II HEAVY/ASTM A-234 WPB, Gr.B butt weld fitting ( above 50nb pipe size)
171 |  | Piping connection should be socket welded up to 50nb size and shall be butt weld above 50nb pipe size. Pipe flanges should be confirming to ASTM A-105 # 150 SORF and flange dimension should be in accordance with ASME/ANSI B 16.5 (150 SORF), fitting to fit | Piping connection should be socket welded up to 50nb size and shall be butt weld above 50nb pipe size. Pipe flanges should be confirming to ASTM A-105 # 150 SORF and flange dimension should be in accordance with ASME/ANSI B 16.5 (150 SORF), fitting to fit
172 |  | Post installation clearance by DIAL, CHW piping shall be tested @15kgf/cm2 hydrostatics pressure for 24hrs hold time and Testing should be witnessed to DIAL Team. | Post installation clearance by DIAL, CHW piping shall be tested @15kgf/cm2 hydrostatics pressure for 24hrs hold time and Testing should be witnessed to DIAL Team.
173 |  | Thermal insulation on CHW and condensate drain piping line shall be 25mm thick. Closed cell antimicrobial Class “O” BS 476 and part 6 7 FM approved nitrile rubberelastomeric insulation thermal conductivity 0.033watts per meter-lvin(W/(M·K)) at 0°C. | Thermal insulation on CHW and condensate drain piping line shall be 25mm thick. Closed cell antimicrobial Class “O” BS 476 and part 6 7 FM approved nitrile rubberelastomeric insulation thermal conductivity 0.033watts per meter-lvin(W/(M·K)) at 0°C.
174 |  | Condensate drain piping shall be complying to IS 4985 Class 3 UPVC pipe. Solvent cement complying with ASTM D2564 shall be used for joints. | Condensate drain piping shall be complying to IS 4985 Class 3 UPVC pipe. Solvent cement complying with ASTM D2564 shall be used for joints.
175 |  | For ceiling suspended chilled water pipe Pipe should be hanged with tie rod of size minimum 10 mm dia. | For ceiling suspended chilled water pipe Pipe should be hanged with tie rod of size minimum 10 mm dia.
2 |  | HVAC High Side | BOQ for HVAC High Side | NOS | 1.000 |  |  | 470,000.00 |  | 635,500.00 |  | 459,000.00
176 | 1.1 | Fresh Air Unit - 2500 CFM Supply Installation of the following cabinet type Fresh Air Fans with Forward curved inclined type heavy duty DIDW centrifugal fan with 3 phase TEFC with IP55 protection class F insulation, Double skin construction complete with Filters, adjusting brackets, twin V drive belt , vibration spring isolators, canvas connection and epoxy painted all as per specs. (Fan Make Kruger/Nicotra. Motor Crompton/Havells/BB )Static Pressure 65 mm | Fresh Air Unit - 2500 CFM Supply Installation of the following cabinet type Fresh Air Fans with Forward curved inclined type heavy duty DIDW centrifugal fan with 3 phase TEFC with IP55 protection class F insulation, Double skin construction complete with Filters, adjusting brackets, twin V drive belt , vibration spring isolators, canvas connection and epoxy painted all as per specs. (Fan Make Kruger/Nicotra. Motor Crompton/Havells/BB )Static Pressure 65 mm | Nos | 1.000 | 99,000.00 | 145000.00 | 145,000.00 | 175000.00 | 175,000.00 | 99000.00 | 99,000.00
177 | 1.2 | Dry Scrubber - 3500 CFM Supply installation of DRY scrubber each comprising of extract air intake section, electrostatic precipitation technology, dry type air cleaner to remove oil, smoke and fumes from exhaust air. Electrostatic section shall be made of 16 gauge galvanized sheet, high bake epoxy powder coated, washable type even air flow distribution plate, stainless steel spiked ionizers to create high voltage DC field, honey comb patented cylindrical structure filter cell which should be alternatively charged positive and negative with large collecting area , to work as magnet for charged smoke and oil particles. Average efficiency of 90-95% in single pass as per ASHRAE test method. Electrostatic Precipitator should be able to charge particles from 0.01 micron to 10 microns through solid state power supply. Collector cell should be of permanent type and incorporate slide out facility for easy removal for cleaning. Power supplies shall be 100% solid state UL Listed, Module of capacity below shall be equipped with multiple protection functions for power and overload and overheating with interlock switch for safety as per approved specification and drawings ) (Air Moving Capacities are - 8000 cfm 90 mmwg S.P.)Make -Rydair, Trion | Dry Scrubber - 3500 CFM Supply installation of DRY scrubber each comprising of extract air intake section, electrostatic precipitation technology, dry type air cleaner to remove oil, smoke and fumes from exhaust air. Electrostatic section shall be made of 16 gauge galvanized sheet, high bake epoxy powder coated, washable type even air flow distribution plate, stainless steel spiked ionizers to create high voltage DC field, honey comb patented cylindrical structure filter cell which should be alternatively charged positive and negative with large collecting area , to work as magnet for charged smoke and oil particles. Average efficiency of 90-95% in single pass as per ASHRAE test method. Electrostatic Precipitator should be able to charge particles from 0.01 micron to 10 microns through solid state power supply. Collector cell should be of permanent type and incorporate slide out facility for easy removal for cleaning. Power supplies shall be 100% solid state UL Listed, Module of capacity below shall be equipped with multiple protection functions for power and overload and overheating with interlock switch for safety as per approved specification and drawings ) (Air Moving Capacities are - 8000 cfm 90 mmwg S.P.)Make -Rydair, Trion | Nos | 1.000 | 185,000.00 | 185000.00 | 185,000.00 | 275000.00 | 275,000.00 | 285000.00 | 285,000.00
178 | 1.3 | Air Washer Unit - 2500 CFM Supply Installation of double skin construction packaged type air washer unit comprising of fan section with floor standing DIDW centrifugal fan, TEFC squirrel cage,induction motor of IP 55 protection,multi sheave pulley mounted on motor,Twin belt drive package wetting Pad section complete with 200 mm Thick Cellulose based Paper Fills with Drop-Stop eliminators,water distribution System complete with FRP Spray Headers,Float Valve,quick fill,Overflow,water circulation pump, tank,drain connection along with GI B class/PVC piping,strainers,fittings,base frame vibration isolators etc.Filter sections shall be complete with 50 mm Thick Aluminum Wire mesh Viscous metallic Filters.The fan section shall be fabricated out of 16 GaugeG.S.Sheet complete with inspection door.Wet section of Air Washer including sump shall be made out of 1.25 mm Thich SS 304 Stainless Steel sheet.(The blower motor shall be sutable for operation on 415+_10 %V,50 Hz,3 phase power supply) etc.The Air washer shall be as per specifications of following characteristics - ( Fan Make Kruger/Nicotra. Motor Crompton/Havells/BB ). | Air Washer Unit - 2500 CFM Supply Installation of double skin construction packaged type air washer unit comprising of fan section with floor standing DIDW centrifugal fan, TEFC squirrel cage,induction motor of IP 55 protection,multi sheave pulley mounted on motor,Twin belt drive package wetting Pad section complete with 200 mm Thick Cellulose based Paper Fills with Drop-Stop eliminators,water distribution System complete with FRP Spray Headers,Float Valve,quick fill,Overflow,water circulation pump, tank,drain connection along with GI B class/PVC piping,strainers,fittings,base frame vibration isolators etc.Filter sections shall be complete with 50 mm Thick Aluminum Wire mesh Viscous metallic Filters.The fan section shall be fabricated out of 16 GaugeG.S.Sheet complete with inspection door.Wet section of Air Washer including sump shall be made out of 1.25 mm Thich SS 304 Stainless Steel sheet.(The blower motor shall be sutable for operation on 415+_10 %V,50 Hz,3 phase power supply) etc.The Air washer shall be as per specifications of following characteristics - ( Fan Make Kruger/Nicotra. Motor Crompton/Havells/BB ).
179 | 1.4 | Exhaust Air Unit - 3500 CFM Supply Installation of Floor Mounted type Cabinate type Exhaust Centrifugal backward inclined DIDW blower with suitable high static pressure to create the required intake velocities and over come the pressure loss at the inlet of filters and ducts. DIDW Centrifugal blower. (Motor outside the effluent air stream.) backward inclined, non over loading type. ( smaller motor) mounted directly on motor shaft twin belt drive system. (slip losses and lesser maintenance) Dynamically balanced to provide a vibration free operation.Fan to be direct driven to motor. Multiblade box type zero leakage manually operated extruded aluminium volume control dampers shall be factory fitted at outlet of Exhaust Fan.Static Pressure 80 mm , Make -Kruger/Greenheck/System Air/Wolter/ Caryaire/ Nicotra | Exhaust Air Unit - 3500 CFM Supply Installation of Floor Mounted type Cabinate type Exhaust Centrifugal backward inclined DIDW blower with suitable high static pressure to create the required intake velocities and over come the pressure loss at the inlet of filters and ducts. DIDW Centrifugal blower. (Motor outside the effluent air stream.) backward inclined, non over loading type. ( smaller motor) mounted directly on motor shaft twin belt drive system. (slip losses and lesser maintenance) Dynamically balanced to provide a vibration free operation.Fan to be direct driven to motor. Multiblade box type zero leakage manually operated extruded aluminium volume control dampers shall be factory fitted at outlet of Exhaust Fan.Static Pressure 80 mm , Make -Kruger/Greenheck/System Air/Wolter/ Caryaire/ Nicotra | Nos | 1.000 | 75,000.00 | 140000.00 | 140,000.00 | 185500.00 | 185,500.00 | 75000.00 | 75,000.00
180 | 1.5 | Ceiling Suspended Air Handling Units 5000 CFM, 9.5 TR Supply Installation of double skin ceiling suspended air handling units complete with 25mm thick insulated panels, forward curved DIDW Blower, cooling coil section with 6 Row DX CHW coil (coil Thickness -0.5mm), filter section with filters (EU-4), fan motor, drive set with double belt, mounting base damper etc.as per specifications and drawings. AHU shall have DOL Starter panel within 7.0 KW and above 7.0 KW star delte starter to be used. Motor should be IP 55 TEFC. ( Fan Make Kruger/Nicotra ). Coil temperature should be 12 deg C. AHU should be complete with filter frame with filter. Static Pressure 35mm AHUs shall be provided with Thermal Break Profile. a) Fan Outlet Velocity should not exceed 1800 FPM b) Coil face velocity should no exceed 500 FPM c) Filter velocity should not exceed 500 FPM | Ceiling Suspended Air Handling Units 5000 CFM, 9.5 TR Supply Installation of double skin ceiling suspended air handling units complete with 25mm thick insulated panels, forward curved DIDW Blower, cooling coil section with 6 Row DX CHW coil (coil Thickness -0.5mm), filter section with filters (EU-4), fan motor, drive set with double belt, mounting base damper etc.as per specifications and drawings. AHU shall have DOL Starter panel within 7.0 KW and above 7.0 KW star delte starter to be used. Motor should be IP 55 TEFC. ( Fan Make Kruger/Nicotra ). Coil temperature should be 12 deg C. AHU should be complete with filter frame with filter. Static Pressure 35mm AHUs shall be provided with Thermal Break Profile. a) Fan Outlet Velocity should not exceed 1800 FPM b) Coil face velocity should no exceed 500 FPM c) Filter velocity should not exceed 500 FPM
181 |  | Notes | Notes
182 |  | HVAC load 5000CFM/8.3TR (with VFD integration) has been approved | HVAC load 5000CFM/8.3TR (with VFD integration) has been approved
183 |  | Kitchen ventilation shall comply to NFPA 96 guideline. | Kitchen ventilation shall comply to NFPA 96 guideline.
184 |  | Section drawing needs to be facilitated for condensate line for prior approval before execution at site. | Section drawing needs to be facilitated for condensate line for prior approval before execution at site.
185 |  | Makeup / exhaust air equipment detail needs to be facilitated for prior approval from DIAL. | Makeup / exhaust air equipment detail needs to be facilitated for prior approval from DIAL.
186 |  | TDS Test certificate for complete HVAC system to be shared for prior approval from DIAL. | TDS Test certificate for complete HVAC system to be shared for prior approval from DIAL.
187 |  | Structural details for equipment placement to be approved by structural consultant (as per permissible load capacity mentioned in the design guideline) and all details to be shared with DIAL for prior approval from DIAL. | Structural details for equipment placement to be approved by structural consultant (as per permissible load capacity mentioned in the design guideline) and all details to be shared with DIAL for prior approval from DIAL.

## Technical Score Detail
|  | RFQ No: R0040 COST COMPARISON REPORT | RFQ No: R0040 COST COMPARISON REPORT | RFQ No: R0040 COST COMPARISON REPORT | Comp. Date : 15/01/2024 | Comp. Date : 15/01/2024 | Comp. Date : 15/01/2024 | Vendor Name : PIONEER PROJECT SOLUTION |  |  |  | Vendor Name : ANJLE MEP PROJECTS PVT LTD |  |  |  | Vendor Name : Pikture Perfect Design Studio Pvt. Ltd
|  | RFQ No: R0040 COST COMPARISON REPORT | RFQ No: R0040 COST COMPARISON REPORT | RFQ No: R0040 COST COMPARISON REPORT | RFQ #: R0040 | RFQ #: R0040 | RFQ #: R0040 | Contact Name : Mohd Ashraf |  |  |  | Contact Name : Priyanka/Premkant Rajpoot |  |  |  | Contact Name : Gangadhar Sharma
|  | RFQ No: R0040 COST COMPARISON REPORT | RFQ No: R0040 COST COMPARISON REPORT | RFQ No: R0040 COST COMPARISON REPORT | RFQ Date : 13/01/2024 15:17:25 | RFQ Date : 13/01/2024 15:17:25 | RFQ Date : 13/01/2024 15:17:25 | Vendor City : |  |  |  | Vendor City : |  |  |  | Vendor City :
|  | RFQ No: R0040 COST COMPARISON REPORT | RFQ No: R0040 COST COMPARISON REPORT | RFQ No: R0040 COST COMPARISON REPORT | BCD Date : | BCD Date : | BCD Date : | Telephone # : |  |  |  | Telephone # : |  |  |  | Telephone # :
|  | RFQ No: R0040 COST COMPARISON REPORT | RFQ No: R0040 COST COMPARISON REPORT | RFQ No: R0040 COST COMPARISON REPORT |  |  |  | Mobile # : |  |  |  | Mobile # : |  |  |  | Mobile # :
PR Number : TFSPL-2324-00102 | PR Number : TFSPL-2324-00102 | PR Number : TFSPL-2324-00102 | PR Number : TFSPL-2324-00102 | PR Number : TFSPL-2324-00102 | PR Number : TFSPL-2324-00102 | PR Number : TFSPL-2324-00102 | PR Number : TFSPL-2324-00102 | Email : projectspioneer@gmail.com |  |  |  | Email : anjlemepprojects@gmail.com |  |  |  | Email : piktureperfectdesignstudio@gmail.com
Package / RFQ Name : TFAS / RFQ / TFSPL-2324-00102 | Package / RFQ Name : TFAS / RFQ / TFSPL-2324-00102 | Package / RFQ Name : TFAS / RFQ / TFSPL-2324-00102 | Package / RFQ Name : TFAS / RFQ / TFSPL-2324-00102 | Package / RFQ Name : TFAS / RFQ / TFSPL-2324-00102 | Package / RFQ Name : TFAS / RFQ / TFSPL-2324-00102 | Package / RFQ Name : TFAS / RFQ / TFSPL-2324-00102 | Package / RFQ Name : TFAS / RFQ / TFSPL-2324-00102 | Round # : 1 (RFQ) |  | Round # : 2 (Auction) |  | Round # : 1 (RFQ) |  | Round # : 2 (Auction) |  | Round # : 1 (RFQ) |  | Round # : 2 (Auction)
Buyer : Jogeswar Sahu | Buyer : Jogeswar Sahu | Buyer : Jogeswar Sahu | Buyer : Jogeswar Sahu | Buyer : Jogeswar Sahu | Buyer : Jogeswar Sahu | Buyer : Jogeswar Sahu | Buyer : Jogeswar Sahu | Quotation Date : |  | Quotation Date : |  | Quotation Date : |  | Quotation Date : |  | Quotation Date : |  | Quotation Date :
Comp. # : 2 | Comp. # : 2 | Comp. # : 2 | Comp. # : 2 | Comp. # : 2 | Currency :INR | Currency :INR | Currency :INR | Quotation Validity Date : |  | Quotation Validity Date : |  | Quotation Validity Date : |  | Quotation Validity Date : |  | Quotation Validity Date : |  | Quotation Validity Date :
Comp. # : 2 | Comp. # : 2 | Comp. # : 2 | Comp. # : 2 | Comp. # : 2 | BUDGET PRICE : | .00 |  | Quote Currency : |  | Quote Currency : |  | Quote Currency : |  | Quote Currency : |  | Quote Currency : |  | Quote Currency :
# | Item Code | Item Description | Last PO Details | Unit | Qty | Last PO Unit Rate | Last PO Total Value | Score | Justification | Score | Justification | Score | Justification | Score | Justification | Score | Justification | Score | Justification
1 |  | HVAC low side |  | NOS | 1.000 | 0.00 | 0.00
2 | 1.1 | Chilled Water pipe |  |  | 0.000 | 0.00 | 0.00
3 |  | Supply, installation, testing commissioning of chilled water pipes in MS class C construction complete with fittings, bends, elbows, unions supports, vibration isolators,sleeves as per specifications and drawings |  |  | 0.000 | 0.00 | 0.00
4 | a | 100 mm dia. |  | Rmt | 0.000 | 0.00 | 0.00
5 | b | 80 mm dia. |  | Rmt | 0.000 | 0.00 | 0.00
6 | c | 65 mm dia. |  | Rmt | 0.000 | 0.00 | 0.00
7 | d | 50 mm dia. |  | Rmt | 0.000 | 0.00 | 0.00
8 | e | 40 mm dia. |  | Rmt | 0.000 | 0.00 | 0.00
9 | f | 32 mm dia. |  | Rmt | 10.000 | 0.00 | 0.00
10 | g | 25 mm dia. |  | Rmt | 0.000 | 0.00 | 0.00
11 | 2.2 | Chilled Water pipe Insulation |  |  | 0.000 | 0.00 | 0.00
12 |  | Providing and fixing insulation of 25 18 mm nitrile foam insullation with class O fire retardant propertiesby applying adhesive as per specifications and drawings. |  |  | 0.000 | 0.00 | 0.00
13 | a | 100 mm dia. |  | Rmt | 0.000 | 0.00 | 0.00
14 | b | 80 mm dia. |  | Rmt | 0.000 | 0.00 | 0.00
15 | c | 65 mm dia. |  | Rmt | 0.000 | 0.00 | 0.00
16 | d | 50 mm dia. |  | Rmt | 0.000 | 0.00 | 0.00
17 | e | 40 mm dia. |  | Rmt | 0.000 | 0.00 | 0.00
18 | f | 32 mm dia. |  | Rmt | 10.000 | 0.00 | 0.00
19 | g | 25 mm dia. |  | Rmt | 0.000 | 0.00 | 0.00
20 | 3 | Butter Fly Valve |  |  | 0.000 | 0.00 | 0.00
21 |  | Supply, installation, testing commissioning of following sizes of Butterfly valve with lug type construction, bolts, supports etc. The valves should be insulated by 18 mm nitrile foam by applying adhesive as per specifications. Valves should be sui |  |  | 0.000 | 0.00 | 0.00
22 | a | 80 mm dia. |  | Nos. | 0.000 | 0.00 | 0.00
23 | b | 65 mm dia. |  | Nos. | 0.000 | 0.00 | 0.00
24 | c | 50 mm dia. |  | Nos. | 0.000 | 0.00 | 0.00
25 | d | 40 mm dia. |  | Nos. | 0.000 | 0.00 | 0.00
26 | e | 32 mm dia. |  | Nos. | 0.000 | 0.00 | 0.00
27 | f | 25 mm dia. |  | Nos. | 0.000 | 0.00 | 0.00
28 | 4 | Ball Valve |  |  | 0.000 | 0.00 | 0.00
29 |  | Supply, installation, testing commissioning of following sizes of Ball valve with lug type construction, bolts, supports etc. The valves should be insulated by 18 mm nitril foam by applying adhesive as per specifications. Valves should be suitabl |  |  | 0.000 | 0.00 | 0.00
30 | e | 32 mm dia. |  | Nos. | 2.000 | 0.00 | 0.00
31 | f | 25 mm dia. |  | Nos. | 0.000 | 0.00 | 0.00
32 | 5 | Balancing Valve |  |  | 0.000 | 0.00 | 0.00
33 |  | Supply, installation, testing commissioning of following sizes of balancing valve with matching flanges, bolts, supports etc. The valves should be insulated by 18 mm nitril foam by applying adhesive as per specifications. Valves should be suitabl |  |  | 0.000 | 0.00 | 0.00
34 | a | 80 mm dia. |  | Nos. | 0.000 | 0.00 | 0.00
35 | b | 65 mm dia. |  | Nos. | 0.000 | 0.00 | 0.00
36 | c | 50 mm dia. |  | Nos. | 0.000 | 0.00 | 0.00
37 | d | 40 mm dia. |  | Nos. | 0.000 | 0.00 | 0.00
38 | e | 32 mm dia. |  | Nos. | 1.000 | 0.00 | 0.00
39 | f | 25 mm dia. |  | Nos. | 0.000 | 0.00 | 0.00
40 | 6 | Two Way valve OR Three Way Valve |  |  | 0.000 | 0.00 | 0.00
41 |  | Supply, installation, testing commissioning of following sizes of Two way Valve with matching flanges, bolts, supports etc. The valves should be insulated by making 24 G aluminium sheet box and filling loose TF thermocole applied as per specifications. |  |  | 0.000 | 0.00 | 0.00
42 | a | 80 mm dia. |  | Nos. | 0.000 | 0.00 | 0.00
43 | b | 65 mm dia. |  | Nos. | 0.000 | 0.00 | 0.00
44 | c | 50 mm dia. |  | Nos. | 0.000 | 0.00 | 0.00
45 | d | 40 mm dia. |  | Nos. | 0.000 | 0.00 | 0.00
46 | e | 32 mm dia. |  | Nos. | 1.000 | 0.00 | 0.00
47 | f | 25 mm dia. |  | Nos. | 0.000 | 0.00 | 0.00
48 | 7 | Y Stainer |  |  | 0.000 | 0.00 | 0.00
49 |  | Supply, installation, testing commissioning of following sizes of Y Stainer with matching flanges, bolts, supports etc. The valves should be insulated by making 24 G aluminium sheet box and filling loose TF thermocole applied as per specifications. |  |  | 0.000 | 0.00 | 0.00
50 | a | 80 mm dia. |  | Nos. | 0.000 | 0.00 | 0.00
51 | b | 65 mm dia. |  | Nos. | 0.000 | 0.00 | 0.00
52 | c | 50 mm dia. |  | Nos. | 0.000 | 0.00 | 0.00
53 | d | 40 mm dia. |  | Nos. | 0.000 | 0.00 | 0.00
54 | e | 32 mm dia. |  | Nos. | 1.000 | 0.00 | 0.00
55 | f | 25 mm dia. |  | Nos. | 0.000 | 0.00 | 0.00
56 | 8 | Auto Air vent valve |  |  | 0.000 | 0.00 | 0.00
57 |  | Supply, installation, testing commissioning of following sizes of Auto Air Vent Valve |  |  | 0.000 | 0.00 | 0.00
58 | a | 3/4 Ball valves for vent / Purge in each risers common headers |  | Nos. | 1.000 | 0.00 | 0.00
59 | 9 | Pressure Guage/Thermometer |  |  | 0.000 | 0.00 | 0.00
60 |  | Supply, installation, testing commissioning of following guages as per drawing |  |  | 0.000 | 0.00 | 0.00
61 | a | Pressure gauge with gauge cock, thermowell |  | Nos. | 1.000 | 0.00 | 0.00
62 | b | Thermometers (Mercury filled V form type) |  | Nos. | 1.000 | 0.00 | 0.00
63 | 10 | Drain Valves |  |  | 0.000 | 0.00 | 0.00
64 | a | 25mm dia |  | Nos. | 2.000 | 0.00 | 0.00
65 | b | 40mm dia |  | Nos. | 0.000 | 0.00 | 0.00
66 | 11 | Drain Piping; |  |  | 0.000 | 0.00 | 0.00
67 |  | Supply, installation, testing commissioning of following sizes insulated CPVC drain pipes from AHU drain pans to nearest floor drain and from CHW pump glands to the nearest drain complete with interconnection, flanges, elbows, tees, nuts, P-trap etc. Th |  |  | 0.000 | 0.00 | 0.00
68 | a | 65mm dia. |  | Rmt | 0.000 | 0.00 | 0.00
69 | b | 50mm dia. |  | Rmt | 2.000 | 0.00 | 0.00
70 | c | 40mm dia. |  | Rmt | 8.000 | 0.00 | 0.00
71 | d | 32mm dia. |  | Rmt | 0.000 | 0.00 | 0.00
72 | e | 25mm dia. |  | Rmt | 0.000 | 0.00 | 0.00
73 | 12 | AIR DISTRIBUTION SYSTEM |  |  | 0.000 | 0.00 | 0.00
74 | 12.1 | GI sheet metal rectangular duct |  |  | 0.000 | 0.00 | 0.00
75 |  | Supply, Fabrication, Installation, Testing Commissioning of following gauges of ducting complete with splitters, supports, dampers, and turning vanes as per specification and HVAC lay out. Aproved Makes JINDAL, TATA, SAIL, Equivalent. All exposed ducts |  |  | 0.000 | 0.00 | 0.00
76 | a | 24 gauge ducting - 0.63 mm thickness (upto - 750mm) |  | Sq. mt | 55.000 | 0.00 | 0.00
77 | b | 22 gauge ducting - 0.80 mm thickness (751 - 1500) |  | Sq. mt | 45.000 | 0.00 | 0.00
78 | c | 20 gauge ducting - 1.00 mm thickness (1501 - 2250) |  | Sq. mt | 5.000 | 0.00 | 0.00
79 | d | 18 gauge ducting - 1.20 mm thickness (2251-2500 plenum) |  | Sq. mt | 0.000 | 0.00 | 0.00
80 | 12.2 | GI sheet metal elpitical duct |  |  | 0.000 | 0.00 | 0.00
81 |  | Supply, Fabrication, Installation, Testing Commissioning of following gauges of ducting complete with splitters, supports, dampers, and turning vanes as per specification and HVAC lay out. Aproved Makes JINDAL, TATA, SAIL, Equivalent. All exposed ducts |  |  | 0.000 | 0.00 | 0.00
82 | a | 24 gauge ducting - 0.63 mm thickness (upto - 750mm) |  | Sq. mt | 0.000 | 0.00 | 0.00
83 | b | 22 gauge ducting - 0.80 mm thickness (751 - 1500) |  | Sq. mt | 0.000 | 0.00 | 0.00
84 | c | 20 gauge ducting - 1.00 mm thickness (1501 - 2250) |  | Sq. mt | 0.000 | 0.00 | 0.00
85 | d | 18 gauge ducting - 1.20 mm thickness (2251-2500 plenum) |  | Sq. mt | 0.000 | 0.00 | 0.00
86 | 12.3 | MS sheet metal rectangular duct |  |  | 0.000 | 0.00 | 0.00
87 |  | Supply, Fabrication, Installation, Testing Commissioning of following gauges of ducting complete with splitters, supports, dampers, and turning vanes as per specification and HVAC lay out. Aproved Makes JINDAL, TATA, SAIL, Equivalent. All exposed ducts |  |  | 0.000 | 0.00 | 0.00
88 | a | 16 gauge MS ducting - |  | Sq. mt | 0.000 | 0.00 | 0.00
89 | 14 | Accoustic Insulation |  |  | 0.000 | 0.00 | 0.00
90 |  | Accoustic lining of duct work with following thicknesss closed cell nitrile rubber- Makes A Flex, K Flex. |  |  | 0.000 | 0.00 | 0.00
91 |  | 15mm Thick |  | Sq. mt | 0.000 | 0.00 | 0.00
92 |  | 25mm Thick |  | Sq. mt | 7.000 | 0.00 | 0.00
93 | 15 | Thermal insulation Nitrile rubber Insulation ( Supply air ) |  |  | 0.000 | 0.00 | 0.00
94 |  | Providing and fixing nitrile rubber insulation with class O fire retardant properties by applying adhesive outside the ducts complete as per specifications and drawings.Make-K Flex, A Flex - Insulation exposed to ambient shall be covered with glass clot |  |  | 0.000 | 0.00 | 0.00
95 | a | 25 mm thick |  | Sq. mt | 0.000 | 0.00 | 0.00
96 | b | 19 mm thick |  | Sq. mt | 0.000 | 0.00 | 0.00
97 | c | 13 mm thick |  | Sq. mt | 48.000 | 0.00 | 0.00
98 | d | 9mm thick |  | Sq. mt | 0.000 | 0.00 | 0.00
99 | e | 6mm thick |  | Sq. mt | 0.000 | 0.00 | 0.00
100 | 16 | Thermal Exhaust Duct Insulation ( Only in BOH ) |  |  | 0.000 | 0.00 | 0.00
101 |  | Exhaust Air Duct insulation with 1325mm thick heatlon insulation within store. No insulation for duct outside store. Insulation exposed to ambient shall be covered with glass cloth UV protection paint. |  | Sq. mt | 42.000 | 0.00 | 0.00
102 | 17 | Thermal insulation- (Out side Building for Air washer) |  |  | 0.000 | 0.00 | 0.00
103 |  | Providing and fixing of 9mm thick nitrial rubber by applying adhesive inside the ducts c. (9mm thick) |  | Sq. mt | 0.000 | 0.00 | 0.00
104 | 18 | Under Deck Insulation |  |  | 0.000 | 0.00 | 0.00
105 | a | Under deck insulation for exporsed concrete slab using 19mm thick nitrile rubber insulation with class O fire retardant properties as per the specifications and drawings. Adhesive used shall be Low VOC type. Insulation to be mechanically fasteed using |  | Sq. mt | 0.000 | 0.00 | 0.00
106 | 19 | Continous / Linear Grilles |  |  | 0.000 | 0.00 | 0.00
107 |  | Extruded Aluminium Powder Coated Continous / Linear Grilles Of Required Airflow Angles with required damper at collar , with four side flanges as per requirements. (Make - AIRVISION/COSMOS) - Quoted Mahadi |  |  | 0.000 | 0.00 | 0.00
108 | a | 4 Width |  | Rmt | 0.000 | 0.00 | 0.00
109 | b | 6 Width |  | Rmt | 5.000 | 0.00 | 0.00
110 | c | 8 Width |  | Rmt | 0.000 | 0.00 | 0.00
111 | d | 10 Width |  | Rmt | 0.000 | 0.00 | 0.00
112 | g | Rount double louvered grill with damper for elipitical duct |  |  | 0.000 | 0.00 | 0.00
113 |  | 24 X6 |  | Nos | 0.000 | 0.00 | 0.00
114 |  | 22 X4 |  | Nos | 0.000 | 0.00 | 0.00
115 |  | 18 X6 |  | Nos | 0.000 | 0.00 | 0.00
116 |  | 48 X4 |  | Nos | 0.000 | 0.00 | 0.00
117 | 20 | Supply Air Square Grille |  |  | 0.000 | 0.00 | 0.00
118 |  | Supply, installation of aluminium extruded powdercoated supply air square grilles with four side flanges (0 degree deflection), with aluminium powder coated, multiple flape type with dampers.(Kitchen Area) |  |  | 0.000 | 0.00 | 0.00
119 | a | Neck Size - 18 x 18 (Outer Size - 24 x 24 ) |  | Nos. | 0.000 | 0.00 | 0.00
120 | b | Neck Size - 15 x 15 (Outer Size - 24 x 24 ) |  | Nos. | 0.000 | 0.00 | 0.00
121 | c | Neck Size - 12 x 12 (Outer Size - 24 x 24 ) |  | Nos. | 0.000 | 0.00 | 0.00
122 | d | Neck Size - 9 x 9 (Outer Size - 24 x 24 ) Double deflection grille |  | Nos. | 0.000 | 0.00 | 0.00
123 | 21 | Return Air Square Grille |  |  | 0.000 | 0.00 | 0.00
124 |  | Return air square grills without damper shall be four side flanges with active sizes as given below. |  |  | 0.000 | 0.00 | 0.00
125 | a | Outer Size - 24 x 24 |  | Nos. | 4.000 | 0.00 | 0.00
126 | b | Outer Size - 12 x 12 |  | Nos. | 0.000 | 0.00 | 0.00
127 | c | Outer Size - 36 x 14 |  | Nos. | 0.000 | 0.00 | 0.00
128 | d | 16 x 16 |  | Nos. | 0.000 | 0.00 | 0.00
129 | e | 8 x 8 |  | Nos. | 0.000 | 0.00 | 0.00
130 | f | 6 x 6 |  | Nos. | 0.000 | 0.00 | 0.00
131 | 22 | Supply Air Diffuser (Diffuser to be mounted on collar with damper) |  |  | 0.000 | 0.00 | 0.00
132 |  | Supply, installation of aluminium extruded powdercoated four way square diffuser with damper. Make-AIRVISION/COSMOS |  |  | 0.000 | 0.00 | 0.00
133 | a | Neck Size - 18 x 18 (Outer Size - 24 x 24 ) |  | Nos. | 12.000 | 0.00 | 0.00
134 | b | Neck Size - 15 x 15 (Outer Size - 24 x 24 ) |  | Nos. | 0.000 | 0.00 | 0.00
135 | 23 | Supply Return Air Diffuser (Diffuser to be mounted on collar with damper) |  |  | 0.000 | 0.00 | 0.00
136 |  | Supply, installation of aluminium extruded powdercoated four way square diffuser without damper. Make-AIRVISION/COSMOS |  |  | 0.000 | 0.00 | 0.00
137 | a | Outer Size - 24 x 24 |  | Nos. | 11.000 | 0.00 | 0.00
138 | b | Outer Size - 12 x 12 |  | Nos. | 0.000 | 0.00 | 0.00
139 | c | Outer Size - 8 x 8 |  | Nos. | 0.000 | 0.00 | 0.00
140 | 24 | Canvass Connection |  |  | 0.000 | 0.00 | 0.00
141 | a | Installation of Double Canvass connection for all air outlet / inlet, Fire retardant type with GI flanges for Units. |  | Nos. | 3.000 | 0.00 | 0.00
142 | b | Installation of Double Canvass connection for Inline Toilet Exhaust Fan. |  | Nos. | 0.000 | 0.00 | 0.00
143 | 25 | Volume Control Damper |  |  | 0.000 | 0.00 | 0.00
144 |  | Supply Installation of volume control damper on AHU mouth y piece. |  | Sq. mt | 2.000 | 0.00 | 0.00
145 | 26 | Collar Damper |  |  | 0.000 | 0.00 | 0.00
146 | a | Supply Installation of Collar Damper on AHU mouth y piece. |  | Sq.mt | 1.000 | 0.00 | 0.00
147 | 27 | Flexible Duct |  |  | 0.000 | 0.00 | 0.00
148 |  | Supply, installation, testing commissioning of Flexible Ducts of following sizes comprising of inner as well as outer skin constructed out of aluminium |  |  | 0.000 | 0.00 | 0.00
149 | a | 250 mm Dia |  | Rmt | 0.000 | 0.00 | 0.00
150 | b | 200 mm Dia |  | Rmt | 0.000 | 0.00 | 0.00
151 | c | 150 mm Dia |  | Rmt | 0.000 | 0.00 | 0.00
152 | 28 | Gas |  |  | 0.000 | 0.00 | 0.00
153 | a | R22 |  | KG | 0.000 | 0.00 | 0.00
154 | b | R32/R407C/R410A |  | KG | 0.000 | 0.00 | 0.00
155 | 29 | Misc. item |  |  | 0.000 | 0.00 | 0.00
156 | a | Hood Installation |  | Nos | 0.000 | 0.00 | 0.00
157 | b | Scaffolding |  | sqft | 0.000 | 0.00 | 0.00
158 | c | Catwalk |  | kg | 0.000 | 0.00 | 0.00
159 | d | DOL Starter Panel upto 7.5 HP with Cabling |  | Nos | 0.000 | 0.00 | 0.00
160 | e | Star delta panel above 7.5 HP |  | Nos | 0.000 | 0.00 | 0.00
161 | f | Cable Tray 300mm width |  | Rmt | 15.000 | 0.00 | 0.00
162 | 30 | Supply, Installation, Testing and Commissioning of motorised fire dampers suitable for at least 120 minutes fire rating as per the specifications and approved shop drawings. Quoted price shall be inclusive of copper control wiring as required. |  |  | 0.000 | 0.00 | 0.00
163 | a. | Bare Fire Dampers |  | SqM | 0.000 | 0.00 | 0.00
164 | b. | Spring return action type actuator complete with |  |  | 0.000 | 0.00 | 0.00
165 |  | control panel and temperature sensor. Torque not less |  | No | 0.000 | 0.00 | 0.00
166 |  | than 16NM |  |  | 0.000 | 0.00 | 0.00
167 |  | Sub total |  |  | 0.000 | 0.00 | 0.00
168 |  | GST extra as applicable |  |  | 0.000 | 0.00 | 0.00
169 |  | All the chasing works in wall supporting the HVAC system shall be in HVAC contractor scope only. |  |  | 0.000 | 0.00 | 0.00
170 |  | Chilled Water Piping - |  |  | 0.000 | 0.00 | 0.00
171 |  | Chilled water piping shall be confirming to IS 1239 Part I class ‘C’ heavy and fitting shall be conforming to ASTM A-105,3000lbs socket weld end (up to 50mm) 1S 1239 Part-II HEAVY/ASTM A-234 WPB, Gr.B butt weld fitting ( above 50nb pipe size) |  |  | 0.000 | 0.00 | 0.00
172 |  | Piping connection should be socket welded up to 50nb size and shall be butt weld above 50nb pipe size. Pipe flanges should be confirming to ASTM A-105 # 150 SORF and flange dimension should be in accordance with ASME/ANSI B 16.5 (150 SORF), fitting to fit |  |  | 0.000 | 0.00 | 0.00
173 |  | Post installation clearance by DIAL, CHW piping shall be tested @15kgf/cm2 hydrostatics pressure for 24hrs hold time and Testing should be witnessed to DIAL Team. |  |  | 0.000 | 0.00 | 0.00
174 |  | Thermal insulation on CHW and condensate drain piping line shall be 25mm thick. Closed cell antimicrobial Class “O” BS 476 and part 6 7 FM approved nitrile rubberelastomeric insulation thermal conductivity 0.033watts per meter-lvin(W/(M·K)) at 0°C. |  |  | 0.000 | 0.00 | 0.00
175 |  | Condensate drain piping shall be complying to IS 4985 Class 3 UPVC pipe. Solvent cement complying with ASTM D2564 shall be used for joints. |  |  | 0.000 | 0.00 | 0.00
176 |  | For ceiling suspended chilled water pipe Pipe should be hanged with tie rod of size minimum 10 mm dia. |  |  | 0.000 | 0.00 | 0.00
177 |  | HVAC High Side |  | NOS | 1.000 | 0.00 | 0.00
178 | 1.1 | Fresh Air Unit - 2500 CFM Supply Installation of the following cabinet type Fresh Air Fans with Forward curved inclined type heavy duty DIDW centrifugal fan with 3 phase TEFC with IP55 protection class F insulation, Double skin construction complete with Filters, adjusting brackets, twin V drive belt , vibration spring isolators, canvas connection and epoxy painted all as per specs. (Fan Make Kruger/Nicotra. Motor Crompton/Havells/BB )Static Pressure 65 mm |  | Nos | 1.000 | 0.00 | 0.00
179 | 1.2 | Dry Scrubber - 3500 CFM Supply installation of DRY scrubber each comprising of extract air intake section, electrostatic precipitation technology, dry type air cleaner to remove oil, smoke and fumes from exhaust air. Electrostatic section shall be made of 16 gauge galvanized sheet, high bake epoxy powder coated, washable type even air flow distribution plate, stainless steel spiked ionizers to create high voltage DC field, honey comb patented cylindrical structure filter cell which should be alternatively charged positive and negative with large collecting area , to work as magnet for charged smoke and oil particles. Average efficiency of 90-95% in single pass as per ASHRAE test method. Electrostatic Precipitator should be able to charge particles from 0.01 micron to 10 microns through solid state power supply. Collector cell should be of permanent type and incorporate slide out facility for easy removal for cleaning. Power supplies shall be 100% solid state UL Listed, Module of capacity below shall be equipped with multiple protection functions for power and overload and overheating with interlock switch for safety as per approved specification and drawings ) (Air Moving Capacities are - 8000 cfm 90 mmwg S.P.)Make -Rydair, Trion |  | Nos | 1.000 | 0.00 | 0.00
180 | 1.3 | Air Washer Unit - 2500 CFM Supply Installation of double skin construction packaged type air washer unit comprising of fan section with floor standing DIDW centrifugal fan, TEFC squirrel cage,induction motor of IP 55 protection,multi sheave pulley mounted on motor,Twin belt drive package wetting Pad section complete with 200 mm Thick Cellulose based Paper Fills with Drop-Stop eliminators,water distribution System complete with FRP Spray Headers,Float Valve,quick fill,Overflow,water circulation pump, tank,drain connection along with GI B class/PVC piping,strainers,fittings,base frame vibration isolators etc.Filter sections shall be complete with 50 mm Thick Aluminum Wire mesh Viscous metallic Filters.The fan section shall be fabricated out of 16 GaugeG.S.Sheet complete with inspection door.Wet section of Air Washer including sump shall be made out of 1.25 mm Thich SS 304 Stainless Steel sheet.(The blower motor shall be sutable for operation on 415+_10 %V,50 Hz,3 phase power supply) etc.The Air washer shall be as per specifications of following characteristics - ( Fan Make Kruger/Nicotra. Motor Crompton/Havells/BB ). |  |  | 0.000 | 0.00 | 0.00
181 | 1.4 | Exhaust Air Unit - 3500 CFM Supply Installation of Floor Mounted type Cabinate type Exhaust Centrifugal backward inclined DIDW blower with suitable high static pressure to create the required intake velocities and over come the pressure loss at the inlet of filters and ducts. DIDW Centrifugal blower. (Motor outside the effluent air stream.) backward inclined, non over loading type. ( smaller motor) mounted directly on motor shaft twin belt drive system. (slip losses and lesser maintenance) Dynamically balanced to provide a vibration free operation.Fan to be direct driven to motor. Multiblade box type zero leakage manually operated extruded aluminium volume control dampers shall be factory fitted at outlet of Exhaust Fan.Static Pressure 80 mm , Make -Kruger/Greenheck/System Air/Wolter/ Caryaire/ Nicotra |  | Nos | 1.000 | 0.00 | 0.00
182 | 1.5 | Ceiling Suspended Air Handling Units 5000 CFM, 9.5 TR Supply Installation of double skin ceiling suspended air handling units complete with 25mm thick insulated panels, forward curved DIDW Blower, cooling coil section with 6 Row DX CHW coil (coil Thickness -0.5mm), filter section with filters (EU-4), fan motor, drive set with double belt, mounting base damper etc.as per specifications and drawings. AHU shall have DOL Starter panel within 7.0 KW and above 7.0 KW star delte starter to be used. Motor should be IP 55 TEFC. ( Fan Make Kruger/Nicotra ). Coil temperature should be 12 deg C. AHU should be complete with filter frame with filter. Static Pressure 35mm AHUs shall be provided with Thermal Break Profile. a) Fan Outlet Velocity should not exceed 1800 FPM b) Coil face velocity should no exceed 500 FPM c) Filter velocity should not exceed 500 FPM |  |  | 0.000 | 0.00 | 0.00
183 |  | Notes |  |  | 0.000 | 0.00 | 0.00
184 |  | HVAC load 5000CFM/8.3TR (with VFD integration) has been approved |  |  | 0.000 | 0.00 | 0.00
185 |  | Kitchen ventilation shall comply to NFPA 96 guideline. |  |  | 0.000 | 0.00 | 0.00
186 |  | Section drawing needs to be facilitated for condensate line for prior approval before execution at site. |  |  | 0.000 | 0.00 | 0.00
187 |  | Makeup / exhaust air equipment detail needs to be facilitated for prior approval from DIAL. |  |  | 0.000 | 0.00 | 0.00
188 |  | TDS Test certificate for complete HVAC system to be shared for prior approval from DIAL. |  |  | 0.000 | 0.00 | 0.00
189 |  | Structural details for equipment placement to be approved by structural consultant (as per permissible load capacity mentioned in the design guideline) and all details to be shared with DIAL for prior approval from DIAL. |  |  | 0.000 | 0.00 | 0.00