## Price Comparison
|  | RFQ No: R0103 COST COMPARISON REPORT | RFQ No: R0103 COST COMPARISON REPORT | RFQ No: R0103 COST COMPARISON REPORT | Comp. Date : 29/01/2024 | Comp. Date : 29/01/2024 | Comp. Date : 29/01/2024 | Vendor Name : PIONEER PROJECT SOLUTION (RV232414136) | [5 empty] | Vendor Name : Mahamaya Engineering (RV232420123) | [5 empty] | Vendor Name : ANJLE MEP PROJECTS PVT LTD (RV232413533)
|  | RFQ No: R0103 COST COMPARISON REPORT | RFQ No: R0103 COST COMPARISON REPORT | RFQ No: R0103 COST COMPARISON REPORT | RFQ #: R0103 | RFQ #: R0103 | RFQ #: R0103 | Contact Name : Mohd Ashraf | [5 empty] | Contact Name : Yash Katoch | [5 empty] | Contact Name : Priyanka/Premkant Rajpoot
|  | RFQ No: R0103 COST COMPARISON REPORT | RFQ No: R0103 COST COMPARISON REPORT | RFQ No: R0103 COST COMPARISON REPORT | RFQ Date : 25/01/2024 15:14:22 | RFQ Date : 25/01/2024 15:14:22 | RFQ Date : 25/01/2024 15:14:22 | Vendor City : | [5 empty] | Vendor City : delhi | [5 empty] | Vendor City :
|  | RFQ No: R0103 COST COMPARISON REPORT | RFQ No: R0103 COST COMPARISON REPORT | RFQ No: R0103 COST COMPARISON REPORT | BCD Date : | BCD Date : | BCD Date : | Telephone # : | [5 empty] | Telephone # : 9810360460 | [5 empty] | Telephone # :
|  | RFQ No: R0103 COST COMPARISON REPORT | RFQ No: R0103 COST COMPARISON REPORT | RFQ No: R0103 COST COMPARISON REPORT |  |  |  | Mobile # : | [5 empty] | Mobile # : 9810360460 | [5 empty] | Mobile # :
PR Number : TFSPL-2324-00185 | PR Number : TFSPL-2324-00185 | PR Number : TFSPL-2324-00185 | PR Number : TFSPL-2324-00185 | PR Number : TFSPL-2324-00185 | PR Number : TFSPL-2324-00185 | PR Number : TFSPL-2324-00185 | PR Number : TFSPL-2324-00185 | Email : projectspioneer@gmail.com | [5 empty] | Email : mahamaya.engineering1@gmail.com | [5 empty] | Email : anjlemepprojects@gmail.com
Package / RFQ Name : TFAS / RFQ / TFSPL-2324-00185 | Package / RFQ Name : TFAS / RFQ / TFSPL-2324-00185 | Package / RFQ Name : TFAS / RFQ / TFSPL-2324-00185 | Package / RFQ Name : TFAS / RFQ / TFSPL-2324-00185 | Package / RFQ Name : TFAS / RFQ / TFSPL-2324-00185 | Package / RFQ Name : TFAS / RFQ / TFSPL-2324-00185 | Package / RFQ Name : TFAS / RFQ / TFSPL-2324-00185 | Package / RFQ Name : TFAS / RFQ / TFSPL-2324-00185 | Round # : 4 (Auction) | [5 empty] | Round # : 4 (Auction) | [5 empty] | Round # : 4 (Auction)
Buyer : Jogeswar Sahu / Technical : / Approver : | Buyer : Jogeswar Sahu / Technical : / Approver : | Buyer : Jogeswar Sahu / Technical : / Approver : | Buyer : Jogeswar Sahu / Technical : / Approver : | Buyer : Jogeswar Sahu / Technical : / Approver : | Buyer : Jogeswar Sahu / Technical : / Approver : | Buyer : Jogeswar Sahu / Technical : / Approver : | Buyer : Jogeswar Sahu / Technical : / Approver : | Quotation Date : |  |  | Quotation Validity Date : |  |  | Quotation Date : |  |  | Quotation Validity Date : |  |  | Quotation Date : |  |  | Quotation Validity Date :
Comp. # : 4 | Comp. # : 4 | Comp. # : 4 | Comp. # : 4 | Comp. # : 4 | Currency :INR | Currency :INR | Currency :INR | Buyer Remark : . | [5 empty] | Buyer Remark : | [5 empty] | Buyer Remark :
Comp. # : 4 | Comp. # : 4 | Comp. # : 4 | Comp. # : 4 | Comp. # : 4 | BUDGET PRICE : | .00 |  | Quote Currency : INR | [5 empty] | Quote Currency : INR | [5 empty] | Quote Currency : INR
# | Item Code | Item Description | Unit | Qty | Last PO Details | Lowest Unit Rate | Lowest Vendor | First Bid | Disc % | GST % | Technical | Unit Price | Total | First Bid | Disc % | GST % | Technical | Unit Price | Total | First Bid | Disc % | GST % | Technical | Unit Price | Total
1 |  | HVAC - High Side CHW AHU | NOS | 1.00 |  | 290700.00 | ANJLE MEP PROJECTS PVT LTD | 291500.00 | 0.00 | 0.00 |  | 290,800.00 | 290,800.00 | 445760.00 | 0.00 | 0.00 |  | 300,000.00 | 300,000.00 | 432200.00 | 0.00 | 0.00 |  | 290,700.00 | 290,700.00
2 |  | HVAV Low Side CHW AHU | NOS | 1.00 |  | 52400.00 | ANJLE MEP PROJECTS PVT LTD | 53400.00 | 0.00 | 0.00 |  | 52,420.00 | 52,420.00 | 60420.00 | 0.00 | 0.00 |  | 55,420.00 | 55,420.00 | 64900.00 | 0.00 | 0.00 |  | 52,400.00 | 52,400.00
3 |  | HVAC - Low Side BOQ | NOS | 1.00 |  | 736780.00 | PIONEER PROJECT SOLUTION | 799910.00 | 0.00 | 0.00 |  | 736,780.00 | 736,780.00 | 1135560.00 | 0.00 | 0.00 |  | 780,000.00 | 780,000.00 | 908900.00 | 0.00 | 0.00 |  | 758,180.00 | 758,180.00
4 |  | HVAC - Ventilation BOQ | NOS | 1.00 |  | 420000.00 | Mahamaya Engineering | 500000.00 | 0.00 | 0.00 |  | 440,000.00 | 440,000.00 | 479000.00 | 0.00 | 0.00 |  | 420,000.00 | 420,000.00 | 1021000.00 | 0.00 | 0.00 |  | 695,000.00 | 695,000.00
Item Total | [8 empty] | .00 | .00 |  |  | 1,520,000.00 |  | .00 | .00 |  |  | 1,555,420.00 |  | .00 | .00 |  |  | 1,796,280.00
Discount Total Value | [7 empty] | Grand Dis. Amt | .00 |  |  |  | .00 | Grand Dis. Amt | .00 |  |  |  | .00 | Grand Dis. Amt | .00 |  |  |  | .00
GST Total Amount | [12 empty] | .00 | [5 empty] | .00 | [5 empty] | .00
Net Landed Cost | [11 empty] | INR | 1,520,000.00 |  |  |  |  | INR | 1,555,420.00 |  |  |  |  | INR | 1,796,280.00
Vendor Status | [7 empty] | Round # : 4 (Auction) | Round # : 4 (Auction)
Sr No. | Vendor Code | Vendor Name | [5 empty] | Status | Remarks
1 | RV232420123 | Mahamaya Engineering | [5 empty] | Participate
2 | RV232414136 | PIONEER PROJECT SOLUTION | [5 empty] | Participate
3 | RV232413533 | ANJLE MEP PROJECTS PVT LTD | [5 empty] | Participate

## BOQ Price Bid
|  | RFQ No: R0103 COST COMPARISON REPORT | RFQ No: R0103 COST COMPARISON REPORT | Comp. Date : 29/01/2024 | Comp. Date : 29/01/2024 | Comp. Date : 29/01/2024 | Vendor Name : PIONEER PROJECT SOLUTION | Vendor Name : PIONEER PROJECT SOLUTION | Vendor Name : Mahamaya Engineering | Vendor Name : Mahamaya Engineering | Vendor Name : ANJLE MEP PROJECTS PVT LTD | Vendor Name : ANJLE MEP PROJECTS PVT LTD
|  | RFQ No: R0103 COST COMPARISON REPORT | RFQ No: R0103 COST COMPARISON REPORT | RFQ #: R0103 | RFQ #: R0103 | RFQ #: R0103 | Contact Name : Mohd Ashraf | Contact Name : Mohd Ashraf | Contact Name : Yash Katoch | Contact Name : Yash Katoch | Contact Name : Priyanka/Premkant Rajpoot | Contact Name : Priyanka/Premkant Rajpoot
|  | RFQ No: R0103 COST COMPARISON REPORT | RFQ No: R0103 COST COMPARISON REPORT | RFQ Date : 25/01/2024 15:14:22 | RFQ Date : 25/01/2024 15:14:22 | RFQ Date : 25/01/2024 15:14:22 | Vendor City : | Vendor City : | Vendor City : delhi | Vendor City : delhi | Vendor City : | Vendor City :
|  | RFQ No: R0103 COST COMPARISON REPORT | RFQ No: R0103 COST COMPARISON REPORT | BCD Date : | BCD Date : | BCD Date : | Telephone # : | Telephone # : | Telephone # : 9810360460 | Telephone # : 9810360460 | Telephone # : | Telephone # :
|  | RFQ No: R0103 COST COMPARISON REPORT | RFQ No: R0103 COST COMPARISON REPORT |  |  |  | Mobile # : | Mobile # : | Mobile # : 9810360460 | Mobile # : 9810360460 | Mobile # : | Mobile # :
PR Number : TFSPL-2324-00185 | PR Number : TFSPL-2324-00185 | PR Number : TFSPL-2324-00185 | PR Number : TFSPL-2324-00185 | PR Number : TFSPL-2324-00185 | PR Number : TFSPL-2324-00185 | PR Number : TFSPL-2324-00185 | Email : projectspioneer@gmail.com | Email : projectspioneer@gmail.com | Email : mahamaya.engineering1@gmail.com | Email : mahamaya.engineering1@gmail.com | Email : anjlemepprojects@gmail.com | Email : anjlemepprojects@gmail.com
Package / RFQ Name : TFAS / RFQ / TFSPL-2324-00185 | Package / RFQ Name : TFAS / RFQ / TFSPL-2324-00185 | Package / RFQ Name : TFAS / RFQ / TFSPL-2324-00185 | Package / RFQ Name : TFAS / RFQ / TFSPL-2324-00185 | Package / RFQ Name : TFAS / RFQ / TFSPL-2324-00185 | Package / RFQ Name : TFAS / RFQ / TFSPL-2324-00185 | Package / RFQ Name : TFAS / RFQ / TFSPL-2324-00185 | Round # : 4 (Auction) | Round # : 4 (Auction) | Round # : 4 (Auction) | Round # : 4 (Auction) | Round # : 4 (Auction) | Round # : 4 (Auction)
Buyer : Jogeswar Sahu | Buyer : Jogeswar Sahu | Buyer : Jogeswar Sahu | Buyer : Jogeswar Sahu | Buyer : Jogeswar Sahu | Buyer : Jogeswar Sahu | Buyer : Jogeswar Sahu | Techanical Score : | Techanical Score : | Techanical Score : | Techanical Score : | Techanical Score : | Techanical Score :
Comp. # : 4 | Comp. # : 4 | Comp. # : 4 | Comp. # : 4 | Currency :INR | Currency :INR | Currency :INR | Quotation Date : | Quotation Date : | Quotation Date : | Quotation Date : | Quotation Date : | Quotation Date :
Comp. # : 4 | Comp. # : 4 | Comp. # : 4 | Comp. # : 4 | BUDGET PRICE :.00 | BUDGET PRICE :.00 | BUDGET PRICE :.00 | Quotation Validity Date : | Quotation Validity Date : | Quotation Validity Date : | Quotation Validity Date : | Quotation Validity Date : | Quotation Validity Date :
Sr No. | Item Code | Item Name | Item Description | UOM | Qty | Minimum Amount | Unit Price | Amount | Unit Price | Amount | Unit Price | Amount
1 |  | HVAC - High Side CHW AHU | HVAC - High Side CHW AHU | NOS | 1.000 |  |  | 290,800.00 |  | 445,760.00 |  | 432,200.00
1 | 1.1 | Ceiling suspended Air Handling Unit - CHW Type | Ceiling suspended Air Handling Unit - CHW Type
2 |  | Supply of double skin ceiling suspended air handling units complete with 25mm thick insulated panels, Forward curved DIDW Blower, cooling coil section with 6 Row CHW coil, filter section with filters, fan motor, drive set, mounting base damper etc.as per a. Chilled water temperature entering 7 deg C exit 12 deg C b. Fan Outlet Velocity should not exceed 1800 FPM c. Coil face velocity should not exceed 500 FPM d. Filter velocity should not exceed 400 FPM (Access door and CHW pipe connection should be on RHS when viewed from filter side). | Supply of double skin ceiling suspended air handling units complete with 25mm thick insulated panels, Forward curved DIDW Blower, cooling coil section with 6 Row CHW coil, filter section with filters, fan motor, drive set, mounting base damper etc.as per a. Chilled water temperature entering 7 deg C exit 12 deg C b. Fan Outlet Velocity should not exceed 1800 FPM c. Coil face velocity should not exceed 500 FPM d. Filter velocity should not exceed 400 FPM (Access door and CHW pipe connection should be on RHS when viewed from filter side).
3 | a | 5720 CFM, 9.0 TR | 5720 CFM, 9.0 TR | Nos. | 1.000 | 195,000.00 | 195000.00 | 195,000.00 | 300000.00 | 300,000.00 | 195000.00 | 195,000.00
4 | 1.2 | Starter Panel | Starter Panel
5 |  | Supply of Direct online starters suitable for motors of Air handling units of below mentioned capacities (KW HP).The starter shall comprise of all necessary power and control equipments including, Auto manual selector switch, start stop push button, LED indicators. | Supply of Direct online starters suitable for motors of Air handling units of below mentioned capacities (KW HP).The starter shall comprise of all necessary power and control equipments including, Auto manual selector switch, start stop push button, LED indicators.
6 | a | 4.14KW (6HP) | 4.14KW (6HP) | Nos. | 1.000 | 22,500.00 | 22500.00 | 22,500.00 | 25000.00 | 25,000.00 | 23400.00 | 23,400.00
7 | 1.3 | Chilled Water pipe | Chilled Water pipe
8 |  | Supply of chilled water pipes in MS class C with necessary clamps, vibration isolator and fittings such as bends, tees etc. but excluding valves, strainers, gauges etc. Adequately supported on rigid supports duly painted as per specification and as requirements | Supply of chilled water pipes in MS class C with necessary clamps, vibration isolator and fittings such as bends, tees etc. but excluding valves, strainers, gauges etc. Adequately supported on rigid supports duly painted as per specification and as requirements
9 | a | 40 mm dia. | 40 mm dia. | Rmt | 14.000 | 9,100.00 | 700.00 | 9,800.00 | 890.00 | 12,460.00 | 650.00 | 9,100.00
10 | 1.4 | Chilled Water pipe Insulation | Chilled Water pipe Insulation
11 |  | Supply of insulation along with adhesive as per specifications and drawings. | Supply of insulation along with adhesive as per specifications and drawings.
12 | a | 40 mm dia. | 40 mm dia. | Rmt | 14.000 | 4,200.00 | 300.00 | 4,200.00 | 950.00 | 13,300.00 | 350.00 | 4,900.00
13 | 2.0 | CHW AHU Valve Station package | CHW AHU Valve Station package
14 |  | Supply of following valve station for air handling Unit. It shall include following Item 1. Ball Valve for AHU drain - 1 nos. 2. Y-Strainer - 1 nos. 3. 2 way control valve - 1 nos. 4. Temperature gauge - 2 nos. 5. Pressure gauge - 2 nos. 6. Balancing valve-1 nos 7.Air release purge valve-1 nos 8.Butterfly valve-5 nos 9. Necessary Insulated copper Pipe - as per site condition | Supply of following valve station for air handling Unit. It shall include following Item 1. Ball Valve for AHU drain - 1 nos. 2. Y-Strainer - 1 nos. 3. 2 way control valve - 1 nos. 4. Temperature gauge - 2 nos. 5. Pressure gauge - 2 nos. 6. Balancing valve-1 nos 7.Air release purge valve-1 nos 8.Butterfly valve-5 nos 9. Necessary Insulated copper Pipe - as per site condition
15 | a | 40 mm dia. | 40 mm dia. | Lot | 1.000 | 60,000.00 | 60000.00 | 60,000.00 | 95000.00 | 95,000.00 | 61500.00 | 61,500.00
2 |  | HVAV Low Side CHW AHU | HVAV Low Side CHW AHU | NOS | 1.000 |  |  | 52,420.00 |  | 60,420.00 |  | 64,900.00
16 | 1.1 | Ceiling suspended Air Handling Unit - CHW Type | Ceiling suspended Air Handling Unit - CHW Type
17 |  | Installation, testing and comissioning of double skin ceiling suspended air handling units complete with 25mm thick insulated panels, Forward curved DIDW Blower, cooling coil section with 6 Row CHW coil, filter section with filters, fan motor, drive set, mounting base damper etc.as per below a. Chilled water temperature entering 7 deg C exit 12 deg C b. Fan Outlet Velocity should not exceed 1800 FPM c. Coil face velocity should not exceed 500 FPM d. Filter velocity should not exceed 400 FPM (Access door and CHW pipe connection should be on RHS when viewed from filter side). | Installation, testing and comissioning of double skin ceiling suspended air handling units complete with 25mm thick insulated panels, Forward curved DIDW Blower, cooling coil section with 6 Row CHW coil, filter section with filters, fan motor, drive set, mounting base damper etc.as per below a. Chilled water temperature entering 7 deg C exit 12 deg C b. Fan Outlet Velocity should not exceed 1800 FPM c. Coil face velocity should not exceed 500 FPM d. Filter velocity should not exceed 400 FPM (Access door and CHW pipe connection should be on RHS when viewed from filter side).
18 | a | 5720 CFM, 9.0 TR | 5720 CFM, 9.0 TR | Nos. | 1.000 | 25,000.00 | 25000.00 | 25,000.00 | 30000.00 | 30,000.00 | 25000.00 | 25,000.00
19 | 1.2 | Starter Panel | Starter Panel
20 |  | Installation, testing and comissioning of Direct online starters suitable for motors of Air handling units of below mentioned capacities (KW HP).The starter shall comprise of all necessary power and control equipments including, Auto manual selector switch. | Installation, testing and comissioning of Direct online starters suitable for motors of Air handling units of below mentioned capacities (KW HP).The starter shall comprise of all necessary power and control equipments including, Auto manual selector switch.
21 | i | 4.14KW (6HP) | 4.14KW (6HP) | Nos. | 1.000 | 5,000.00 | 5000.00 | 5,000.00 | 5000.00 | 5,000.00 | 6500.00 | 6,500.00
22 | 1.3 | Chilled Water pipe | Chilled Water pipe
23 |  | Installation, testing and comissioning of chilled water pipes in MS class C with necessary clamps, vibration isolator and fittings such as bends, tees etc. but excluding valves, strainers, gauges etc. Adequately supported on rigid supports duly painted. | Installation, testing and comissioning of chilled water pipes in MS class C with necessary clamps, vibration isolator and fittings such as bends, tees etc. but excluding valves, strainers, gauges etc. Adequately supported on rigid supports duly painted.
24 | a | 40 mm dia. | 40 mm dia. | Rmt | 14.000 | 4,900.00 | 350.00 | 4,900.00 | 350.00 | 4,900.00 | 350.00 | 4,900.00
25 | 1.4 | Chilled Water pipe Insulation | Chilled Water pipe Insulation
26 |  | Installation, testing and comissioning of insulation by applying adhesive as per specifications and drawings. | Installation, testing and comissioning of insulation by applying adhesive as per specifications and drawings.
27 | a | 40 mm dia. | 40 mm dia. | Rmt | 14.000 | 2,520.00 | 250.00 | 3,500.00 | 180.00 | 2,520.00 | 250.00 | 3,500.00
28 | 2.0 | CHW AHU Valve Station | CHW AHU Valve Station
29 |  | Installation, testing and comissioning of following valve station for Air Handling Unit . It shall include following Item 1. Ball Valve for AHU drain - 1 nos. 2. Y-Strainer - 1 nos. 3. 2 way control valve - 1 nos. 4. Temperature gauge - 2 nos. 5. Pressure gauge - 2 nos. 6. Balancing valve-1 nos 7.Air release purge valve-1 nos 8.Butterfly valve-5 nos 9. Necessary Insulated copper Pipe - as per site condition | Installation, testing and comissioning of following valve station for Air Handling Unit . It shall include following Item 1. Ball Valve for AHU drain - 1 nos. 2. Y-Strainer - 1 nos. 3. 2 way control valve - 1 nos. 4. Temperature gauge - 2 nos. 5. Pressure gauge - 2 nos. 6. Balancing valve-1 nos 7.Air release purge valve-1 nos 8.Butterfly valve-5 nos 9. Necessary Insulated copper Pipe - as per site condition
30 | a | 40 mm dia. | 40 mm dia. | Lot | 1.000 | 15,000.00 | 15000.00 | 15,000.00 | 18000.00 | 18,000.00 | 25000.00 | 25,000.00
3 |  | HVAC - Low Side BOQ | HVAC - Low Side BOQ | NOS | 1.000 |  |  | 774,785.00 |  | 1,135,560.00 |  | 908,900.00
31 | 1.0 | AIR DISTRIBUTION SYSTEM | AIR DISTRIBUTION SYSTEM
32 | 1.1 | GI sheet metal rectangular duct | GI sheet metal rectangular duct
33 |  | Supply, Fabrication, Installation, Testing Commissioning of following gauges of ducting complete with splitters, neccessary supports, dampers, and turning vanes as per specification and HVAC layout. Aproved Makes JINDAL, TATA, SAIL, Equivalent. All exposed ducts and supports shall be painting with 2 coats of primer 2 coats of epoxy paint. (Make-JSW ESSAR) | Supply, Fabrication, Installation, Testing Commissioning of following gauges of ducting complete with splitters, neccessary supports, dampers, and turning vanes as per specification and HVAC layout. Aproved Makes JINDAL, TATA, SAIL, Equivalent. All exposed ducts and supports shall be painting with 2 coats of primer 2 coats of epoxy paint. (Make-JSW ESSAR)
34 | a | 24 gauge ducting - 0.63 mm thickness (Width upto - 750mm) | 24 gauge ducting - 0.63 mm thickness (Width upto - 750mm) | Sq. mt | 278.000 | 347,500.00 | 1250.00 | 347,500.00 | 1750.00 | 486,500.00 | 1250.00 | 347,500.00
35 | b | 22 gauge ducting - 0.80 mm thickness (Width 751 - 1500) | 22 gauge ducting - 0.80 mm thickness (Width 751 - 1500) | Sq. mt | 32.000 | 46,400.00 | 1450.00 | 46,400.00 | 1550.00 | 49,600.00 | 1450.00 | 46,400.00
36 | 2.0 | Accoustic Insulation | Accoustic Insulation
37 |  | Accoustic lining of duct work with 25mm thick -32kg m3 Density,Resin Bonded fibreglass Rigid Boards using shalikote primer hot bitumen and mechanically fastened Nuts Washers,covered with RP tissue and 30 G aluminium perforated sheet as per specs. Makes KIMMCO,OWEN S CORNING, U P TWIGA. | Accoustic lining of duct work with 25mm thick -32kg m3 Density,Resin Bonded fibreglass Rigid Boards using shalikote primer hot bitumen and mechanically fastened Nuts Washers,covered with RP tissue and 30 G aluminium perforated sheet as per specs. Makes KIMMCO,OWEN S CORNING, U P TWIGA. | Sq. mt | 30.000 | 40,500.00 | 1450.00 | 43,500.00 | 1350.00 | 40,500.00 | 1650.00 | 49,500.00
38 | 3.0 | XLPE Insulation (Supply Exhaust Fresh Air Duct) | XLPE Insulation (Supply Exhaust Fresh Air Duct)
39 |  | Providing and fixing XLPE insulation by applying adhesive on ducts complete as per specifications and drawings. Make-SUPREME PARAMOUNT. (Exhaust- out side insulation, Fresh air -outside insulation, Supply- Inside insulation, Supply-outside painted.) | Providing and fixing XLPE insulation by applying adhesive on ducts complete as per specifications and drawings. Make-SUPREME PARAMOUNT. (Exhaust- out side insulation, Fresh air -outside insulation, Supply- Inside insulation, Supply-outside painted.)
40 | a | 13 mm thick | 13 mm thick | Sq. mt | 305.000 | 198,250.00 | 650.00 | 198,250.00 | 850.00 | 259,250.00 | 850.00 | 259,250.00
41 | 4.0 | Thermal Exhaust Duct Insulation ( Only in BOH ) | Thermal Exhaust Duct Insulation ( Only in BOH )
42 |  | Exhaust Air Duct insulation with 13mm thick heatlon insulation within store. No insulation for duct outside store. | Exhaust Air Duct insulation with 13mm thick heatlon insulation within store. No insulation for duct outside store. | Sq. mt | 0.000 | .00 | 0.00 | .00 | 0.00 | .00 | 0.00 | .00
43 | 5.0 | Thermal insulation- (Out side Building ) | Thermal insulation- (Out side Building )
44 |  | Providing and fixing nitrial rubber by applying adhesive outside the ducts complete with 2 layer of UV paint and fiber glass cloth. (13mm thick) | Providing and fixing nitrial rubber by applying adhesive outside the ducts complete with 2 layer of UV paint and fiber glass cloth. (13mm thick) | Sq. mt | 0.000 | .00 | 0.00 | .00 | 0.00 | .00 | 0.00 | .00
45 | 4.0 | Continous Linear Grilles | Continous Linear Grilles
46 |  | Extruded Aluminium Powder Coated Continous Linear Grilles Of Required Airflow Angles (0 15 30 45 degree deflection 1 or 2 way) with four side flanges as per requirements. (Make - AIRVISION COSMOS) | Extruded Aluminium Powder Coated Continous Linear Grilles Of Required Airflow Angles (0 15 30 45 degree deflection 1 or 2 way) with four side flanges as per requirements. (Make - AIRVISION COSMOS)
47 | a | 6 Width | 6 Width | Rmt | 7.000 | 9,275.00 | 2050.00 | 14,350.00 | 1325.00 | 9,275.00 | 1350.00 | 9,450.00
48 | b | 8 Width | 8 Width | Rmt | 7.000 | 10,850.00 | 2450.00 | 17,150.00 | 1725.00 | 12,075.00 | 1550.00 | 10,850.00
49 | 5.0 | Supply Air Square Grille | Supply Air Square Grille
50 |  | Supply, installation of aluminium extruded white powder-coated supply air square grilles with four side flanges (0 22.5 45 degree deflection 1 or 2 way), with aluminium powder coated, multiple flape type with dampers. (Kitchen Area) | Supply, installation of aluminium extruded white powder-coated supply air square grilles with four side flanges (0 22.5 45 degree deflection 1 or 2 way), with aluminium powder coated, multiple flape type with dampers. (Kitchen Area)
51 | a | Neck Size - 12 x 12 (Outer Size - 14 x 14 ) | Neck Size - 12 x 12 (Outer Size - 14 x 14 ) | Nos. | 8.000 | 16,000.00 | 2000.00 | 16,000.00 | 6500.00 | 52,000.00 | 2250.00 | 18,000.00
52 | 6.0 | Return Air Square Grille | Return Air Square Grille
53 |  | Return air square grills without damper shall be four side flanges with active sizes as given below. | Return air square grills without damper shall be four side flanges with active sizes as given below.
54 | a | Neck Size - 14 x 14 (Outer Size - 16 x 16 ) | Neck Size - 14 x 14 (Outer Size - 16 x 16 ) | Nos. | 11.000 | 13,200.00 | 1200.00 | 13,200.00 | 7500.00 | 82,500.00 | 2450.00 | 26,950.00
55 | 7.0 | Canvass Connection | Canvass Connection
56 | a | Installation of Double Canvass connection for all air outlet inlet, Fire retardant type with GI flanges for Units. | Installation of Double Canvass connection for all air outlet inlet, Fire retardant type with GI flanges for Units. | Nos. | 7.000 | 17,500.00 | 2500.00 | 17,500.00 | 3500.00 | 24,500.00 | 2650.00 | 18,550.00
57 | 8.0 | Volume Control Damper (make - Cosmos Caryaire Air Product) | Volume Control Damper (make - Cosmos Caryaire Air Product)
58 |  | Supply Installation of volume control damper made of 100x40x1.55mm thk galvanised steel frame with opposed blades of 1.55mm galvanised sheet steel. | Supply Installation of volume control damper made of 100x40x1.55mm thk galvanised steel frame with opposed blades of 1.55mm galvanised sheet steel. | Sq. mt | 3.000 | 18,750.00 | 8500.00 | 25,500.00 | 8500.00 | 25,500.00 | 6250.00 | 18,750.00
59 | 9.0 | Collar Damper (make - Cosmos Caryaire Air Product) | Collar Damper (make - Cosmos Caryaire Air Product)
60 | a | Supply Installation of Collar Damper gear operated with vertical blades. | Supply Installation of Collar Damper gear operated with vertical blades. | Sq.mt | 4.000 | 1,400.00 | 5500.00 | 22,000.00 | 350.00 | 1,400.00 | 4250.00 | 17,000.00
61 | 10.0 | Drain Piping | Drain Piping
62 |  | Supply, Installation, testing commisioning of Drain Water piping work out of PVC HDPE hard pipes with insulation Complete with T joints and bends | Supply, Installation, testing commisioning of Drain Water piping work out of PVC HDPE hard pipes with insulation Complete with T joints and bends
63 | a | 32mm | 32mm | Rmt | 6.000 | 960.00 | 160.00 | 960.00 | 410.00 | 2,460.00 | 450.00 | 2,700.00
64 | 11.0 | Air Curtain | Air Curtain
65 | a | 1200 mm Long | 1200 mm Long | Nos. | 1.000 | 30,500.00 | 30500.00 | 30,500.00 | 35000.00 | 35,000.00 | 56500.00 | 56,500.00
66 | 12.0 | Electrical Cabling | Electrical Cabling
67 |  | Providing and laying Electrical PVC CU armoured cable from Weather proof enclosure MCB to Cassette Hi-wall Ductable ODU or DOL starter to Air handling units with 12SWG Earth WIRE (with cable glands lugs) | Providing and laying Electrical PVC CU armoured cable from Weather proof enclosure MCB to Cassette Hi-wall Ductable ODU or DOL starter to Air handling units with 12SWG Earth WIRE (with cable glands lugs)
68 | a | 3 C X 2.5 sq. mm. CU ARMOURED | 3 C X 2.5 sq. mm. CU ARMOURED | Rmt | 0.000 | .00 | 0.00 | .00 | 0.00 | .00 | 0.00 | .00
69 | b | 3 C X 4.0 sq. mm. CU ARMOURED | 3 C X 4.0 sq. mm. CU ARMOURED | Rmt | 0.000 | .00 | 0.00 | .00 | 0.00 | .00 | 0.00 | .00
70 | c | 3 C X 6.0 sq. mm. CU ARMOURED | 3 C X 6.0 sq. mm. CU ARMOURED | Rmt | 0.000 | .00 | 0.00 | .00 | 0.00 | .00 | 0.00 | .00
71 | d | 3 C X 10.0 sq. mm. CU ARMOURED | 3 C X 10.0 sq. mm. CU ARMOURED | Rmt | 0.000 | .00 | 0.00 | .00 | 0.00 | .00 | 0.00 | .00
72 | e | 3 C X 16.0 sq. mm. CU ARMOURED | 3 C X 16.0 sq. mm. CU ARMOURED | Rmt | 0.000 | .00 | 0.00 | .00 | 0.00 | .00 | 0.00 | .00
73 | f | 4 C X 2.5 sq. mm. CU ARMOURED | 4 C X 2.5 sq. mm. CU ARMOURED | Rmt | 0.000 | .00 | 0.00 | .00 | 0.00 | .00 | 0.00 | .00
74 | g | 4 C X 4.0 sq. mm. CU ARMOURED | 4 C X 4.0 sq. mm. CU ARMOURED | Rmt | 20.000 | 5,600.00 | 280.00 | 5,600.00 | 1250.00 | 25,000.00 | 750.00 | 15,000.00
75 | h | 4 C X 6.0 sq. mm. CU ARMOURED | 4 C X 6.0 sq. mm. CU ARMOURED | Rmt | 0.000 | .00 | 0.00 | .00 | 0.00 | .00 | 0.00 | .00
76 | i | 4 C X 10.0 sq. mm. CU ARMOURED | 4 C X 10.0 sq. mm. CU ARMOURED | Rmt | 0.000 | .00 | 0.00 | .00 | 0.00 | .00 | 0.00 | .00
77 | j | 4 C X 16.0 sq. mm. CU ARMOURED | 4 C X 16.0 sq. mm. CU ARMOURED | Rmt | 0.000 | .00 | 0.00 | .00 | 0.00 | .00 | 0.00 | .00
78 | 13.0 | Electrical work for HVAC | Electrical work for HVAC
79 | a | Supply and installation of all cabling, glanding, termination from starter panel to CSU. | Supply and installation of all cabling, glanding, termination from starter panel to CSU. | Lot | 1.000 | 1,500.00 | 1500.00 | 1,500.00 | 30000.00 | 30,000.00 | 12500.00 | 12,500.00
4 |  | HVAC - Ventilation BOQ | HVAC - Ventilation BOQ | NOS | 1.000 |  |  | 440,000.00 |  | 479,000.00 |  | 1,021,000.00
80 |  | VENTILATION UNIT FOR KITCHEN TOILET | VENTILATION UNIT FOR KITCHEN TOILET
81 | 1.0 | AIR WASHER UNIT (with Fresh Air Filters) | AIR WASHER UNIT (with Fresh Air Filters)
82 |  | Supply of Cabinate type Air Washer Unit backward inclined DIDW blower with suitable high static pressure to create the required intake velocities and over come the pressure loss at the inlet of filters and ducts. DIDW Centrifugal blower. (Motor outside the effluent air stream.) Backward inclined, non over loading type. ( smaller motor) mounted directly on motor shaft. (slip losses and lesser maintenance) Dynamically balanced to provide a vibration free operation. Control Panel Wall mounted incorporated with suitable starter of make siemens L T with single phase prevention.Fan to be direct driven to motor. The unit shall have water pump for recirculating water, Filter and water elliminator. | Supply of Cabinate type Air Washer Unit backward inclined DIDW blower with suitable high static pressure to create the required intake velocities and over come the pressure loss at the inlet of filters and ducts. DIDW Centrifugal blower. (Motor outside the effluent air stream.) Backward inclined, non over loading type. ( smaller motor) mounted directly on motor shaft. (slip losses and lesser maintenance) Dynamically balanced to provide a vibration free operation. Control Panel Wall mounted incorporated with suitable starter of make siemens L T with single phase prevention.Fan to be direct driven to motor. The unit shall have water pump for recirculating water, Filter and water elliminator.
83 | a | 4100 CFM | 4100 CFM
84 |  | 4100 CFM (external Static Pressure 100 mm) | 4100 CFM (external Static Pressure 100 mm) | Nos | 1.000 | 120,000.00 | 175000.00 | 175,000.00 | 120000.00 | 120,000.00 | 265000.00 | 265,000.00
85 | 2.0 | DRY SCRUBBER UNIT | DRY SCRUBBER UNIT
86 |  | Supply,Installation, testing commisioning of packaged type Exhaust Fan section along with Dry Type Scrubber, Stable placement of unit on respective foundation along with vibration isolation pad as per detail drawing specification, connecting all wiring, cabling, ducting other accessories as required to run unit acceptably.each comprising of extract air intake section, electrostatic precipitation technology, dry type air cleaner to remove oil, smoke and fumes from exhaust air. Electrostatic section shall be made of 16 gauge galvanized sheet, high bake epoxy powder coated, washable type even air flow distribution plate, stainless steel spiked ionizers to create high voltage DC field, honey comb patented cylindrical structure filter cell which should be alternatively charged positive and negative with large collecting area , to work as magnet for charged smoke and oil particles. Average efficiency of 90-95% in single pass as per ASHRAE test method. Electrostatic Precipitator should be able to charge particles from 0.01 micron to 10 microns through solid state power supply. Collector cell should be of permanent type and incorporate slide out facility for easy removal for cleaning. Power supplies shall be 100% solid state UL Listed, Module of capacity below shall be equipped with multiple protection functions for power and overload and overheating with interlock switch for safety as per approved specification and drawings). | Supply,Installation, testing commisioning of packaged type Exhaust Fan section along with Dry Type Scrubber, Stable placement of unit on respective foundation along with vibration isolation pad as per detail drawing specification, connecting all wiring, cabling, ducting other accessories as required to run unit acceptably.each comprising of extract air intake section, electrostatic precipitation technology, dry type air cleaner to remove oil, smoke and fumes from exhaust air. Electrostatic section shall be made of 16 gauge galvanized sheet, high bake epoxy powder coated, washable type even air flow distribution plate, stainless steel spiked ionizers to create high voltage DC field, honey comb patented cylindrical structure filter cell which should be alternatively charged positive and negative with large collecting area , to work as magnet for charged smoke and oil particles. Average efficiency of 90-95% in single pass as per ASHRAE test method. Electrostatic Precipitator should be able to charge particles from 0.01 micron to 10 microns through solid state power supply. Collector cell should be of permanent type and incorporate slide out facility for easy removal for cleaning. Power supplies shall be 100% solid state UL Listed, Module of capacity below shall be equipped with multiple protection functions for power and overload and overheating with interlock switch for safety as per approved specification and drawings).
87 | a | 4500 CFM | 4500 CFM
88 |  | 4500 CFM (external Static Pressure 100 mm) | 4500 CFM (external Static Pressure 100 mm) | Nos | 1.000 | 285,000.00 | 325000.00 | 325,000.00 | 285000.00 | 285,000.00 | 670000.00 | 670,000.00
89 | 3 | Freight ( Outstation) | Freight ( Outstation) | Nos | 2.000 | .00 | 0.00 | .00 | 15000.00 | 30,000.00 | 22500.00 | 45,000.00
90 | 4 | Installation ( Outstation) | Installation ( Outstation) | Nos | 2.000 | .00 | 0.00 | .00 | 22000.00 | 44,000.00 | 20500.00 | 41,000.00

## Technical Score Detail
|  | RFQ No: R0103 COST COMPARISON REPORT | RFQ No: R0103 COST COMPARISON REPORT | RFQ No: R0103 COST COMPARISON REPORT | Comp. Date : 29/01/2024 | Comp. Date : 29/01/2024 | Comp. Date : 29/01/2024 | Vendor Name : PIONEER PROJECT SOLUTION |  | Vendor Name : Mahamaya Engineering |  | Vendor Name : ANJLE MEP PROJECTS PVT LTD
|  | RFQ No: R0103 COST COMPARISON REPORT | RFQ No: R0103 COST COMPARISON REPORT | RFQ No: R0103 COST COMPARISON REPORT | RFQ #: R0103 | RFQ #: R0103 | RFQ #: R0103 | Contact Name : Mohd Ashraf |  | Contact Name : Yash Katoch |  | Contact Name : Priyanka/Premkant Rajpoot
|  | RFQ No: R0103 COST COMPARISON REPORT | RFQ No: R0103 COST COMPARISON REPORT | RFQ No: R0103 COST COMPARISON REPORT | RFQ Date : 25/01/2024 15:14:22 | RFQ Date : 25/01/2024 15:14:22 | RFQ Date : 25/01/2024 15:14:22 | Vendor City : |  | Vendor City : delhi |  | Vendor City :
|  | RFQ No: R0103 COST COMPARISON REPORT | RFQ No: R0103 COST COMPARISON REPORT | RFQ No: R0103 COST COMPARISON REPORT | BCD Date : | BCD Date : | BCD Date : | Telephone # : |  | Telephone # : 9810360460 |  | Telephone # :
|  | RFQ No: R0103 COST COMPARISON REPORT | RFQ No: R0103 COST COMPARISON REPORT | RFQ No: R0103 COST COMPARISON REPORT |  |  |  | Mobile # : |  | Mobile # : 9810360460 |  | Mobile # :
PR Number : TFSPL-2324-00185 | PR Number : TFSPL-2324-00185 | PR Number : TFSPL-2324-00185 | PR Number : TFSPL-2324-00185 | PR Number : TFSPL-2324-00185 | PR Number : TFSPL-2324-00185 | PR Number : TFSPL-2324-00185 | PR Number : TFSPL-2324-00185 | Email : projectspioneer@gmail.com |  | Email : mahamaya.engineering1@gmail.com |  | Email : anjlemepprojects@gmail.com
Package / RFQ Name : TFAS / RFQ / TFSPL-2324-00185 | Package / RFQ Name : TFAS / RFQ / TFSPL-2324-00185 | Package / RFQ Name : TFAS / RFQ / TFSPL-2324-00185 | Package / RFQ Name : TFAS / RFQ / TFSPL-2324-00185 | Package / RFQ Name : TFAS / RFQ / TFSPL-2324-00185 | Package / RFQ Name : TFAS / RFQ / TFSPL-2324-00185 | Package / RFQ Name : TFAS / RFQ / TFSPL-2324-00185 | Package / RFQ Name : TFAS / RFQ / TFSPL-2324-00185 | Round # : 4 (Auction) |  | Round # : 4 (Auction) |  | Round # : 4 (Auction)
Buyer : Jogeswar Sahu | Buyer : Jogeswar Sahu | Buyer : Jogeswar Sahu | Buyer : Jogeswar Sahu | Buyer : Jogeswar Sahu | Buyer : Jogeswar Sahu | Buyer : Jogeswar Sahu | Buyer : Jogeswar Sahu | Quotation Date : |  | Quotation Date : |  | Quotation Date :
Comp. # : 4 | Comp. # : 4 | Comp. # : 4 | Comp. # : 4 | Comp. # : 4 | Currency :INR | Currency :INR | Currency :INR | Quotation Validity Date : |  | Quotation Validity Date : |  | Quotation Validity Date :
Comp. # : 4 | Comp. # : 4 | Comp. # : 4 | Comp. # : 4 | Comp. # : 4 | BUDGET PRICE : | .00 |  | Quote Currency : |  | Quote Currency : |  | Quote Currency :
# | Item Code | Item Description | Last PO Details | Unit | Qty | Last PO Unit Rate | Last PO Total Value | Score | Justification | Score | Justification | Score | Justification
1 |  | HVAC - High Side CHW AHU |  | NOS | 1.000 | 0.00 | 0.00
2 | 1.1 | Ceiling suspended Air Handling Unit - CHW Type |  |  | 0.000 | 0.00 | 0.00
3 |  | Supply of double skin ceiling suspended air handling units complete with 25mm thick insulated panels, Forward curved DIDW Blower, cooling coil section with 6 Row CHW coil, filter section with filters, fan motor, drive set, mounting base damper etc.as per a. Chilled water temperature entering 7 deg C exit 12 deg C b. Fan Outlet Velocity should not exceed 1800 FPM c. Coil face velocity should not exceed 500 FPM d. Filter velocity should not exceed 400 FPM (Access door and CHW pipe connection should be on RHS when viewed from filter side). |  |  | 0.000 | 0.00 | 0.00
4 | a | 5720 CFM, 9.0 TR |  | Nos. | 1.000 | 0.00 | 0.00
5 | 1.2 | Starter Panel |  |  | 0.000 | 0.00 | 0.00
6 |  | Supply of Direct online starters suitable for motors of Air handling units of below mentioned capacities (KW HP).The starter shall comprise of all necessary power and control equipments including, Auto manual selector switch, start stop push button, LED indicators. |  |  | 0.000 | 0.00 | 0.00
7 | a | 4.14KW (6HP) |  | Nos. | 1.000 | 0.00 | 0.00
8 | 1.3 | Chilled Water pipe |  |  | 0.000 | 0.00 | 0.00
9 |  | Supply of chilled water pipes in MS class C with necessary clamps, vibration isolator and fittings such as bends, tees etc. but excluding valves, strainers, gauges etc. Adequately supported on rigid supports duly painted as per specification and as requirements |  |  | 0.000 | 0.00 | 0.00
10 | a | 40 mm dia. |  | Rmt | 14.000 | 0.00 | 0.00
11 | 1.4 | Chilled Water pipe Insulation |  |  | 0.000 | 0.00 | 0.00
12 |  | Supply of insulation along with adhesive as per specifications and drawings. |  |  | 0.000 | 0.00 | 0.00
13 | a | 40 mm dia. |  | Rmt | 14.000 | 0.00 | 0.00
14 | 2.0 | CHW AHU Valve Station package |  |  | 0.000 | 0.00 | 0.00
15 |  | Supply of following valve station for air handling Unit. It shall include following Item 1. Ball Valve for AHU drain - 1 nos. 2. Y-Strainer - 1 nos. 3. 2 way control valve - 1 nos. 4. Temperature gauge - 2 nos. 5. Pressure gauge - 2 nos. 6. Balancing valve-1 nos 7.Air release purge valve-1 nos 8.Butterfly valve-5 nos 9. Necessary Insulated copper Pipe - as per site condition |  |  | 0.000 | 0.00 | 0.00
16 | a | 40 mm dia. |  | Lot | 1.000 | 0.00 | 0.00
17 |  | HVAV Low Side CHW AHU |  | NOS | 1.000 | 0.00 | 0.00
18 | 1.1 | Ceiling suspended Air Handling Unit - CHW Type |  |  | 0.000 | 0.00 | 0.00
19 |  | Installation, testing and comissioning of double skin ceiling suspended air handling units complete with 25mm thick insulated panels, Forward curved DIDW Blower, cooling coil section with 6 Row CHW coil, filter section with filters, fan motor, drive set, mounting base damper etc.as per below a. Chilled water temperature entering 7 deg C exit 12 deg C b. Fan Outlet Velocity should not exceed 1800 FPM c. Coil face velocity should not exceed 500 FPM d. Filter velocity should not exceed 400 FPM (Access door and CHW pipe connection should be on RHS when viewed from filter side). |  |  | 0.000 | 0.00 | 0.00
20 | a | 5720 CFM, 9.0 TR |  | Nos. | 1.000 | 0.00 | 0.00
21 | 1.2 | Starter Panel |  |  | 0.000 | 0.00 | 0.00
22 |  | Installation, testing and comissioning of Direct online starters suitable for motors of Air handling units of below mentioned capacities (KW HP).The starter shall comprise of all necessary power and control equipments including, Auto manual selector switch. |  |  | 0.000 | 0.00 | 0.00
23 | i | 4.14KW (6HP) |  | Nos. | 1.000 | 0.00 | 0.00
24 | 1.3 | Chilled Water pipe |  |  | 0.000 | 0.00 | 0.00
25 |  | Installation, testing and comissioning of chilled water pipes in MS class C with necessary clamps, vibration isolator and fittings such as bends, tees etc. but excluding valves, strainers, gauges etc. Adequately supported on rigid supports duly painted. |  |  | 0.000 | 0.00 | 0.00
26 | a | 40 mm dia. |  | Rmt | 14.000 | 0.00 | 0.00
27 | 1.4 | Chilled Water pipe Insulation |  |  | 0.000 | 0.00 | 0.00
28 |  | Installation, testing and comissioning of insulation by applying adhesive as per specifications and drawings. |  |  | 0.000 | 0.00 | 0.00
29 | a | 40 mm dia. |  | Rmt | 14.000 | 0.00 | 0.00
30 | 2.0 | CHW AHU Valve Station |  |  | 0.000 | 0.00 | 0.00
31 |  | Installation, testing and comissioning of following valve station for Air Handling Unit . It shall include following Item 1. Ball Valve for AHU drain - 1 nos. 2. Y-Strainer - 1 nos. 3. 2 way control valve - 1 nos. 4. Temperature gauge - 2 nos. 5. Pressure gauge - 2 nos. 6. Balancing valve-1 nos 7.Air release purge valve-1 nos 8.Butterfly valve-5 nos 9. Necessary Insulated copper Pipe - as per site condition |  |  | 0.000 | 0.00 | 0.00
32 | a | 40 mm dia. |  | Lot | 1.000 | 0.00 | 0.00
33 |  | HVAC - Low Side BOQ |  | NOS | 1.000 | 0.00 | 0.00
34 | 1.0 | AIR DISTRIBUTION SYSTEM |  |  | 0.000 | 0.00 | 0.00
35 | 1.1 | GI sheet metal rectangular duct |  |  | 0.000 | 0.00 | 0.00
36 |  | Supply, Fabrication, Installation, Testing Commissioning of following gauges of ducting complete with splitters, neccessary supports, dampers, and turning vanes as per specification and HVAC layout. Aproved Makes JINDAL, TATA, SAIL, Equivalent. All exposed ducts and supports shall be painting with 2 coats of primer 2 coats of epoxy paint. (Make-JSW ESSAR) |  |  | 0.000 | 0.00 | 0.00
37 | a | 24 gauge ducting - 0.63 mm thickness (Width upto - 750mm) |  | Sq. mt | 278.000 | 0.00 | 0.00
38 | b | 22 gauge ducting - 0.80 mm thickness (Width 751 - 1500) |  | Sq. mt | 32.000 | 0.00 | 0.00
39 | 2.0 | Accoustic Insulation |  |  | 0.000 | 0.00 | 0.00
40 |  | Accoustic lining of duct work with 25mm thick -32kg m3 Density,Resin Bonded fibreglass Rigid Boards using shalikote primer hot bitumen and mechanically fastened Nuts Washers,covered with RP tissue and 30 G aluminium perforated sheet as per specs. Makes KIMMCO,OWEN S CORNING, U P TWIGA. |  | Sq. mt | 30.000 | 0.00 | 0.00
41 | 3.0 | XLPE Insulation (Supply Exhaust Fresh Air Duct) |  |  | 0.000 | 0.00 | 0.00
42 |  | Providing and fixing XLPE insulation by applying adhesive on ducts complete as per specifications and drawings. Make-SUPREME PARAMOUNT. (Exhaust- out side insulation, Fresh air -outside insulation, Supply- Inside insulation, Supply-outside painted.) |  |  | 0.000 | 0.00 | 0.00
43 | a | 13 mm thick |  | Sq. mt | 305.000 | 0.00 | 0.00
44 | 4.0 | Thermal Exhaust Duct Insulation ( Only in BOH ) |  |  | 0.000 | 0.00 | 0.00
45 |  | Exhaust Air Duct insulation with 13mm thick heatlon insulation within store. No insulation for duct outside store. |  | Sq. mt | 0.000 | 0.00 | 0.00
46 | 5.0 | Thermal insulation- (Out side Building ) |  |  | 0.000 | 0.00 | 0.00
47 |  | Providing and fixing nitrial rubber by applying adhesive outside the ducts complete with 2 layer of UV paint and fiber glass cloth. (13mm thick) |  | Sq. mt | 0.000 | 0.00 | 0.00
48 | 4.0 | Continous Linear Grilles |  |  | 0.000 | 0.00 | 0.00
49 |  | Extruded Aluminium Powder Coated Continous Linear Grilles Of Required Airflow Angles (0 15 30 45 degree deflection 1 or 2 way) with four side flanges as per requirements. (Make - AIRVISION COSMOS) |  |  | 0.000 | 0.00 | 0.00
50 | a | 6 Width |  | Rmt | 7.000 | 0.00 | 0.00
51 | b | 8 Width |  | Rmt | 7.000 | 0.00 | 0.00
52 | 5.0 | Supply Air Square Grille |  |  | 0.000 | 0.00 | 0.00
53 |  | Supply, installation of aluminium extruded white powder-coated supply air square grilles with four side flanges (0 22.5 45 degree deflection 1 or 2 way), with aluminium powder coated, multiple flape type with dampers. (Kitchen Area) |  |  | 0.000 | 0.00 | 0.00
54 | a | Neck Size - 12 x 12 (Outer Size - 14 x 14 ) |  | Nos. | 8.000 | 0.00 | 0.00
55 | 6.0 | Return Air Square Grille |  |  | 0.000 | 0.00 | 0.00
56 |  | Return air square grills without damper shall be four side flanges with active sizes as given below. |  |  | 0.000 | 0.00 | 0.00
57 | a | Neck Size - 14 x 14 (Outer Size - 16 x 16 ) |  | Nos. | 11.000 | 0.00 | 0.00
58 | 7.0 | Canvass Connection |  |  | 0.000 | 0.00 | 0.00
59 | a | Installation of Double Canvass connection for all air outlet inlet, Fire retardant type with GI flanges for Units. |  | Nos. | 7.000 | 0.00 | 0.00
60 | 8.0 | Volume Control Damper (make - Cosmos Caryaire Air Product) |  |  | 0.000 | 0.00 | 0.00
61 |  | Supply Installation of volume control damper made of 100x40x1.55mm thk galvanised steel frame with opposed blades of 1.55mm galvanised sheet steel. |  | Sq. mt | 3.000 | 0.00 | 0.00
62 | 9.0 | Collar Damper (make - Cosmos Caryaire Air Product) |  |  | 0.000 | 0.00 | 0.00
63 | a | Supply Installation of Collar Damper gear operated with vertical blades. |  | Sq.mt | 4.000 | 0.00 | 0.00
64 | 10.0 | Drain Piping |  |  | 0.000 | 0.00 | 0.00
65 |  | Supply, Installation, testing commisioning of Drain Water piping work out of PVC HDPE hard pipes with insulation Complete with T joints and bends |  |  | 0.000 | 0.00 | 0.00
66 | a | 32mm |  | Rmt | 6.000 | 0.00 | 0.00
67 | 11.0 | Air Curtain |  |  | 0.000 | 0.00 | 0.00
68 | a | 1200 mm Long |  | Nos. | 1.000 | 0.00 | 0.00
69 | 12.0 | Electrical Cabling |  |  | 0.000 | 0.00 | 0.00
70 |  | Providing and laying Electrical PVC CU armoured cable from Weather proof enclosure MCB to Cassette Hi-wall Ductable ODU or DOL starter to Air handling units with 12SWG Earth WIRE (with cable glands lugs) |  |  | 0.000 | 0.00 | 0.00
71 | a | 3 C X 2.5 sq. mm. CU ARMOURED |  | Rmt | 0.000 | 0.00 | 0.00
72 | b | 3 C X 4.0 sq. mm. CU ARMOURED |  | Rmt | 0.000 | 0.00 | 0.00
73 | c | 3 C X 6.0 sq. mm. CU ARMOURED |  | Rmt | 0.000 | 0.00 | 0.00
74 | d | 3 C X 10.0 sq. mm. CU ARMOURED |  | Rmt | 0.000 | 0.00 | 0.00
75 | e | 3 C X 16.0 sq. mm. CU ARMOURED |  | Rmt | 0.000 | 0.00 | 0.00
76 | f | 4 C X 2.5 sq. mm. CU ARMOURED |  | Rmt | 0.000 | 0.00 | 0.00
77 | g | 4 C X 4.0 sq. mm. CU ARMOURED |  | Rmt | 20.000 | 0.00 | 0.00
78 | h | 4 C X 6.0 sq. mm. CU ARMOURED |  | Rmt | 0.000 | 0.00 | 0.00
79 | i | 4 C X 10.0 sq. mm. CU ARMOURED |  | Rmt | 0.000 | 0.00 | 0.00
80 | j | 4 C X 16.0 sq. mm. CU ARMOURED |  | Rmt | 0.000 | 0.00 | 0.00
81 | 13.0 | Electrical work for HVAC |  |  | 0.000 | 0.00 | 0.00
82 | a | Supply and installation of all cabling, glanding, termination from starter panel to CSU. |  | Lot | 1.000 | 0.00 | 0.00
83 |  | HVAC - Ventilation BOQ |  | NOS | 1.000 | 0.00 | 0.00
84 |  | VENTILATION UNIT FOR KITCHEN TOILET |  |  | 0.000 | 0.00 | 0.00
85 | 1.0 | AIR WASHER UNIT (with Fresh Air Filters) |  |  | 0.000 | 0.00 | 0.00
86 |  | Supply of Cabinate type Air Washer Unit backward inclined DIDW blower with suitable high static pressure to create the required intake velocities and over come the pressure loss at the inlet of filters and ducts. DIDW Centrifugal blower. (Motor outside the effluent air stream.) Backward inclined, non over loading type. ( smaller motor) mounted directly on motor shaft. (slip losses and lesser maintenance) Dynamically balanced to provide a vibration free operation. Control Panel Wall mounted incorporated with suitable starter of make siemens L T with single phase prevention.Fan to be direct driven to motor. The unit shall have water pump for recirculating water, Filter and water elliminator. |  |  | 0.000 | 0.00 | 0.00
87 | a | 4100 CFM |  |  | 0.000 | 0.00 | 0.00
88 |  | 4100 CFM (external Static Pressure 100 mm) |  | Nos | 1.000 | 0.00 | 0.00
89 | 2.0 | DRY SCRUBBER UNIT |  |  | 0.000 | 0.00 | 0.00
90 |  | Supply,Installation, testing commisioning of packaged type Exhaust Fan section along with Dry Type Scrubber, Stable placement of unit on respective foundation along with vibration isolation pad as per detail drawing specification, connecting all wiring, cabling, ducting other accessories as required to run unit acceptably.each comprising of extract air intake section, electrostatic precipitation technology, dry type air cleaner to remove oil, smoke and fumes from exhaust air. Electrostatic section shall be made of 16 gauge galvanized sheet, high bake epoxy powder coated, washable type even air flow distribution plate, stainless steel spiked ionizers to create high voltage DC field, honey comb patented cylindrical structure filter cell which should be alternatively charged positive and negative with large collecting area , to work as magnet for charged smoke and oil particles. Average efficiency of 90-95% in single pass as per ASHRAE test method. Electrostatic Precipitator should be able to charge particles from 0.01 micron to 10 microns through solid state power supply. Collector cell should be of permanent type and incorporate slide out facility for easy removal for cleaning. Power supplies shall be 100% solid state UL Listed, Module of capacity below shall be equipped with multiple protection functions for power and overload and overheating with interlock switch for safety as per approved specification and drawings). |  |  | 0.000 | 0.00 | 0.00
91 | a | 4500 CFM |  |  | 0.000 | 0.00 | 0.00
92 |  | 4500 CFM (external Static Pressure 100 mm) |  | Nos | 1.000 | 0.00 | 0.00
93 | 3 | Freight ( Outstation) |  | Nos | 2.000 | 0.00 | 0.00
94 | 4 | Installation ( Outstation) |  | Nos | 2.000 | 0.00 | 0.00