## Price Comparison
|  | RFQ No: R0179 COST COMPARISON REPORT | RFQ No: R0179 COST COMPARISON REPORT | RFQ No: R0179 COST COMPARISON REPORT | Comp. Date : 20/02/2024 | Comp. Date : 20/02/2024 | Comp. Date : 20/02/2024 | Vendor Name : ANJLE MEP PROJECTS PVT LTD (RV232413533) | [20 empty] | Vendor Name : PIONEER PROJECT SOLUTION (RV232414136)
|  | RFQ No: R0179 COST COMPARISON REPORT | RFQ No: R0179 COST COMPARISON REPORT | RFQ No: R0179 COST COMPARISON REPORT | RFQ #: R0179 | RFQ #: R0179 | RFQ #: R0179 | Contact Name : Priyanka/Premkant Rajpoot | [20 empty] | Contact Name : Mohd Ashraf
|  | RFQ No: R0179 COST COMPARISON REPORT | RFQ No: R0179 COST COMPARISON REPORT | RFQ No: R0179 COST COMPARISON REPORT | RFQ Date : 19/02/2024 17:22:21 | RFQ Date : 19/02/2024 17:22:21 | RFQ Date : 19/02/2024 17:22:21 | Vendor City : | [20 empty] | Vendor City :
|  | RFQ No: R0179 COST COMPARISON REPORT | RFQ No: R0179 COST COMPARISON REPORT | RFQ No: R0179 COST COMPARISON REPORT | BCD Date : | BCD Date : | BCD Date : | Telephone # : | [20 empty] | Telephone # :
|  | RFQ No: R0179 COST COMPARISON REPORT | RFQ No: R0179 COST COMPARISON REPORT | RFQ No: R0179 COST COMPARISON REPORT |  |  |  | Mobile # : | [20 empty] | Mobile # :
PR Number : TFSPL-2324-00251 | PR Number : TFSPL-2324-00251 | PR Number : TFSPL-2324-00251 | PR Number : TFSPL-2324-00251 | PR Number : TFSPL-2324-00251 | PR Number : TFSPL-2324-00251 | PR Number : TFSPL-2324-00251 | PR Number : TFSPL-2324-00251 | Email : anjlemepprojects@gmail.com | [20 empty] | Email : projectspioneer@gmail.com
Package / RFQ Name : HVAC work - Internation Food Hall | Package / RFQ Name : HVAC work - Internation Food Hall | Package / RFQ Name : HVAC work - Internation Food Hall | Package / RFQ Name : HVAC work - Internation Food Hall | Package / RFQ Name : HVAC work - Internation Food Hall | Package / RFQ Name : HVAC work - Internation Food Hall | Package / RFQ Name : HVAC work - Internation Food Hall | Package / RFQ Name : HVAC work - Internation Food Hall | Round # : 1 (RFQ) |  |  |  |  | Round # : 2 (RFQ) |  |  |  |  | Round # : 3 (RFQ) |  |  |  |  | Round # : 4 (Auction) | [5 empty] | Round # : 1 (RFQ) |  |  |  |  | Round # : 2 (RFQ) |  |  |  |  | Round # : 3 (RFQ) |  |  |  |  | Round # : 4 (Auction)
Buyer : Jogeswar Sahu / Technical : / Approver : | Buyer : Jogeswar Sahu / Technical : / Approver : | Buyer : Jogeswar Sahu / Technical : / Approver : | Buyer : Jogeswar Sahu / Technical : / Approver : | Buyer : Jogeswar Sahu / Technical : / Approver : | Buyer : Jogeswar Sahu / Technical : / Approver : | Buyer : Jogeswar Sahu / Technical : / Approver : | Buyer : Jogeswar Sahu / Technical : / Approver : | Quotation Date : |  | Quotation Validity Date : |  |  | Quotation Date : |  | Quotation Validity Date : |  |  | Quotation Date : |  | Quotation Validity Date : |  |  | Quotation Date : |  |  | Quotation Validity Date : |  |  | Quotation Date : |  | Quotation Validity Date : |  |  | Quotation Date : |  | Quotation Validity Date : |  |  | Quotation Date : |  | Quotation Validity Date : |  |  | Quotation Date : |  |  | Quotation Validity Date :
Comp. # : 4 | Comp. # : 4 | Comp. # : 4 | Comp. # : 4 | Comp. # : 4 | Currency :INR | Currency :INR | Currency :INR | Buyer Remark : |  |  |  |  | Buyer Remark : . |  |  |  |  | Buyer Remark : |  |  |  |  | Buyer Remark : . | [5 empty] | Buyer Remark : |  |  |  |  | Buyer Remark : |  |  |  |  | Buyer Remark : |  |  |  |  | Buyer Remark :
Comp. # : 4 | Comp. # : 4 | Comp. # : 4 | Comp. # : 4 | Comp. # : 4 | BUDGET PRICE : | .00 |  | Quote Currency : INR |  |  |  |  | Quote Currency : INR |  |  |  |  | Quote Currency : INR |  |  |  |  | Quote Currency : INR | [5 empty] | Quote Currency : INR |  |  |  |  | Quote Currency : INR |  |  |  |  | Quote Currency : INR |  |  |  |  | Quote Currency : INR
# | Item Code | Item Description | Unit | Qty | Last PO Details | Lowest Unit Rate | Lowest Vendor | Price | Disc % | GST % | Unit Price | Total | Price | Disc % | GST % | Unit Price | Total | Price | Disc % | GST % | Unit Price | Total | Price | Disc % | GST % | Technical | Unit Price | Total | Price | Disc % | GST % | Unit Price | Total | Price | Disc % | GST % | Unit Price | Total | Price | Disc % | GST % | Unit Price | Total | Price | Disc % | GST % | Technical | Unit Price | Total
1 |  | High Side - HVAC | NOS | 1.00 |  | 1314700.00 | ANJLE MEP PROJECTS PVT LTD | 1900000.00 | 0.00 | 28.00 | 1,900,000.00 | 1,900,000.00 | 1900000.00 | 0.00 | 18.00 | 1,404,400.00 | 1,404,400.00 | 1900000.00 | 0.00 | 18.00 | 1,404,400.00 | 1,404,400.00 | 1900000.00 | 0.00 | 0.00 |  | 1,314,700.00 | 1,314,700.00 | 1405000.00 | 0.00 | 18.00 | 1,405,000.00 | 1,405,000.00 | 1405000.00 | 0.00 | 18.00 | 1,405,000.00 | 1,405,000.00 | 1405000.00 | 0.00 | 18.00 | 1,315,000.00 | 1,315,000.00 | 1405000.00 | 0.00 | 0.00 |  | 1,315,000.00 | 1,315,000.00
2 |  | Low Side - HVAC | NOS | 1.00 |  | 1622000.00 | ANJLE MEP PROJECTS PVT LTD | 2090700.00 | 0.00 | 18.00 | 2,090,700.00 | 2,090,700.00 | 2090700.00 | 0.00 | 18.00 | 1,622,000.00 | 1,622,000.00 | 2090700.00 | 0.00 | 18.00 | 1,622,000.00 | 1,622,000.00 | 2090700.00 | 0.00 | 0.00 |  | 1,622,000.00 | 1,622,000.00 | 1646100.00 | 0.00 | 18.00 | 1,646,100.00 | 1,646,100.00 | 1646100.00 | 0.00 | 18.00 | 1,646,100.00 | 1,646,100.00 | 1646100.00 | 0.00 | 18.00 | 1,641,100.00 | 1,641,100.00 | 1646100.00 | 0.00 | 0.00 |  | 1,641,100.00 | 1,641,100.00
Item Total | [8 empty] | .00 | 908,326.00 |  | 3,990,700.00 |  | .00 | 544,752.00 |  | 3,026,400.00 |  | .00 | 544,752.00 |  | 3,026,400.00 |  | .00 | .00 |  |  | 2,936,700.00 |  | .00 | 549,198.00 |  | 3,051,100.00 |  | .00 | 549,198.00 |  | 3,051,100.00 |  | .00 | 532,098.00 |  | 2,956,100.00 |  | .00 | .00 |  |  | 2,956,100.00
Discount Total Value | [7 empty] | Grand Dis. Amt | .00 |  |  | .00 | Grand Dis. Amt | .00 |  |  | .00 | Grand Dis. Amt | .00 |  |  | .00 | Grand Dis. Amt | .00 |  |  |  | .00 | Grand Dis. Amt | .00 |  |  | .00 | Grand Dis. Amt | .00 |  |  | .00 | Grand Dis. Amt | .00 |  |  | .00 | Grand Dis. Amt | .00 |  |  |  | .00
GST Total Amount | [11 empty] | 908,326.00 |  |  |  |  | 544,752.00 |  |  |  |  | 544,752.00 | [5 empty] | .00 |  |  |  |  | 549,198.00 |  |  |  |  | 549,198.00 |  |  |  |  | 532,098.00 | [5 empty] | .00
Net Landed Cost | [10 empty] | INR | 4,899,026.00 |  |  |  | INR | 3,571,152.00 |  |  |  | INR | 3,571,152.00 |  |  |  |  | INR | 2,936,700.00 |  |  |  | INR | 3,600,298.00 |  |  |  | INR | 3,600,298.00 |  |  |  | INR | 3,488,198.00 |  |  |  |  | INR | 2,956,100.00
Vendor Status | [7 empty] | Round # : 1 (RFQ) | Round # : 1 (RFQ) | Round # : 2 (RFQ) | Round # : 2 (RFQ) | Round # : 3 (RFQ) | Round # : 3 (RFQ) | Round # : 4 (Auction) | Round # : 4 (Auction)
Sr No. | Vendor Code | Vendor Name | [5 empty] | Status | Remarks | Status | Remarks | Status | Remarks | Status | Remarks
1 | RV232414136 | PIONEER PROJECT SOLUTION | [5 empty] | Participate |  | Participate |  | Participate |  | Participate
2 | RV232413533 | ANJLE MEP PROJECTS PVT LTD | [5 empty] | Participate |  | Participate |  | Participate |  | Participate
3 | T053067 | Carrier | [9 empty] | Not Participate |  | Not Participate
4 | T053066 | Bluestar Ltd | [9 empty] | Regret | We cannot quote for Chilled water type requirements. | Not Participate | We cannot quote for Chilled water type requirements.

## BOQ Price Bid
|  | RFQ No: R0179 COST COMPARISON REPORT | RFQ No: R0179 COST COMPARISON REPORT | Comp. Date : 20/02/2024 | Comp. Date : 20/02/2024 | Comp. Date : 20/02/2024 | Vendor Name : ANJLE MEP PROJECTS PVT LTD | Vendor Name : ANJLE MEP PROJECTS PVT LTD | Vendor Name : PIONEER PROJECT SOLUTION | Vendor Name : PIONEER PROJECT SOLUTION
|  | RFQ No: R0179 COST COMPARISON REPORT | RFQ No: R0179 COST COMPARISON REPORT | RFQ #: R0179 | RFQ #: R0179 | RFQ #: R0179 | Contact Name : Priyanka/Premkant Rajpoot | Contact Name : Priyanka/Premkant Rajpoot | Contact Name : Mohd Ashraf | Contact Name : Mohd Ashraf
|  | RFQ No: R0179 COST COMPARISON REPORT | RFQ No: R0179 COST COMPARISON REPORT | RFQ Date : 19/02/2024 17:22:21 | RFQ Date : 19/02/2024 17:22:21 | RFQ Date : 19/02/2024 17:22:21 | Vendor City : | Vendor City : | Vendor City : | Vendor City :
|  | RFQ No: R0179 COST COMPARISON REPORT | RFQ No: R0179 COST COMPARISON REPORT | BCD Date : | BCD Date : | BCD Date : | Telephone # : | Telephone # : | Telephone # : | Telephone # :
|  | RFQ No: R0179 COST COMPARISON REPORT | RFQ No: R0179 COST COMPARISON REPORT |  |  |  | Mobile # : | Mobile # : | Mobile # : | Mobile # :
PR Number : TFSPL-2324-00251 | PR Number : TFSPL-2324-00251 | PR Number : TFSPL-2324-00251 | PR Number : TFSPL-2324-00251 | PR Number : TFSPL-2324-00251 | PR Number : TFSPL-2324-00251 | PR Number : TFSPL-2324-00251 | Email : anjlemepprojects@gmail.com | Email : anjlemepprojects@gmail.com | Email : projectspioneer@gmail.com | Email : projectspioneer@gmail.com
Package / RFQ Name : HVAC work - Internation Food Hall | Package / RFQ Name : HVAC work - Internation Food Hall | Package / RFQ Name : HVAC work - Internation Food Hall | Package / RFQ Name : HVAC work - Internation Food Hall | Package / RFQ Name : HVAC work - Internation Food Hall | Package / RFQ Name : HVAC work - Internation Food Hall | Package / RFQ Name : HVAC work - Internation Food Hall | Round # : 4 (Auction) | Round # : 4 (Auction) | Round # : 4 (Auction) | Round # : 4 (Auction)
Buyer : Jogeswar Sahu | Buyer : Jogeswar Sahu | Buyer : Jogeswar Sahu | Buyer : Jogeswar Sahu | Buyer : Jogeswar Sahu | Buyer : Jogeswar Sahu | Buyer : Jogeswar Sahu | Techanical Score : | Techanical Score : | Techanical Score : | Techanical Score :
Comp. # : 4 | Comp. # : 4 | Comp. # : 4 | Comp. # : 4 | Currency :INR | Currency :INR | Currency :INR | Quotation Date : | Quotation Date : | Quotation Date : | Quotation Date :
Comp. # : 4 | Comp. # : 4 | Comp. # : 4 | Comp. # : 4 | BUDGET PRICE :.00 | BUDGET PRICE :.00 | BUDGET PRICE :.00 | Quotation Validity Date : | Quotation Validity Date : | Quotation Validity Date : | Quotation Validity Date :
Sr No. | Item Code | Item Name | Item Description | UOM | Qty | Minimum Amount | Unit Price | Amount | Unit Price | Amount
1 |  | High Side - HVAC | High Side - HVAC | NOS | 1.000 |  |  | 1,404,400.00 |  | 1,315,000.00
1 | Note: | Prices shall be based on supply, installation, testing commissioning (SITC) at site including all taxes, duties, transportation insurance etc. | Prices shall be based on supply, installation, testing commissioning (SITC) at site including all taxes, duties, transportation insurance etc.
2 | 1 | CHILLED WATER TYPE CEILING SUSPENDED AHU (AIR HANDLING UNIT) | CHILLED WATER TYPE CEILING SUSPENDED AHU (AIR HANDLING UNIT)
3 | 1.1 | CEILING SUSPENDED AHU | CEILING SUSPENDED AHU
4 |  | Supply and assembly of Ceiling Suspended Double skin cabinet type AHU Integrated (Air handling units) of following specifications | Supply and assembly of Ceiling Suspended Double skin cabinet type AHU Integrated (Air handling units) of following specifications
5 |  | Frame Structure It shall consist of 48mm Extruded Aluminium with thermal break profile. | Frame Structure It shall consist of 48mm Extruded Aluminium with thermal break profile.
6 |  | Panel 45mm + - 2mm thick double skin sandwich panels with rockwool insulation of density 64 kg m3 or PUF insulation of 48 kg m3 , The sheet thickness shall be minimum 0.6 mm for the outer skin precoated and 0.8 mm thickness for the inner skin of plain GI. | Panel 45mm + - 2mm thick double skin sandwich panels with rockwool insulation of density 64 kg m3 or PUF insulation of 48 kg m3 , The sheet thickness shall be minimum 0.6 mm for the outer skin precoated and 0.8 mm thickness for the inner skin of plain GI.
7 |  | Filtration Section It shall be provided with single stage washable type of prefilter MERV 8 first stage which shall be placed before coil section. | Filtration Section It shall be provided with single stage washable type of prefilter MERV 8 first stage which shall be placed before coil section.
8 |  | Coil Section Chilled water coil Multi row deep constructed with Aluminium fins of min 0.11mm thick 12 Fins per inch, and copper tubes of min 27 Guage thickness HYRDOPHYLLIC coated fins. Copper tube shall be min 12.5mm diameter. AHRI certified coil.The coil face area velocity shall not exceed 2.5m sec (500 fpm). | Coil Section Chilled water coil Multi row deep constructed with Aluminium fins of min 0.11mm thick 12 Fins per inch, and copper tubes of min 27 Guage thickness HYRDOPHYLLIC coated fins. Copper tube shall be min 12.5mm diameter. AHRI certified coil.The coil face area velocity shall not exceed 2.5m sec (500 fpm).
9 |  | Drain Pan Condensate drain pan shall be fabricated from 18G SS 304 powder coated, insulated with 13 mm thick closed cell elastomeric(nitrile rubber) insulation. | Drain Pan Condensate drain pan shall be fabricated from 18G SS 304 powder coated, insulated with 13 mm thick closed cell elastomeric(nitrile rubber) insulation.
10 |  | Fan Section SISW DIDW Direct drive backward curved fan. The fan section shall be provided with limt switch for safety to shut off fan during Opening of access door. Fan outlet velocity not to exceed 1600 FPM. The sound level shall not be exceed more than 60dB @ 1m from the source. Vibration isolators, Door Limit switch, as per Technical Specifications, AHU Summary Sheet and drawings. Total static pressue has to calculated by Contractor as per the configuration. | Fan Section SISW DIDW Direct drive backward curved fan. The fan section shall be provided with limt switch for safety to shut off fan during Opening of access door. Fan outlet velocity not to exceed 1600 FPM. The sound level shall not be exceed more than 60dB @ 1m from the source. Vibration isolators, Door Limit switch, as per Technical Specifications, AHU Summary Sheet and drawings. Total static pressue has to calculated by Contractor as per the configuration.
11 |  | Other Details AHU to house control box terminal box with Auto-Manual switch and incomer power terminal, with SPP, Over Undervoltage protection, shortcircuit protection and with no-nc contacts (potential free contact) to be provided for tripping on signal from Fire Dampers Fire Alarm Panel. Power cable from Terminal box to motor control cabling of required size upto the thermostat sensor etc. to be provided. Internal electrical and control wiring of AHU to be provided as factory fitted from AHU supplier. The cost shall include all necessary supports accessories required for installation. | Other Details AHU to house control box terminal box with Auto-Manual switch and incomer power terminal, with SPP, Over Undervoltage protection, shortcircuit protection and with no-nc contacts (potential free contact) to be provided for tripping on signal from Fire Dampers Fire Alarm Panel. Power cable from Terminal box to motor control cabling of required size upto the thermostat sensor etc. to be provided. Internal electrical and control wiring of AHU to be provided as factory fitted from AHU supplier. The cost shall include all necessary supports accessories required for installation.
12 |  | Contractor shall design the chilled water coil according to the following conditions | Contractor shall design the chilled water coil according to the following conditions
13 |  | a. Coil air entering temperature - 69.8°F DB | a. Coil air entering temperature - 69.8°F DB
14 |  | b. Coil air leaving temperature - 54°F DB 52.99°F WB | b. Coil air leaving temperature - 54°F DB 52.99°F WB
15 |  | c. Chilled water temperature entering - 7.0°C 44.6°F | c. Chilled water temperature entering - 7.0°C 44.6°F
16 |  | d. Chilled water temperature leaving - 12.0°C 53.6°F | d. Chilled water temperature leaving - 12.0°C 53.6°F
17 |  | e. Ambient temperature - DB - 110°F 43.3°C WB - 82°F 27.7°C | e. Ambient temperature - DB - 110°F 43.3°C WB - 82°F 27.7°C
18 |  | Make VTS Zeco Citizen | Make VTS Zeco Citizen
19 |  | Type Capacity TR ESP No. of FA | Type Capacity TR ESP No. of FA
20 |  | (Cfm) (mm WG) Rows CFM | (Cfm) (mm WG) Rows CFM
21 | a | CS AHU 4300 9.4 25 4 6 450 | CS AHU 4300 9.4 25 4 6 450 | Nos. | 2.000 | 360,000.00 | 209200.00 | 418,400.00 | 180000.00 | 360,000.00
22 |  | GENERAL NOTES | GENERAL NOTES
23 | a. | LHS RHS VALVE station location to be confirmed. | LHS RHS VALVE station location to be confirmed.
24 | b. | Fan outlet velocity - 1600 FPM | Fan outlet velocity - 1600 FPM
25 | c. | Contractor shall submit static pressure calculation for all above units to Client Consultant. | Contractor shall submit static pressure calculation for all above units to Client Consultant.
26 | d. | Any change in motor HP shall be made at no extra cost to client. | Any change in motor HP shall be made at no extra cost to client.
27 | e. | Fan efficiency shall be minimum 75% | Fan efficiency shall be minimum 75%
28 | f. | The cost shall be included liftting shifting of each equipment material with all necesaary arrnagement. Also, it shall be included the cost of scaffloding required for Installation of such material equipment. | The cost shall be included liftting shifting of each equipment material with all necesaary arrnagement. Also, it shall be included the cost of scaffloding required for Installation of such material equipment.
29 | 3 | VENTILATION SYSTEM | VENTILATION SYSTEM
30 | 3.1 | KITCHEN EXHAUST AIR FAN | KITCHEN EXHAUST AIR FAN
31 |  | SITC of Cabinet type SISW Centrifugal Blower, Direct Drive, Statically Dynamically Balanced, Backward Curved Impeller fan, Dunlop Anti- Vibration Pads etc. Motor should be outside stream with TEFC squirrel cage, weather protection shield, IP 65 rating with Class H Insulation motor, suitable for 3phase, 415volts, 50hz power supply. Sound level should be 65dB @ 3mtr distance. Fan should be painted with 2 coat of zinc chromate primer and 2 coats Epoxy paint. The quote shall include with MS frame and required accessories. (Vendor to crosscheck static pressure calculation). | SITC of Cabinet type SISW Centrifugal Blower, Direct Drive, Statically Dynamically Balanced, Backward Curved Impeller fan, Dunlop Anti- Vibration Pads etc. Motor should be outside stream with TEFC squirrel cage, weather protection shield, IP 65 rating with Class H Insulation motor, suitable for 3phase, 415volts, 50hz power supply. Sound level should be 65dB @ 3mtr distance. Fan should be painted with 2 coat of zinc chromate primer and 2 coats Epoxy paint. The quote shall include with MS frame and required accessories. (Vendor to crosscheck static pressure calculation).
32 |  | Make Waves Systems Air Nicotra Humidin | Make Waves Systems Air Nicotra Humidin
33 | a | 11100CFM, 65mm TSP | 11100CFM, 65mm TSP | No. | 1.000 | 255,000.00 | 272500.00 | 272,500.00 | 255000.00 | 255,000.00
34 | 3.2 | KITCHEN DRY SCRUBBER | KITCHEN DRY SCRUBBER
35 |  | SITC of Dry scrubber – Electrostatic Air cleaner with starter panel as per specifications, suitable for following capacities, including electrical starter panel . The Air filtration efficiency should be between 90 to 95% units shall be staked one above other or side by side as per site requirement, if vendor will propose multiple units. | SITC of Dry scrubber – Electrostatic Air cleaner with starter panel as per specifications, suitable for following capacities, including electrical starter panel . The Air filtration efficiency should be between 90 to 95% units shall be staked one above other or side by side as per site requirement, if vendor will propose multiple units.
36 |  | Finishing - Power coated, Dark Blue | Finishing - Power coated, Dark Blue
37 |  | Operating voltage - 220 Vac+ -10%, 50 Hz (Single phase) | Operating voltage - 220 Vac+ -10%, 50 Hz (Single phase)
38 |  | Features - Short circuit, arc protection and auto restore power supply, BMS (Building Management System) terminals provided, Auto power cut-off when door is opened, Indicator LEDs for normal or wash indicator, Set of Terminals for remote LED normal or wash indicator | Features - Short circuit, arc protection and auto restore power supply, BMS (Building Management System) terminals provided, Auto power cut-off when door is opened, Indicator LEDs for normal or wash indicator, Set of Terminals for remote LED normal or wash indicator
39 |  | Efficiency - Upto 95%, meets NIOSH 5026 Oil Mist Test | Efficiency - Upto 95%, meets NIOSH 5026 Oil Mist Test
40 |  | Particle Size - Collects particles as small as 0.01 microns | Particle Size - Collects particles as small as 0.01 microns
41 |  | Motor - Sealead ball bearings UL, single phase. | Motor - Sealead ball bearings UL, single phase.
42 |  | Cell - Ionizing voltage - 12 KVdc | Cell - Ionizing voltage - 12 KVdc
43 |  | Collector voltage - 6 KVdc | Collector voltage - 6 KVdc
44 |  | One cell comprising of 9 ionizing wires and 25 collection plates | One cell comprising of 9 ionizing wires and 25 collection plates
45 |  | Controls - Auto cut-off when door is opened. Indicator lights for fault, normal or wash function. | Controls - Auto cut-off when door is opened. Indicator lights for fault, normal or wash function.
46 |  | Pre-filter - Aluminium mesh, washable Dry contact for BMS. | Pre-filter - Aluminium mesh, washable Dry contact for BMS.
47 |  | Make Rydair Espair | Make Rydair Espair
48 |  | CFM - 5550 | CFM - 5550 | Nos. | 2.000 | 469,000.00 | 234500.00 | 469,000.00 | 235000.00 | 470,000.00
49 | 3.3 | KITCHEN AIR-WASHER FAN | KITCHEN AIR-WASHER FAN
50 |  | SITC of Cabinet type Air-washer fan with Centrifugal Blower, Belt Direct Drive, Statically Dynamically Balanced, Backward Curved Impeller, MERV 8 filter, Dunlop Anti- Vibration Pads, filters,Water Circulation Pump, etc. Motor should be TEFC squirrel cage, IP 55 rating with Class F Insulation, suitable for 3phase, 415volts, 50hz power supply. Sound level should be 65dB @ 3mtr distance. Fan should be painted with 2 coat of zinc chromate primer and 2 coats Epoxy paint. MERV 8 G4 pleated pre-filters should be made of 100% synthetic media to capture common airborne contaminants as per ASHRAE Standard 52.2. (Vendor to crosscheck static pressure calculation) Air Washer will be supplied with Water Circulation Pump, Water Inlet Connection, Overflow, Drain Outlet with 3 8” Brass Spray Nozzles, Interconnected Piping for Air Washer. | SITC of Cabinet type Air-washer fan with Centrifugal Blower, Belt Direct Drive, Statically Dynamically Balanced, Backward Curved Impeller, MERV 8 filter, Dunlop Anti- Vibration Pads, filters,Water Circulation Pump, etc. Motor should be TEFC squirrel cage, IP 55 rating with Class F Insulation, suitable for 3phase, 415volts, 50hz power supply. Sound level should be 65dB @ 3mtr distance. Fan should be painted with 2 coat of zinc chromate primer and 2 coats Epoxy paint. MERV 8 G4 pleated pre-filters should be made of 100% synthetic media to capture common airborne contaminants as per ASHRAE Standard 52.2. (Vendor to crosscheck static pressure calculation) Air Washer will be supplied with Water Circulation Pump, Water Inlet Connection, Overflow, Drain Outlet with 3 8” Brass Spray Nozzles, Interconnected Piping for Air Washer.
51 |  | Make Waves Systems Air Nicotra Humidin | Make Waves Systems Air Nicotra Humidin
52 | a | 8600 CFM, 50mm TSP | 8600 CFM, 50mm TSP | No | 1.000 | 230,000.00 | 244500.00 | 244,500.00 | 230000.00 | 230,000.00
2 |  | Low Side - HVAC |  | NOS | 1.000 |  |  | 1,622,000.00 |  | 1,641,100.00
53 | 2 | CHILLED WATER PIPING | CHILLED WATER PIPING
54 | 2.1 | CHW PIPE | CHW PIPE
55 |  | SITC of MS Heavy duty class C ERW Chilled Water pipe conforming to IS 1239 Part I class ‘C’ heavy and fitting shall be conforming to ASTM A-105,3000lbs socket weld end (up to 50mm) 1S 1239 Part-II HEAVY ASTM A-234 WPB, Gr.B butt weld fitting ( above 50NB pipe size). The cost also shall cover primer painted including bends, tees, MS supports, PUFF saddles, anchor fasteners, steel angles and any other material required to complete the work. The piping flange connection bolts, washers and nuts should be hot dipped galvanised. Flourscent Plastic Sticker paint shall be applied to indicate Water flow directions. Only End flanges to be used for capping of pipes. Table E of BS code for flange thickness to be adhered. | SITC of MS Heavy duty class C ERW Chilled Water pipe conforming to IS 1239 Part I class ‘C’ heavy and fitting shall be conforming to ASTM A-105,3000lbs socket weld end (up to 50mm) 1S 1239 Part-II HEAVY ASTM A-234 WPB, Gr.B butt weld fitting ( above 50NB pipe size). The cost also shall cover primer painted including bends, tees, MS supports, PUFF saddles, anchor fasteners, steel angles and any other material required to complete the work. The piping flange connection bolts, washers and nuts should be hot dipped galvanised. Flourscent Plastic Sticker paint shall be applied to indicate Water flow directions. Only End flanges to be used for capping of pipes. Table E of BS code for flange thickness to be adhered.
56 |  | Make Jindal Hissar TATA | Make Jindal Hissar TATA
57 | b | F 25 mm | F 25 mm | Rmt | 0.000 | .00 | 0.00 | .00 | 0.00 | .00
58 | c | F 32 mm | F 32 mm | Rmt | 0.000 | .00 | 0.00 | .00 | 0.00 | .00
59 | d | F 40 mm | F 40 mm | Rmt | 60.000 | 61,200.00 | 1020.00 | 61,200.00 | 1150.00 | 69,000.00
60 | 2.2 | CHILLED WATER PIPING INSULATION - INTERNAL USE | CHILLED WATER PIPING INSULATION - INTERNAL USE
61 |  | SITC of insulation for chilled water. piping. For internal pipe - Stick 25mm thick Nitrile rubber class O Closed cell nitrile rubber with anti-microbial coating on it. Insulation shall have Thermal conductivity of 0.033 W (m.K) and water vapor permeance of 0.10. Joints should be sealed with 50 mm wide 3 mm thick self adhesive tape and putting PVC bands at all supports. Further, insulation shall be wrapped with 7 mil cloth with required adhesive on it. | SITC of insulation for chilled water. piping. For internal pipe - Stick 25mm thick Nitrile rubber class O Closed cell nitrile rubber with anti-microbial coating on it. Insulation shall have Thermal conductivity of 0.033 W (m.K) and water vapor permeance of 0.10. Joints should be sealed with 50 mm wide 3 mm thick self adhesive tape and putting PVC bands at all supports. Further, insulation shall be wrapped with 7 mil cloth with required adhesive on it.
62 |  | Make Armaflex K-flex | Make Armaflex K-flex
63 | a | F 25 mm | F 25 mm | Rmt | 0.000 | .00 | 0.00 | .00 | 0.00 | .00
64 | b | F 32 mm | F 32 mm | Rmt | 0.000 | .00 | 0.00 | .00 | 0.00 | .00
65 | c | F 40 mm | F 40 mm | Rmt | 60.000 | 27,000.00 | 450.00 | 27,000.00 | 450.00 | 27,000.00
66 | 2.3 | BALL VALVE | BALL VALVE
67 |  | SITC of following sizes of Ball Valve consist of Cap, Brass Body, Rated for 150 psi SWP, 600 psi WOG Pressure Two-piece construction; with brass body, regular port, B-16 chrome-plated ball and stem, replaceable “Teflon” or “TFE” seats and seals, blowout-proof stem, vinyl covered steel handle, threaded or soldered ends and extended stem for insulated piping. Same valve shall be used as a Drain valve. | SITC of following sizes of Ball Valve consist of Cap, Brass Body, Rated for 150 psi SWP, 600 psi WOG Pressure Two-piece construction; with brass body, regular port, B-16 chrome-plated ball and stem, replaceable “Teflon” or “TFE” seats and seals, blowout-proof stem, vinyl covered steel handle, threaded or soldered ends and extended stem for insulated piping. Same valve shall be used as a Drain valve.
68 |  | Make Zoloto Audco Kitz | Make Zoloto Audco Kitz
69 | a | F 25 mm | F 25 mm | Nos. | 4.000 | 7,400.00 | 1850.00 | 7,400.00 | 2050.00 | 8,200.00
70 | b | F 32 mm | F 32 mm | Nos. | 0.000 | .00 | 0.00 | .00 | 0.00 | .00
71 | c | F 40 mm | F 40 mm | Nos. | 12.000 | 41,400.00 | 3450.00 | 41,400.00 | 3550.00 | 42,600.00
72 | 2.4 | BALL VALVE WITH Y-STRAINER | BALL VALVE WITH Y-STRAINER
73 |  | SITC of following sizes of Brass Ball Valve with Y-Strainer consist of Cap, Brass Body, Rated for 150 psi SWP, 600 psi WOG Pressure Two-piece construction; with brass body, regular port, B-16 chrome-plated ball and stem, replaceable “Teflon” or “TFE” seats and seals, blowout-proof stem, vinyl covered steel handle, threaded or soldered ends and extended stem for insulated piping. Filter element shall be of non magnetic SS sheet with perforation. | SITC of following sizes of Brass Ball Valve with Y-Strainer consist of Cap, Brass Body, Rated for 150 psi SWP, 600 psi WOG Pressure Two-piece construction; with brass body, regular port, B-16 chrome-plated ball and stem, replaceable “Teflon” or “TFE” seats and seals, blowout-proof stem, vinyl covered steel handle, threaded or soldered ends and extended stem for insulated piping. Filter element shall be of non magnetic SS sheet with perforation.
74 |  | Make Zoloto Audco Kitz | Make Zoloto Audco Kitz
75 | a | F 25 mm | F 25 mm | Nos. | 0.000 | .00 | 0.00 | .00 | 0.00 | .00
76 | b | F 32 mm | F 32 mm | Nos. | 0.000 | .00 | 0.00 | .00 | 0.00 | .00
77 | c | F 40 mm | F 40 mm | Nos. | 2.000 | 7,700.00 | 3950.00 | 7,900.00 | 3850.00 | 7,700.00
78 | 2.5 | PIBCV VALVES | PIBCV VALVES
79 |  | SITC of Pressure Independent Balancing cum Control Valves (PIBCV) including integrated motorised control valve and balancing device for combined flow and water balancing requirement. Valve body to be rated for PN 16. The valve design flow rate should be factory calibrated with + - 5% flow accuracy. Valve shall have necessary measuring ports, drain port, flanges etc., Valve shall also provide temperature sensor with necessary cabling (min 2mtr length to be considered with each valve). The balancing to be done through microprocessor based hand held terminal POT and the same results shall be furnished in the water balancing report as part of commissioning report and handing over manual. | SITC of Pressure Independent Balancing cum Control Valves (PIBCV) including integrated motorised control valve and balancing device for combined flow and water balancing requirement. Valve body to be rated for PN 16. The valve design flow rate should be factory calibrated with + - 5% flow accuracy. Valve shall have necessary measuring ports, drain port, flanges etc., Valve shall also provide temperature sensor with necessary cabling (min 2mtr length to be considered with each valve). The balancing to be done through microprocessor based hand held terminal POT and the same results shall be furnished in the water balancing report as part of commissioning report and handing over manual.
80 |  | Make Oventrop Siemens Danfoss | Make Oventrop Siemens Danfoss
81 | a | F 25 mm | F 25 mm | Nos. | 0.000 | .00 | 0.00 | .00 | 0.00 | .00
82 | b | F 32 mm | F 32 mm | Nos. | 0.000 | .00 | 0.00 | .00 | 0.00 | .00
83 | c | F 40 mm | F 40 mm | Nos. | 2.000 | 57,000.00 | 35500.00 | 71,000.00 | 28500.00 | 57,000.00
84 | 2.6 | Auto Air Vent Valves | Auto Air Vent Valves
85 |  | Make Anergy Flamco | Make Anergy Flamco
86 |  | Providing and fitting Auto Vent Valves. | Providing and fitting Auto Vent Valves.
87 | a | SITC of Auto air vent in each risers common headers AHU. 3 4 auto vent valves at each coil riser header. | SITC of Auto air vent in each risers common headers AHU. 3 4 auto vent valves at each coil riser header. | Nos. | 4.000 | 4,800.00 | 1250.00 | 5,000.00 | 1200.00 | 4,800.00
88 | 2.7 | SITC of Pressure gauges Thermometers | SITC of Pressure gauges Thermometers
89 |  | Make H Guru Waree | Make H Guru Waree
90 |  | Necessary pressure gauges and thermometers 4 Dial type. | Necessary pressure gauges and thermometers 4 Dial type.
91 | a | Water Pressure gauges 150mm dial complete with gauge valves, mounting, fittings and copper tubing extension wherever required. Pressure gauges Range 0-10 Kg CM2 | Water Pressure gauges 150mm dial complete with gauge valves, mounting, fittings and copper tubing extension wherever required. Pressure gauges Range 0-10 Kg CM2 | Nos. | 4.000 | 5,800.00 | 1450.00 | 5,800.00 | 1850.00 | 7,400.00
92 | b | Thermometers of the mercury in glass stem type and copper separable well complete with guard etc., of industrial grade mounting on water lines. Length 9 12 inches, Thermometer, Range 0-50 deg C | Thermometers of the mercury in glass stem type and copper separable well complete with guard etc., of industrial grade mounting on water lines. Length 9 12 inches, Thermometer, Range 0-50 deg C | Nos. | 4.000 | 4,200.00 | 1350.00 | 5,400.00 | 1050.00 | 4,200.00
93 | c | Thermowells | Thermowells | Nos. | 8.000 | 2,000.00 | 300.00 | 2,400.00 | 250.00 | 2,000.00
94 | d | SITC of Brass Test Plug of industrial grade mounting on water | SITC of Brass Test Plug of industrial grade mounting on water | Nos. | 0.000 | .00 | 0.00 | .00 | 0.00 | .00
95 | 2.8 | INSULATED CONDENSATE DRAIN PIPE | INSULATED CONDENSATE DRAIN PIPE
96 |  | SITC of UPVC pipes of following sizes for drain with necessary supports and fittings such as elbows, tees reducers etc. Condensate drain piping shall be complying to IS 4985 Class 3 UPVC pipe. Solvent cement complying with ASTM D2564 shall be used for joints. The insulation line to be insulated with nitrile rubber insulation of thickness 9mm and wrapped by weather proof protection tape. The Pipe wherever concealed should also have a parallel line as a standby arrangement in case of block of primary pipe. | SITC of UPVC pipes of following sizes for drain with necessary supports and fittings such as elbows, tees reducers etc. Condensate drain piping shall be complying to IS 4985 Class 3 UPVC pipe. Solvent cement complying with ASTM D2564 shall be used for joints. The insulation line to be insulated with nitrile rubber insulation of thickness 9mm and wrapped by weather proof protection tape. The Pipe wherever concealed should also have a parallel line as a standby arrangement in case of block of primary pipe.
97 |  | Make Supreme, Prince, Astral | Make Supreme, Prince, Astral
98 | a | F 25 mm | F 25 mm | Rmt | 15.000 | 2,100.00 | 170.00 | 2,550.00 | 140.00 | 2,100.00
99 | b | F 32 mm | F 32 mm | Rmt | 20.000 | 3,200.00 | 210.00 | 4,200.00 | 160.00 | 3,200.00
100 | c | F 40 mm | F 40 mm | Rmt | 0.000 | .00 | 550.00 | .00 | 0.00 | .00
101 |  | NOTES FOR PIPING | NOTES FOR PIPING
102 | a | Piping connection shall be socket welded up to 50nb size and shall be butt weld above 50nb pipe size. Pipe flanges shall be confirming to ASTM A-105 # 150 SORF and flange dimension should be in accordance with ASME ANSI B 16.5 (150 SORF), fitting to fitting welding is not allowed. Nozzle connections thredolets weldolets are not allowed by puncturing the pipe. Only equal unequal Tee’s shall be used for branch connection from header. Socket weld end Tee shall be used for branch connection (up-to -50nb pipe size) w.r.t to pressure gauge temperature gauge Air vent Drain point etc. | Piping connection shall be socket welded up to 50nb size and shall be butt weld above 50nb pipe size. Pipe flanges shall be confirming to ASTM A-105 # 150 SORF and flange dimension should be in accordance with ASME ANSI B 16.5 (150 SORF), fitting to fitting welding is not allowed. Nozzle connections thredolets weldolets are not allowed by puncturing the pipe. Only equal unequal Tee’s shall be used for branch connection from header. Socket weld end Tee shall be used for branch connection (up-to -50nb pipe size) w.r.t to pressure gauge temperature gauge Air vent Drain point etc.
103 | b | Cover all open pipe ends with muslin cloth during construction | Cover all open pipe ends with muslin cloth during construction
104 | c | Pipe cleaning chemical treatment as per specs shall be included in the piping cost. | Pipe cleaning chemical treatment as per specs shall be included in the piping cost.
105 | d | Unit rates for all indicated sizes of pipes valves shall be furnished. | Unit rates for all indicated sizes of pipes valves shall be furnished.
106 | e | Cleaning Painting of pipe before insulation shall be included in piping cost. | Cleaning Painting of pipe before insulation shall be included in piping cost.
107 | f | The piping support should be as per tender specification and additional supports are to be provided Contractor as decided by Consultant. | The piping support should be as per tender specification and additional supports are to be provided Contractor as decided by Consultant.
108 | g | All the valves shall be insulated with the same material as that of Chilled water pipng and cost of insulation for valves shall be considered. | All the valves shall be insulated with the same material as that of Chilled water pipng and cost of insulation for valves shall be considered.
109 | 3.4 | FRAMEWORK FOR FANS | FRAMEWORK FOR FANS
110 |  | Supply, Fabrication and Installation of MS frame using channels angle iron sections as required for mounting of ventilation fans scrubber in areas shown in the layout. The frame work shall be applied with red oxide primer and thereafter, two coats of enamel paint of approved colour. The general arrangement drawing for frame work shall be got approved from the Architects Structural Engineers prior to commencement of fabrication. | Supply, Fabrication and Installation of MS frame using channels angle iron sections as required for mounting of ventilation fans scrubber in areas shown in the layout. The frame work shall be applied with red oxide primer and thereafter, two coats of enamel paint of approved colour. The general arrangement drawing for frame work shall be got approved from the Architects Structural Engineers prior to commencement of fabrication. | Kg | 350.000 | 71,750.00 | 205.00 | 71,750.00 | 230.00 | 80,500.00
111 |  | Note | Note
112 | a. | Fan outlet velocity - 1600 FPM | Fan outlet velocity - 1600 FPM
113 | b. | All cabinet fans should have plenum section. | All cabinet fans should have plenum section.
114 | c. | Fresh air fan should to have 6mm thick synthetic media washable filter with framework. | Fresh air fan should to have 6mm thick synthetic media washable filter with framework.
115 | d. | Contractor shall submit static pressure calculation for all above units to Client Consultant for their approval. Also, the total static drops across the systems shall cover the overall length from suction discharge to grille (inside the outlet). | Contractor shall submit static pressure calculation for all above units to Client Consultant for their approval. Also, the total static drops across the systems shall cover the overall length from suction discharge to grille (inside the outlet).
116 | e. | Any change in motor HP or coil selection shall be made at no extra cost to client. | Any change in motor HP or coil selection shall be made at no extra cost to client.
117 | f. | Fan efficiency shall be minimum 75% | Fan efficiency shall be minimum 75%
118 | g. | The cost shall be included liftting shifting of each equipment material with all necesaary arrnagement. Also, it shall be included the cost of scaffloding required for Installation of such material equipment. | The cost shall be included liftting shifting of each equipment material with all necesaary arrnagement. Also, it shall be included the cost of scaffloding required for Installation of such material equipment.
119 |  | SUB-TOTAL | SUB-TOTAL
120 | 4 | SHEET METAL WORKS | SHEET METAL WORKS
121 | 4.1 | FACTORY FABRICATED G.I RECTANGULAR DUCT | FACTORY FABRICATED G.I RECTANGULAR DUCT
122 |  | Supply, Fabrication, Testing, and Commissioning of Factory Fabricated GI Sheet Metal 120GSM Rectangular boxed ducting, Plenums, Cowls, Elbows with turning vanes, Splitters, Reducers, Flanges, Collars etc as per IS and Installaton as per SMACNA and IS 655 standards, The complete ducting shall be provided with MS Supports, Rods, Angles, Flanges, Bracing, Rubber Gaskets, Wooden frames, Canvas Connections, etc. as per drawings and specifications. | Supply, Fabrication, Testing, and Commissioning of Factory Fabricated GI Sheet Metal 120GSM Rectangular boxed ducting, Plenums, Cowls, Elbows with turning vanes, Splitters, Reducers, Flanges, Collars etc as per IS and Installaton as per SMACNA and IS 655 standards, The complete ducting shall be provided with MS Supports, Rods, Angles, Flanges, Bracing, Rubber Gaskets, Wooden frames, Canvas Connections, etc. as per drawings and specifications.
123 |  | GI Sheet Makes Tata, Jindal, SAIL, Ispat | GI Sheet Makes Tata, Jindal, SAIL, Ispat
124 |  | Make Rola Star, Zeco Ductofab | Make Rola Star, Zeco Ductofab
125 | a | 18 Gauge GI Sheet Metal Duct (Above 2251mm Plenum) | 18 Gauge GI Sheet Metal Duct (Above 2251mm Plenum) | Sq.mtr | 25.000 | 40,750.00 | 1630.00 | 40,750.00 | 1650.00 | 41,250.00
126 | b | 20 Gauge GI Sheet Metal Duct (1501-2250mm) for Kitchen Exhaust Works | 20 Gauge GI Sheet Metal Duct (1501-2250mm) for Kitchen Exhaust Works | Sq.mtr | 125.000 | 180,000.00 | 1440.00 | 180,000.00 | 1450.00 | 181,250.00
127 | c | 22 Gauge GI Sheet Metal Duct (751-1500mm) | 22 Gauge GI Sheet Metal Duct (751-1500mm) | Sq.mtr | 20.000 | 26,800.00 | 1340.00 | 26,800.00 | 1350.00 | 27,000.00
128 | d | 24 Gauge GI Sheet Metal Duct (0-750mm) | 24 Gauge GI Sheet Metal Duct (0-750mm) | Sq.mtr | 200.000 | 228,000.00 | 1140.00 | 228,000.00 | 1150.00 | 230,000.00
129 | 4.2 | G.I ELLIPTICAL DUCTING | G.I ELLIPTICAL DUCTING
130 |  | Supply, Fabrication, erection, testing commissioning of factory fabricated GI sheet metal Elliptical ducting complete with turning vanes, neoprene rubber gasket, external painting, duct supports (gripple support eye bolt threaded rod), hangers etc. as per drawings and specifications. All ducts has to be powder coated by HVAC contractor, sample to be presented for the validation for Client. Color Code shall be provided by Client Arch. | Supply, Fabrication, erection, testing commissioning of factory fabricated GI sheet metal Elliptical ducting complete with turning vanes, neoprene rubber gasket, external painting, duct supports (gripple support eye bolt threaded rod), hangers etc. as per drawings and specifications. All ducts has to be powder coated by HVAC contractor, sample to be presented for the validation for Client. Color Code shall be provided by Client Arch.
131 | a | 20 Gauge GI Sheet Metal Duct (1501-2250mm) | 20 Gauge GI Sheet Metal Duct (1501-2250mm) | Sq.mtr | 0.000 | .00 | 2250.00 | .00 | 0.00 | .00
132 | b | 22 Gauge GI Sheet Metal Duct (751-1500mm) | 22 Gauge GI Sheet Metal Duct (751-1500mm) | Sq.mtr | 80.000 | 123,200.00 | 1540.00 | 123,200.00 | 1550.00 | 124,000.00
133 | c | 24 Gauge GI Sheet Metal Duct (0-750mm) | 24 Gauge GI Sheet Metal Duct (0-750mm) | Sq.mtr | 75.000 | 100,500.00 | 1340.00 | 100,500.00 | 1350.00 | 101,250.00
134 | 4.3 | EXTRUDED ALUMINIUM CEILING GRILLES | EXTRUDED ALUMINIUM CEILING GRILLES
135 |  | Supply, Installation, Testing and Balancing of Powder coated aluminium linear supply air grilles complete with removable inner core as per approved shop drawing and specifications. The area of grille can be of any geometrical shape (Square rectangular Linear). The grilles shall be with 15 30 45° deflections as per requirement. The Colour shall be decided and approved by client and architect. | Supply, Installation, Testing and Balancing of Powder coated aluminium linear supply air grilles complete with removable inner core as per approved shop drawing and specifications. The area of grille can be of any geometrical shape (Square rectangular Linear). The grilles shall be with 15 30 45° deflections as per requirement. The Colour shall be decided and approved by client and architect.
136 |  | Make Cosmos, Air Master System Air | Make Cosmos, Air Master System Air
137 | a | Linear Square Rectangular Grille | Linear Square Rectangular Grille | Sq.mtr | 7.000 | 42,000.00 | 6050.00 | 42,350.00 | 6000.00 | 42,000.00
138 | 4.4 | EXTRUDED ALUMINIUM ROUND AIR DIFFUSER | EXTRUDED ALUMINIUM ROUND AIR DIFFUSER
139 |  | Supply, Installation, Testing and Balancing of Powder coated aluminium supply air round diffuser complete with removable inner core as per approved shop drawing and specifications. The diffuser shall also be provided with Black painted GI opposed blade damper (OBD) of required sizes. Each diffuser shall have double inlet rings to connect flexible ducts. The diffuser shall be suitable for gypsum grid ceiling. The Colour shall be decided and approved by client and architect. | Supply, Installation, Testing and Balancing of Powder coated aluminium supply air round diffuser complete with removable inner core as per approved shop drawing and specifications. The diffuser shall also be provided with Black painted GI opposed blade damper (OBD) of required sizes. Each diffuser shall have double inlet rings to connect flexible ducts. The diffuser shall be suitable for gypsum grid ceiling. The Colour shall be decided and approved by client and architect.
140 |  | Make Cosmos Ruskin Titus Air Master | Make Cosmos Ruskin Titus Air Master
141 |  | ROUND DIFFUSER FOR GYPSUM CEILING | ROUND DIFFUSER FOR GYPSUM CEILING
142 | a | Supply Air Diffuser with OBD - Neck Size 325Fmm | Supply Air Diffuser with OBD - Neck Size 325Fmm | Nos. | 15.000 | 37,500.00 | 2500.00 | 37,500.00 | 2500.00 | 37,500.00
143 | b | Supply Air Diffuser with OBD - Neck Size 225Fmm | Supply Air Diffuser with OBD - Neck Size 225Fmm | Nos. | 7.000 | 15,750.00 | 2250.00 | 15,750.00 | 2300.00 | 16,100.00
144 | c | Return Air Diffuser without OBD | Return Air Diffuser without OBD | Nos. | 3.000 | 5,850.00 | 1950.00 | 5,850.00 | 2000.00 | 6,000.00
145 | 4.5 | SS EXHAUST AND FRESH AIR GRILLES | SS EXHAUST AND FRESH AIR GRILLES
146 |  | SITC of 18G S.S 304 Grills adjustable Double Deflector With S.S Volume Control Dampers. Grills to be of Double Deflection Type for ease of deflection on all sides and to have necessary built in Dampers for adjustable nature. | SITC of 18G S.S 304 Grills adjustable Double Deflector With S.S Volume Control Dampers. Grills to be of Double Deflection Type for ease of deflection on all sides and to have necessary built in Dampers for adjustable nature.
147 |  | Make Carryaire System Air Dynacraft Air Master | Make Carryaire System Air Dynacraft Air Master
148 | a | Linear Square Rectangular Grille | Linear Square Rectangular Grille | Sq.mtr | 1.000 | 10,500.00 | 11400.00 | 11,400.00 | 10500.00 | 10,500.00
149 | 4.6 | EXTRUDED ALUMINIUM LOUVER with BIRD SCREEN | EXTRUDED ALUMINIUM LOUVER with BIRD SCREEN
150 |  | SITC of Aluminium extruded powder coated Louver with four side flanges, wire mesh bird screen etc. | SITC of Aluminium extruded powder coated Louver with four side flanges, wire mesh bird screen etc. | Sq.mtr | 0.000 | .00 | 0.00 | .00 | 0.00 | .00
151 | 4.7 | OPPOSED BLADE DAMPER | OPPOSED BLADE DAMPER
152 |  | SITC of Aluminium Opposed blade dampers black powder coated vertical blades type for supply air collar. The damper should be gear operated type. | SITC of Aluminium Opposed blade dampers black powder coated vertical blades type for supply air collar. The damper should be gear operated type. | Sq.mtr | 2.000 | 8,500.00 | 4250.00 | 8,500.00 | 4500.00 | 9,000.00
153 |  | Make Cosmos, Air Master System Air | Make Cosmos, Air Master System Air
154 | 4.8 | DOOR TRANSFER GRILLE | DOOR TRANSFER GRILLE
155 |  | SITC of Aluminium extruded powder coated Door transfer grills. | SITC of Aluminium extruded powder coated Door transfer grills.
156 |  | Door transfer grille (Back to Back) | Door transfer grille (Back to Back) | Sq.mtr | 1.000 | 5,640.00 | 5640.00 | 5,640.00 | 5750.00 | 5,750.00
157 |  | Make Cosmos, Air Master System Air | Make Cosmos, Air Master System Air
158 | 4.9 | MULTI LEAF VOLUME CONTROL DAMPER | MULTI LEAF VOLUME CONTROL DAMPER
159 |  | SITC of opposed blade aerofoil type 1.2 mm thick Anodized Aluminium volume control dampers for ducts shall be provided with concealed gears, plastic operator and quadrants for manual control of volume of air flow and for proper balancing of the air distribution system as per the approved shop drawings and specifications. | SITC of opposed blade aerofoil type 1.2 mm thick Anodized Aluminium volume control dampers for ducts shall be provided with concealed gears, plastic operator and quadrants for manual control of volume of air flow and for proper balancing of the air distribution system as per the approved shop drawings and specifications. | Sq.mtr | 5.000 | 42,250.00 | 8450.00 | 42,250.00 | 8500.00 | 42,500.00
160 |  | Make Cosmos, Air Master System Air | Make Cosmos, Air Master System Air
161 | 4.10 | CURTAIN TYPE FIRE DAMPER | CURTAIN TYPE FIRE DAMPER
162 |  | SITC of curtain type fire dampers consist of 16G GI frame, 20G GI interlocking blades secured with SS springs, blades outside airstream clamped with fusible link UL-555 listed with melting point 165 225°F, etc; as per the approved shop drawings and specifications. | SITC of curtain type fire dampers consist of 16G GI frame, 20G GI interlocking blades secured with SS springs, blades outside airstream clamped with fusible link UL-555 listed with melting point 165 225°F, etc; as per the approved shop drawings and specifications.
163 |  | Make Cosmos, Air Master System Air | Make Cosmos, Air Master System Air
164 | a | Bare fire dampers | Bare fire dampers | Sq.mtr | 0.000 | .00 | 0.00 | .00 | 0.00 | .00
165 | b | Fusible link as per specification UL 555 and CBRI approved | Fusible link as per specification UL 555 and CBRI approved | Nos. | 0.000 | .00 | 0.00 | .00 | 0.00 | .00
166 | 4.11 | DISC VALVE | DISC VALVE
167 |  | SITC of Aluminium powder coated Disc valve suitable for exhausting toilet foul air, comprising of an adjustable centre cone and coupling sleeve made of Aluminium sheet duly epoxy painted with approved color. | SITC of Aluminium powder coated Disc valve suitable for exhausting toilet foul air, comprising of an adjustable centre cone and coupling sleeve made of Aluminium sheet duly epoxy painted with approved color.
168 |  | Make Cosmos, Air Master System Air | Make Cosmos, Air Master System Air
169 | a | 150mmF | 150mmF | Nos. | 0.000 | .00 | 0.00 | .00 | 0.00 | .00
170 | 4.12 | CANVAS CONNECTION | CANVAS CONNECTION
171 |  | SITC of Flexible connections between mouth piece of Fan and initial piece of ducting with inspection zip. Flexible connections shall be double thickness non-flammable material (Fire retardant type). | SITC of Flexible connections between mouth piece of Fan and initial piece of ducting with inspection zip. Flexible connections shall be double thickness non-flammable material (Fire retardant type).
172 | a | For AHU | For AHU | Nos | 2.000 | 5,000.00 | 2650.00 | 5,300.00 | 2500.00 | 5,000.00
173 | b | For Ventilation Fan | For Ventilation Fan | Nos | 4.000 | 10,000.00 | 2650.00 | 10,600.00 | 2500.00 | 10,000.00
174 |  | NOTES | NOTES
175 |  | The ducting support should be as per tender specification and additional supports are to be provided by Contractor as decided by Consultant. | The ducting support should be as per tender specification and additional supports are to be provided by Contractor as decided by Consultant.
176 |  | Muslin cloth cover for all air outlets during construction. | Muslin cloth cover for all air outlets during construction.
177 |  | Pressure testing of complete duct work as per DW SMACNA standard. | Pressure testing of complete duct work as per DW SMACNA standard.
178 |  | Silicon sealant for longitudinal transverse joints as per specification. | Silicon sealant for longitudinal transverse joints as per specification.
179 |  | Diffusers grilles shall be powder coated as per color approved by Architect. | Diffusers grilles shall be powder coated as per color approved by Architect.
180 |  | SUB-TOTAL | SUB-TOTAL
181 | 5 | THERMAL ACOUSTIC INSULATION | THERMAL ACOUSTIC INSULATION
182 | 5.1 | THERMAL INSULATION | THERMAL INSULATION
183 |  | Supply fixing of Thermal insulation for supply air duct using 19mm thick class O BS 476 Part 6-7 FM Approved nitrile rubber elastomeric insulation thermal conductivity of 0.033 (W (M·K)) and water vapor permeance of 0.10 at 0°C for air conditioning ducting. Joints should be sealed with 50 mm wide 3 mm thick self adhesive tape. The duct shall be stick with recommended adhesive. | Supply fixing of Thermal insulation for supply air duct using 19mm thick class O BS 476 Part 6-7 FM Approved nitrile rubber elastomeric insulation thermal conductivity of 0.033 (W (M·K)) and water vapor permeance of 0.10 at 0°C for air conditioning ducting. Joints should be sealed with 50 mm wide 3 mm thick self adhesive tape. The duct shall be stick with recommended adhesive. | Sq.mtr | 350.000 | 226,800.00 | 648.00 | 226,800.00 | 650.00 | 227,500.00
184 |  | Make Armaflex K-flex | Make Armaflex K-flex
185 | 5.2 | ACOUSTIC INSULATION | ACOUSTIC INSULATION
186 |  | Supply fixing acoustic insulation for ducting using Class 1 closed cell elastomeric insulation of 10mm thick Nitrile rubber insulation adhesive, longitudinal transverse joints sealed with adhesive in neat clean manner. Material shall be processed Nitrile Rubber foam with anti-microbial protection. Insulation shall have thermal conductivity of 0.047 W (m.K) and density of 140 - 180 kg m³. | Supply fixing acoustic insulation for ducting using Class 1 closed cell elastomeric insulation of 10mm thick Nitrile rubber insulation adhesive, longitudinal transverse joints sealed with adhesive in neat clean manner. Material shall be processed Nitrile Rubber foam with anti-microbial protection. Insulation shall have thermal conductivity of 0.047 W (m.K) and density of 140 - 180 kg m³. | Sq.mtr | 30.000 | 28,500.00 | 952.00 | 28,560.00 | 950.00 | 28,500.00
187 |  | Make Armaflex K-flex | Make Armaflex K-flex
188 | 5.3 | THERMAL INSULATION FOR KITCHEN DUCTS | THERMAL INSULATION FOR KITCHEN DUCTS
189 |  | SITC of Glass Fibre Blanket Insulation material bonded with Thrmosetting Resin, with factory applied laminated aluminium foil of 22 micrns with fibre glass backing. Nominal density 48 Kg CuM. Thermal conductivity, < 0.033 W m.K at 24 degreeC. All Insuation material and adhesives shall be as per Class I for surface spread and in accordance with BS 476, Class O for non-combustible grade. | SITC of Glass Fibre Blanket Insulation material bonded with Thrmosetting Resin, with factory applied laminated aluminium foil of 22 micrns with fibre glass backing. Nominal density 48 Kg CuM. Thermal conductivity, < 0.033 W m.K at 24 degreeC. All Insuation material and adhesives shall be as per Class I for surface spread and in accordance with BS 476, Class O for non-combustible grade.
190 |  | Makes UP Twiga, Owens Corning, Supreme | Makes UP Twiga, Owens Corning, Supreme
191 |  | 80 mm Thick | 80 mm Thick | Sq.mtr | 150.000 | 141,000.00 | 940.00 | 141,000.00 | 950.00 | 142,500.00
192 |  | Note | Note
193 | a. | Insulation work to be coordinated with other agencies and repair to be included by contractor as per site requirement. | Insulation work to be coordinated with other agencies and repair to be included by contractor as per site requirement.
194 | b. | Vendors to take care of the installation, if any damages takes place the vendor to repair or replace and hand over to clients in good and acceptable condition. | Vendors to take care of the installation, if any damages takes place the vendor to repair or replace and hand over to clients in good and acceptable condition.
195 | c. | Thermal insulation shall be internal for Elliptical Expossed ducting. | Thermal insulation shall be internal for Elliptical Expossed ducting.
196 |  | SUB-TOTAL | SUB-TOTAL
197 | 6 | ELECTRICAL WORKS | ELECTRICAL WORKS
198 | 6.1 | STARTER PANEL | STARTER PANEL
199 |  | SITC of indoor outdoor, wall mounting type DOL Delta 3PH, 415V AC MOTOR STARTERS with VFD in CRCA Sheet Steel enclosure with necssary supporting brackets and required accessories, etc., The Enclosure shall be provided with knockouts suitable for cable termination at TOP BOTTOM for incoming and outgoing power cables of A2XFY type and size specified. The starters shall be complete with suitable MPCB MCCB, Contactor, Bi-metal O L relay with SPP, ON OFF Push buttons, on off trip indication Lamp, on off push button, phase indication Lamp. Selection of relay, contractor, MPCB MCCB etc. as per Type-2 Coordination. Starter panel shall be BMS compatible. Variable frequency drives shall be provided with necessary sensors and controllers complete with control wiring in all respect as required. VFDs shall be provided with necessary bypass arrangement inside electrical starter panels with IP-55 enclosure. | SITC of indoor outdoor, wall mounting type DOL Delta 3PH, 415V AC MOTOR STARTERS with VFD in CRCA Sheet Steel enclosure with necssary supporting brackets and required accessories, etc., The Enclosure shall be provided with knockouts suitable for cable termination at TOP BOTTOM for incoming and outgoing power cables of A2XFY type and size specified. The starters shall be complete with suitable MPCB MCCB, Contactor, Bi-metal O L relay with SPP, ON OFF Push buttons, on off trip indication Lamp, on off push button, phase indication Lamp. Selection of relay, contractor, MPCB MCCB etc. as per Type-2 Coordination. Starter panel shall be BMS compatible. Variable frequency drives shall be provided with necessary sensors and controllers complete with control wiring in all respect as required. VFDs shall be provided with necessary bypass arrangement inside electrical starter panels with IP-55 enclosure.
200 |  | Suitable for Star Delta Panel with VFD | Suitable for Star Delta Panel with VFD
201 | a | 11100 CFM Exhaust fan | 11100 CFM Exhaust fan | No. | 0.000 | .00 | 0.00 | .00 | 0.00 | .00
202 | b | 8600 CFM Air-washer Fan | 8600 CFM Air-washer Fan | No. | 0.000 | .00 | 0.00 | .00 | 0.00 | .00
203 | c | 9.3 Tr 4300 CFM AHU | 9.3 Tr 4300 CFM AHU | No. | 0.000 | .00 | 0.00 | .00 | 0.00 | .00
204 | 6.2 | ISOLATOR | ISOLATOR
205 |  | S I of 32A, FP, 300mA ELMCB, in powder coated (IP66) sheet metal box for terminating power to equipment etc. | S I of 32A, FP, 300mA ELMCB, in powder coated (IP66) sheet metal box for terminating power to equipment etc. | Nos. | 0.000 | .00 | 0.00 | .00 | 0.00 | .00
206 |  | S I of 25A, FP, 300mA ELMCB, in powder coated (IP66) sheet metal box for terminating power to equipment etc. | S I of 25A, FP, 300mA ELMCB, in powder coated (IP66) sheet metal box for terminating power to equipment etc. | Nos. | 0.000 | .00 | 0.00 | .00 | 0.00 | .00
207 | 6.3 | POWER CABLING | POWER CABLING
208 |  | Supply, handling, laying effecting proper connections testing and commissioning of following sizes of 1.1 KV grade XLPE insulated FRLS Aluminium Copper conductor cables laid over MS supports cable racks or fixing on walls including clamping the cable to supports in an approved manner as required complete with Copper earthing as specified for continuous earthing along with cable. All complete as required and as per final instruction as given by Owners Consultants and as per Technical specifications. Earthing shall be measured separately and shall be connected in two runs. Power to ELCB S be provided near each Fan ODU by electrical contractor. | Supply, handling, laying effecting proper connections testing and commissioning of following sizes of 1.1 KV grade XLPE insulated FRLS Aluminium Copper conductor cables laid over MS supports cable racks or fixing on walls including clamping the cable to supports in an approved manner as required complete with Copper earthing as specified for continuous earthing along with cable. All complete as required and as per final instruction as given by Owners Consultants and as per Technical specifications. Earthing shall be measured separately and shall be connected in two runs. Power to ELCB S be provided near each Fan ODU by electrical contractor.
209 |  | Suitable Power Cable | Suitable Power Cable
210 | a | 11100 CFM Exhaust fan | 11100 CFM Exhaust fan | Rmt | 5.000 | 2,750.00 | 550.00 | 2,750.00 | 550.00 | 2,750.00
211 | b | 8600 CFM Air-washer Fan | 8600 CFM Air-washer Fan | Rmt | 5.000 | 2,700.00 | 540.00 | 2,700.00 | 550.00 | 2,750.00
212 | c | 5550 CFM Dry Scrubber | 5550 CFM Dry Scrubber | Rmt | 10.000 | 2,500.00 | 250.00 | 2,500.00 | 250.00 | 2,500.00
213 | d | 9.3 Tr 4300 CFM AHU | 9.3 Tr 4300 CFM AHU | Rmt | 10.000 | 4,400.00 | 440.00 | 4,400.00 | 450.00 | 4,500.00
214 | e | Earthing | Earthing
215 |  | 8 SWG GI Earthing | 8 SWG GI Earthing | Rmt | 40.000 | 4,400.00 | 110.00 | 4,400.00 | 120.00 | 4,800.00
216 | 6.4 | CABLE TERMINATION | CABLE TERMINATION
217 |  | Supply Making of Cable termination of armoured unarmoured cables 1.1 KV grade including installation of cable glands, cable lugs (Aluminium for A2XFY copper for 2XFY YY Double compression type), heat shrinkable sleeves on long ends, crimping paste etc. The work includes testing commissioning of cables, meggaring values submitting reports of tests. (One set includes termination of all cores of one end only). All crimping tools dies shall be arranged by contractor. | Supply Making of Cable termination of armoured unarmoured cables 1.1 KV grade including installation of cable glands, cable lugs (Aluminium for A2XFY copper for 2XFY YY Double compression type), heat shrinkable sleeves on long ends, crimping paste etc. The work includes testing commissioning of cables, meggaring values submitting reports of tests. (One set includes termination of all cores of one end only). All crimping tools dies shall be arranged by contractor.
218 |  | Suitable for | Suitable for
219 | a | 11100 CFM Exhaust fan | 11100 CFM Exhaust fan | Nos. | 2.000 | 1,000.00 | 500.00 | 1,000.00 | 500.00 | 1,000.00
220 | b | 8600 CFM Air-washer Fan | 8600 CFM Air-washer Fan | Nos. | 2.000 | 1,000.00 | 500.00 | 1,000.00 | 500.00 | 1,000.00
221 | c | 9.3 Tr 4300 CFM AHU | 9.3 Tr 4300 CFM AHU | Nos. | 4.000 | 2,000.00 | 500.00 | 2,000.00 | 500.00 | 2,000.00
222 | 6.5 | CABLE TRAYS | CABLE TRAYS
223 |  | Supplying Fixing of following sizes of GI cable tray duly painted perforated type of height 50mm along with necessary bends, reducers etc. anchored along the wall suspended from the ceiling with necessary MS supports. | Supplying Fixing of following sizes of GI cable tray duly painted perforated type of height 50mm along with necessary bends, reducers etc. anchored along the wall suspended from the ceiling with necessary MS supports.
224 | a | 50mm wide x 1.6mm thick | 50mm wide x 1.6mm thick | Rmt | 30.000 | 7,500.00 | 250.00 | 7,500.00 | 550.00 | 16,500.00
225 | b | 100mm wide x 1.6mm thick | 100mm wide x 1.6mm thick | Rmt | 0.000 | .00 | 350.00 | .00 | 0.00 | .00

## Technical Score Detail
|  | RFQ No: R0179 COST COMPARISON REPORT | RFQ No: R0179 COST COMPARISON REPORT | RFQ No: R0179 COST COMPARISON REPORT | Comp. Date : 20/02/2024 | Comp. Date : 20/02/2024 | Comp. Date : 20/02/2024 | Vendor Name : ANJLE MEP PROJECTS PVT LTD | [7 empty] | Vendor Name : PIONEER PROJECT SOLUTION
|  | RFQ No: R0179 COST COMPARISON REPORT | RFQ No: R0179 COST COMPARISON REPORT | RFQ No: R0179 COST COMPARISON REPORT | RFQ #: R0179 | RFQ #: R0179 | RFQ #: R0179 | Contact Name : Priyanka/Premkant Rajpoot | [7 empty] | Contact Name : Mohd Ashraf
|  | RFQ No: R0179 COST COMPARISON REPORT | RFQ No: R0179 COST COMPARISON REPORT | RFQ No: R0179 COST COMPARISON REPORT | RFQ Date : 19/02/2024 17:22:21 | RFQ Date : 19/02/2024 17:22:21 | RFQ Date : 19/02/2024 17:22:21 | Vendor City : | [7 empty] | Vendor City :
|  | RFQ No: R0179 COST COMPARISON REPORT | RFQ No: R0179 COST COMPARISON REPORT | RFQ No: R0179 COST COMPARISON REPORT | BCD Date : | BCD Date : | BCD Date : | Telephone # : | [7 empty] | Telephone # :
|  | RFQ No: R0179 COST COMPARISON REPORT | RFQ No: R0179 COST COMPARISON REPORT | RFQ No: R0179 COST COMPARISON REPORT |  |  |  | Mobile # : | [7 empty] | Mobile # :
PR Number : TFSPL-2324-00251 | PR Number : TFSPL-2324-00251 | PR Number : TFSPL-2324-00251 | PR Number : TFSPL-2324-00251 | PR Number : TFSPL-2324-00251 | PR Number : TFSPL-2324-00251 | PR Number : TFSPL-2324-00251 | PR Number : TFSPL-2324-00251 | Email : anjlemepprojects@gmail.com | [7 empty] | Email : projectspioneer@gmail.com
Package / RFQ Name : HVAC work - Internation Food Hall | Package / RFQ Name : HVAC work - Internation Food Hall | Package / RFQ Name : HVAC work - Internation Food Hall | Package / RFQ Name : HVAC work - Internation Food Hall | Package / RFQ Name : HVAC work - Internation Food Hall | Package / RFQ Name : HVAC work - Internation Food Hall | Package / RFQ Name : HVAC work - Internation Food Hall | Package / RFQ Name : HVAC work - Internation Food Hall | Round # : 1 (RFQ) |  | Round # : 2 (RFQ) |  | Round # : 3 (RFQ) |  | Round # : 4 (Auction) |  | Round # : 1 (RFQ) |  | Round # : 2 (RFQ) |  | Round # : 3 (RFQ) |  | Round # : 4 (Auction)
Buyer : Jogeswar Sahu | Buyer : Jogeswar Sahu | Buyer : Jogeswar Sahu | Buyer : Jogeswar Sahu | Buyer : Jogeswar Sahu | Buyer : Jogeswar Sahu | Buyer : Jogeswar Sahu | Buyer : Jogeswar Sahu | Quotation Date : |  | Quotation Date : |  | Quotation Date : |  | Quotation Date : |  | Quotation Date : |  | Quotation Date : |  | Quotation Date : |  | Quotation Date :
Comp. # : 4 | Comp. # : 4 | Comp. # : 4 | Comp. # : 4 | Comp. # : 4 | Currency :INR | Currency :INR | Currency :INR | Quotation Validity Date : |  | Quotation Validity Date : |  | Quotation Validity Date : |  | Quotation Validity Date : |  | Quotation Validity Date : |  | Quotation Validity Date : |  | Quotation Validity Date : |  | Quotation Validity Date :
Comp. # : 4 | Comp. # : 4 | Comp. # : 4 | Comp. # : 4 | Comp. # : 4 | BUDGET PRICE : | .00 |  | Quote Currency : |  | Quote Currency : |  | Quote Currency : |  | Quote Currency : |  | Quote Currency : |  | Quote Currency : |  | Quote Currency : |  | Quote Currency :
# | Item Code | Item Description | Last PO Details | Unit | Qty | Last PO Unit Rate | Last PO Total Value | Score | Justification | Score | Justification | Score | Justification | Score | Justification | Score | Justification | Score | Justification | Score | Justification | Score | Justification
1 |  | High Side - HVAC |  | NOS | 1.000 | 0.00 | 0.00
2 | Note: | Prices shall be based on supply, installation, testing commissioning (SITC) at site including all taxes, duties, transportation insurance etc. |  |  | 0.000 | 0.00 | 0.00
3 | 1 | CHILLED WATER TYPE CEILING SUSPENDED AHU (AIR HANDLING UNIT) |  |  | 0.000 | 0.00 | 0.00
4 | 1.1 | CEILING SUSPENDED AHU |  |  | 0.000 | 0.00 | 0.00
5 |  | Supply and assembly of Ceiling Suspended Double skin cabinet type AHU Integrated (Air handling units) of following specifications |  |  | 0.000 | 0.00 | 0.00
6 |  | Frame Structure It shall consist of 48mm Extruded Aluminium with thermal break profile. |  |  | 0.000 | 0.00 | 0.00
7 |  | Panel 45mm + - 2mm thick double skin sandwich panels with rockwool insulation of density 64 kg m3 or PUF insulation of 48 kg m3 , The sheet thickness shall be minimum 0.6 mm for the outer skin precoated and 0.8 mm thickness for the inner skin of plain GI. |  |  | 0.000 | 0.00 | 0.00
8 |  | Filtration Section It shall be provided with single stage washable type of prefilter MERV 8 first stage which shall be placed before coil section. |  |  | 0.000 | 0.00 | 0.00
9 |  | Coil Section Chilled water coil Multi row deep constructed with Aluminium fins of min 0.11mm thick 12 Fins per inch, and copper tubes of min 27 Guage thickness HYRDOPHYLLIC coated fins. Copper tube shall be min 12.5mm diameter. AHRI certified coil.The coil face area velocity shall not exceed 2.5m sec (500 fpm). |  |  | 0.000 | 0.00 | 0.00
10 |  | Drain Pan Condensate drain pan shall be fabricated from 18G SS 304 powder coated, insulated with 13 mm thick closed cell elastomeric(nitrile rubber) insulation. |  |  | 0.000 | 0.00 | 0.00
11 |  | Fan Section SISW DIDW Direct drive backward curved fan. The fan section shall be provided with limt switch for safety to shut off fan during Opening of access door. Fan outlet velocity not to exceed 1600 FPM. The sound level shall not be exceed more than 60dB @ 1m from the source. Vibration isolators, Door Limit switch, as per Technical Specifications, AHU Summary Sheet and drawings. Total static pressue has to calculated by Contractor as per the configuration. |  |  | 0.000 | 0.00 | 0.00
12 |  | Other Details AHU to house control box terminal box with Auto-Manual switch and incomer power terminal, with SPP, Over Undervoltage protection, shortcircuit protection and with no-nc contacts (potential free contact) to be provided for tripping on signal from Fire Dampers Fire Alarm Panel. Power cable from Terminal box to motor control cabling of required size upto the thermostat sensor etc. to be provided. Internal electrical and control wiring of AHU to be provided as factory fitted from AHU supplier. The cost shall include all necessary supports accessories required for installation. |  |  | 0.000 | 0.00 | 0.00
13 |  | Contractor shall design the chilled water coil according to the following conditions |  |  | 0.000 | 0.00 | 0.00
14 |  | a. Coil air entering temperature - 69.8°F DB |  |  | 0.000 | 0.00 | 0.00
15 |  | b. Coil air leaving temperature - 54°F DB 52.99°F WB |  |  | 0.000 | 0.00 | 0.00
16 |  | c. Chilled water temperature entering - 7.0°C 44.6°F |  |  | 0.000 | 0.00 | 0.00
17 |  | d. Chilled water temperature leaving - 12.0°C 53.6°F |  |  | 0.000 | 0.00 | 0.00
18 |  | e. Ambient temperature - DB - 110°F 43.3°C WB - 82°F 27.7°C |  |  | 0.000 | 0.00 | 0.00
19 |  | Make VTS Zeco Citizen |  |  | 0.000 | 0.00 | 0.00
20 |  | Type Capacity TR ESP No. of FA |  |  | 0.000 | 0.00 | 0.00
21 |  | (Cfm) (mm WG) Rows CFM |  |  | 0.000 | 0.00 | 0.00
22 | a | CS AHU 4300 9.4 25 4 6 450 |  | Nos. | 2.000 | 0.00 | 0.00
23 |  | GENERAL NOTES |  |  | 0.000 | 0.00 | 0.00
24 | a. | LHS RHS VALVE station location to be confirmed. |  |  | 0.000 | 0.00 | 0.00
25 | b. | Fan outlet velocity - 1600 FPM |  |  | 0.000 | 0.00 | 0.00
26 | c. | Contractor shall submit static pressure calculation for all above units to Client Consultant. |  |  | 0.000 | 0.00 | 0.00
27 | d. | Any change in motor HP shall be made at no extra cost to client. |  |  | 0.000 | 0.00 | 0.00
28 | e. | Fan efficiency shall be minimum 75% |  |  | 0.000 | 0.00 | 0.00
29 | f. | The cost shall be included liftting shifting of each equipment material with all necesaary arrnagement. Also, it shall be included the cost of scaffloding required for Installation of such material equipment. |  |  | 0.000 | 0.00 | 0.00
30 | 3 | VENTILATION SYSTEM |  |  | 0.000 | 0.00 | 0.00
31 | 3.1 | KITCHEN EXHAUST AIR FAN |  |  | 0.000 | 0.00 | 0.00
32 |  | SITC of Cabinet type SISW Centrifugal Blower, Direct Drive, Statically Dynamically Balanced, Backward Curved Impeller fan, Dunlop Anti- Vibration Pads etc. Motor should be outside stream with TEFC squirrel cage, weather protection shield, IP 65 rating with Class H Insulation motor, suitable for 3phase, 415volts, 50hz power supply. Sound level should be 65dB @ 3mtr distance. Fan should be painted with 2 coat of zinc chromate primer and 2 coats Epoxy paint. The quote shall include with MS frame and required accessories. (Vendor to crosscheck static pressure calculation). |  |  | 0.000 | 0.00 | 0.00
33 |  | Make Waves Systems Air Nicotra Humidin |  |  | 0.000 | 0.00 | 0.00
34 | a | 11100CFM, 65mm TSP |  | No. | 1.000 | 0.00 | 0.00
35 | 3.2 | KITCHEN DRY SCRUBBER |  |  | 0.000 | 0.00 | 0.00
36 |  | SITC of Dry scrubber – Electrostatic Air cleaner with starter panel as per specifications, suitable for following capacities, including electrical starter panel . The Air filtration efficiency should be between 90 to 95% units shall be staked one above other or side by side as per site requirement, if vendor will propose multiple units. |  |  | 0.000 | 0.00 | 0.00
37 |  | Finishing - Power coated, Dark Blue |  |  | 0.000 | 0.00 | 0.00
38 |  | Operating voltage - 220 Vac+ -10%, 50 Hz (Single phase) |  |  | 0.000 | 0.00 | 0.00
39 |  | Features - Short circuit, arc protection and auto restore power supply, BMS (Building Management System) terminals provided, Auto power cut-off when door is opened, Indicator LEDs for normal or wash indicator, Set of Terminals for remote LED normal or wash indicator |  |  | 0.000 | 0.00 | 0.00
40 |  | Efficiency - Upto 95%, meets NIOSH 5026 Oil Mist Test |  |  | 0.000 | 0.00 | 0.00
41 |  | Particle Size - Collects particles as small as 0.01 microns |  |  | 0.000 | 0.00 | 0.00
42 |  | Motor - Sealead ball bearings UL, single phase. |  |  | 0.000 | 0.00 | 0.00
43 |  | Cell - Ionizing voltage - 12 KVdc |  |  | 0.000 | 0.00 | 0.00
44 |  | Collector voltage - 6 KVdc |  |  | 0.000 | 0.00 | 0.00
45 |  | One cell comprising of 9 ionizing wires and 25 collection plates |  |  | 0.000 | 0.00 | 0.00
46 |  | Controls - Auto cut-off when door is opened. Indicator lights for fault, normal or wash function. |  |  | 0.000 | 0.00 | 0.00
47 |  | Pre-filter - Aluminium mesh, washable Dry contact for BMS. |  |  | 0.000 | 0.00 | 0.00
48 |  | Make Rydair Espair |  |  | 0.000 | 0.00 | 0.00
49 |  | CFM - 5550 |  | Nos. | 2.000 | 0.00 | 0.00
50 | 3.3 | KITCHEN AIR-WASHER FAN |  |  | 0.000 | 0.00 | 0.00
51 |  | SITC of Cabinet type Air-washer fan with Centrifugal Blower, Belt Direct Drive, Statically Dynamically Balanced, Backward Curved Impeller, MERV 8 filter, Dunlop Anti- Vibration Pads, filters,Water Circulation Pump, etc. Motor should be TEFC squirrel cage, IP 55 rating with Class F Insulation, suitable for 3phase, 415volts, 50hz power supply. Sound level should be 65dB @ 3mtr distance. Fan should be painted with 2 coat of zinc chromate primer and 2 coats Epoxy paint. MERV 8 G4 pleated pre-filters should be made of 100% synthetic media to capture common airborne contaminants as per ASHRAE Standard 52.2. (Vendor to crosscheck static pressure calculation) Air Washer will be supplied with Water Circulation Pump, Water Inlet Connection, Overflow, Drain Outlet with 3 8” Brass Spray Nozzles, Interconnected Piping for Air Washer. |  |  | 0.000 | 0.00 | 0.00
52 |  | Make Waves Systems Air Nicotra Humidin |  |  | 0.000 | 0.00 | 0.00
53 | a | 8600 CFM, 50mm TSP |  | No | 1.000 | 0.00 | 0.00
54 |  | Low Side - HVAC |  | NOS | 1.000 | 0.00 | 0.00
55 | 2 | CHILLED WATER PIPING |  |  | 0.000 | 0.00 | 0.00
56 | 2.1 | CHW PIPE |  |  | 0.000 | 0.00 | 0.00
57 |  | SITC of MS Heavy duty class C ERW Chilled Water pipe conforming to IS 1239 Part I class ‘C’ heavy and fitting shall be conforming to ASTM A-105,3000lbs socket weld end (up to 50mm) 1S 1239 Part-II HEAVY ASTM A-234 WPB, Gr.B butt weld fitting ( above 50NB pipe size). The cost also shall cover primer painted including bends, tees, MS supports, PUFF saddles, anchor fasteners, steel angles and any other material required to complete the work. The piping flange connection bolts, washers and nuts should be hot dipped galvanised. Flourscent Plastic Sticker paint shall be applied to indicate Water flow directions. Only End flanges to be used for capping of pipes. Table E of BS code for flange thickness to be adhered. |  |  | 0.000 | 0.00 | 0.00
58 |  | Make Jindal Hissar TATA |  |  | 0.000 | 0.00 | 0.00
59 | b | F 25 mm |  | Rmt | 0.000 | 0.00 | 0.00
60 | c | F 32 mm |  | Rmt | 0.000 | 0.00 | 0.00
61 | d | F 40 mm |  | Rmt | 60.000 | 0.00 | 0.00
62 | 2.2 | CHILLED WATER PIPING INSULATION - INTERNAL USE |  |  | 0.000 | 0.00 | 0.00
63 |  | SITC of insulation for chilled water. piping. For internal pipe - Stick 25mm thick Nitrile rubber class O Closed cell nitrile rubber with anti-microbial coating on it. Insulation shall have Thermal conductivity of 0.033 W (m.K) and water vapor permeance of 0.10. Joints should be sealed with 50 mm wide 3 mm thick self adhesive tape and putting PVC bands at all supports. Further, insulation shall be wrapped with 7 mil cloth with required adhesive on it. |  |  | 0.000 | 0.00 | 0.00
64 |  | Make Armaflex K-flex |  |  | 0.000 | 0.00 | 0.00
65 | a | F 25 mm |  | Rmt | 0.000 | 0.00 | 0.00
66 | b | F 32 mm |  | Rmt | 0.000 | 0.00 | 0.00
67 | c | F 40 mm |  | Rmt | 60.000 | 0.00 | 0.00
68 | 2.3 | BALL VALVE |  |  | 0.000 | 0.00 | 0.00
69 |  | SITC of following sizes of Ball Valve consist of Cap, Brass Body, Rated for 150 psi SWP, 600 psi WOG Pressure Two-piece construction; with brass body, regular port, B-16 chrome-plated ball and stem, replaceable “Teflon” or “TFE” seats and seals, blowout-proof stem, vinyl covered steel handle, threaded or soldered ends and extended stem for insulated piping. Same valve shall be used as a Drain valve. |  |  | 0.000 | 0.00 | 0.00
70 |  | Make Zoloto Audco Kitz |  |  | 0.000 | 0.00 | 0.00
71 | a | F 25 mm |  | Nos. | 4.000 | 0.00 | 0.00
72 | b | F 32 mm |  | Nos. | 0.000 | 0.00 | 0.00
73 | c | F 40 mm |  | Nos. | 12.000 | 0.00 | 0.00
74 | 2.4 | BALL VALVE WITH Y-STRAINER |  |  | 0.000 | 0.00 | 0.00
75 |  | SITC of following sizes of Brass Ball Valve with Y-Strainer consist of Cap, Brass Body, Rated for 150 psi SWP, 600 psi WOG Pressure Two-piece construction; with brass body, regular port, B-16 chrome-plated ball and stem, replaceable “Teflon” or “TFE” seats and seals, blowout-proof stem, vinyl covered steel handle, threaded or soldered ends and extended stem for insulated piping. Filter element shall be of non magnetic SS sheet with perforation. |  |  | 0.000 | 0.00 | 0.00
76 |  | Make Zoloto Audco Kitz |  |  | 0.000 | 0.00 | 0.00
77 | a | F 25 mm |  | Nos. | 0.000 | 0.00 | 0.00
78 | b | F 32 mm |  | Nos. | 0.000 | 0.00 | 0.00
79 | c | F 40 mm |  | Nos. | 2.000 | 0.00 | 0.00
80 | 2.5 | PIBCV VALVES |  |  | 0.000 | 0.00 | 0.00
81 |  | SITC of Pressure Independent Balancing cum Control Valves (PIBCV) including integrated motorised control valve and balancing device for combined flow and water balancing requirement. Valve body to be rated for PN 16. The valve design flow rate should be factory calibrated with + - 5% flow accuracy. Valve shall have necessary measuring ports, drain port, flanges etc., Valve shall also provide temperature sensor with necessary cabling (min 2mtr length to be considered with each valve). The balancing to be done through microprocessor based hand held terminal POT and the same results shall be furnished in the water balancing report as part of commissioning report and handing over manual. |  |  | 0.000 | 0.00 | 0.00
82 |  | Make Oventrop Siemens Danfoss |  |  | 0.000 | 0.00 | 0.00
83 | a | F 25 mm |  | Nos. | 0.000 | 0.00 | 0.00
84 | b | F 32 mm |  | Nos. | 0.000 | 0.00 | 0.00
85 | c | F 40 mm |  | Nos. | 2.000 | 0.00 | 0.00
86 | 2.6 | Auto Air Vent Valves |  |  | 0.000 | 0.00 | 0.00
87 |  | Make Anergy Flamco |  |  | 0.000 | 0.00 | 0.00
88 |  | Providing and fitting Auto Vent Valves. |  |  | 0.000 | 0.00 | 0.00
89 | a | SITC of Auto air vent in each risers common headers AHU. 3 4 auto vent valves at each coil riser header. |  | Nos. | 4.000 | 0.00 | 0.00
90 | 2.7 | SITC of Pressure gauges Thermometers |  |  | 0.000 | 0.00 | 0.00
91 |  | Make H Guru Waree |  |  | 0.000 | 0.00 | 0.00
92 |  | Necessary pressure gauges and thermometers 4 Dial type. |  |  | 0.000 | 0.00 | 0.00
93 | a | Water Pressure gauges 150mm dial complete with gauge valves, mounting, fittings and copper tubing extension wherever required. Pressure gauges Range 0-10 Kg CM2 |  | Nos. | 4.000 | 0.00 | 0.00
94 | b | Thermometers of the mercury in glass stem type and copper separable well complete with guard etc., of industrial grade mounting on water lines. Length 9 12 inches, Thermometer, Range 0-50 deg C |  | Nos. | 4.000 | 0.00 | 0.00
95 | c | Thermowells |  | Nos. | 8.000 | 0.00 | 0.00
96 | d | SITC of Brass Test Plug of industrial grade mounting on water |  | Nos. | 0.000 | 0.00 | 0.00
97 | 2.8 | INSULATED CONDENSATE DRAIN PIPE |  |  | 0.000 | 0.00 | 0.00
98 |  | SITC of UPVC pipes of following sizes for drain with necessary supports and fittings such as elbows, tees reducers etc. Condensate drain piping shall be complying to IS 4985 Class 3 UPVC pipe. Solvent cement complying with ASTM D2564 shall be used for joints. The insulation line to be insulated with nitrile rubber insulation of thickness 9mm and wrapped by weather proof protection tape. The Pipe wherever concealed should also have a parallel line as a standby arrangement in case of block of primary pipe. |  |  | 0.000 | 0.00 | 0.00
99 |  | Make Supreme, Prince, Astral |  |  | 0.000 | 0.00 | 0.00
100 | a | F 25 mm |  | Rmt | 15.000 | 0.00 | 0.00
101 | b | F 32 mm |  | Rmt | 20.000 | 0.00 | 0.00
102 | c | F 40 mm |  | Rmt | 0.000 | 0.00 | 0.00
103 |  | NOTES FOR PIPING |  |  | 0.000 | 0.00 | 0.00
104 | a | Piping connection shall be socket welded up to 50nb size and shall be butt weld above 50nb pipe size. Pipe flanges shall be confirming to ASTM A-105 # 150 SORF and flange dimension should be in accordance with ASME ANSI B 16.5 (150 SORF), fitting to fitting welding is not allowed. Nozzle connections thredolets weldolets are not allowed by puncturing the pipe. Only equal unequal Tee’s shall be used for branch connection from header. Socket weld end Tee shall be used for branch connection (up-to -50nb pipe size) w.r.t to pressure gauge temperature gauge Air vent Drain point etc. |  |  | 0.000 | 0.00 | 0.00
105 | b | Cover all open pipe ends with muslin cloth during construction |  |  | 0.000 | 0.00 | 0.00
106 | c | Pipe cleaning chemical treatment as per specs shall be included in the piping cost. |  |  | 0.000 | 0.00 | 0.00
107 | d | Unit rates for all indicated sizes of pipes valves shall be furnished. |  |  | 0.000 | 0.00 | 0.00
108 | e | Cleaning Painting of pipe before insulation shall be included in piping cost. |  |  | 0.000 | 0.00 | 0.00
109 | f | The piping support should be as per tender specification and additional supports are to be provided Contractor as decided by Consultant. |  |  | 0.000 | 0.00 | 0.00
110 | g | All the valves shall be insulated with the same material as that of Chilled water pipng and cost of insulation for valves shall be considered. |  |  | 0.000 | 0.00 | 0.00
111 | 3.4 | FRAMEWORK FOR FANS |  |  | 0.000 | 0.00 | 0.00
112 |  | Supply, Fabrication and Installation of MS frame using channels angle iron sections as required for mounting of ventilation fans scrubber in areas shown in the layout. The frame work shall be applied with red oxide primer and thereafter, two coats of enamel paint of approved colour. The general arrangement drawing for frame work shall be got approved from the Architects Structural Engineers prior to commencement of fabrication. |  | Kg | 350.000 | 0.00 | 0.00
113 |  | Note |  |  | 0.000 | 0.00 | 0.00
114 | a. | Fan outlet velocity - 1600 FPM |  |  | 0.000 | 0.00 | 0.00
115 | b. | All cabinet fans should have plenum section. |  |  | 0.000 | 0.00 | 0.00
116 | c. | Fresh air fan should to have 6mm thick synthetic media washable filter with framework. |  |  | 0.000 | 0.00 | 0.00
117 | d. | Contractor shall submit static pressure calculation for all above units to Client Consultant for their approval. Also, the total static drops across the systems shall cover the overall length from suction discharge to grille (inside the outlet). |  |  | 0.000 | 0.00 | 0.00
118 | e. | Any change in motor HP or coil selection shall be made at no extra cost to client. |  |  | 0.000 | 0.00 | 0.00
119 | f. | Fan efficiency shall be minimum 75% |  |  | 0.000 | 0.00 | 0.00
120 | g. | The cost shall be included liftting shifting of each equipment material with all necesaary arrnagement. Also, it shall be included the cost of scaffloding required for Installation of such material equipment. |  |  | 0.000 | 0.00 | 0.00
121 |  | SUB-TOTAL |  |  | 0.000 | 0.00 | 0.00
122 | 4 | SHEET METAL WORKS |  |  | 0.000 | 0.00 | 0.00
123 | 4.1 | FACTORY FABRICATED G.I RECTANGULAR DUCT |  |  | 0.000 | 0.00 | 0.00
124 |  | Supply, Fabrication, Testing, and Commissioning of Factory Fabricated GI Sheet Metal 120GSM Rectangular boxed ducting, Plenums, Cowls, Elbows with turning vanes, Splitters, Reducers, Flanges, Collars etc as per IS and Installaton as per SMACNA and IS 655 standards, The complete ducting shall be provided with MS Supports, Rods, Angles, Flanges, Bracing, Rubber Gaskets, Wooden frames, Canvas Connections, etc. as per drawings and specifications. |  |  | 0.000 | 0.00 | 0.00
125 |  | GI Sheet Makes Tata, Jindal, SAIL, Ispat |  |  | 0.000 | 0.00 | 0.00
126 |  | Make Rola Star, Zeco Ductofab |  |  | 0.000 | 0.00 | 0.00
127 | a | 18 Gauge GI Sheet Metal Duct (Above 2251mm Plenum) |  | Sq.mtr | 25.000 | 0.00 | 0.00
128 | b | 20 Gauge GI Sheet Metal Duct (1501-2250mm) for Kitchen Exhaust Works |  | Sq.mtr | 125.000 | 0.00 | 0.00
129 | c | 22 Gauge GI Sheet Metal Duct (751-1500mm) |  | Sq.mtr | 20.000 | 0.00 | 0.00
130 | d | 24 Gauge GI Sheet Metal Duct (0-750mm) |  | Sq.mtr | 200.000 | 0.00 | 0.00
131 | 4.2 | G.I ELLIPTICAL DUCTING |  |  | 0.000 | 0.00 | 0.00
132 |  | Supply, Fabrication, erection, testing commissioning of factory fabricated GI sheet metal Elliptical ducting complete with turning vanes, neoprene rubber gasket, external painting, duct supports (gripple support eye bolt threaded rod), hangers etc. as per drawings and specifications. All ducts has to be powder coated by HVAC contractor, sample to be presented for the validation for Client. Color Code shall be provided by Client Arch. |  |  | 0.000 | 0.00 | 0.00
133 | a | 20 Gauge GI Sheet Metal Duct (1501-2250mm) |  | Sq.mtr | 0.000 | 0.00 | 0.00
134 | b | 22 Gauge GI Sheet Metal Duct (751-1500mm) |  | Sq.mtr | 80.000 | 0.00 | 0.00
135 | c | 24 Gauge GI Sheet Metal Duct (0-750mm) |  | Sq.mtr | 75.000 | 0.00 | 0.00
136 | 4.3 | EXTRUDED ALUMINIUM CEILING GRILLES |  |  | 0.000 | 0.00 | 0.00
137 |  | Supply, Installation, Testing and Balancing of Powder coated aluminium linear supply air grilles complete with removable inner core as per approved shop drawing and specifications. The area of grille can be of any geometrical shape (Square rectangular Linear). The grilles shall be with 15 30 45° deflections as per requirement. The Colour shall be decided and approved by client and architect. |  |  | 0.000 | 0.00 | 0.00
138 |  | Make Cosmos, Air Master System Air |  |  | 0.000 | 0.00 | 0.00
139 | a | Linear Square Rectangular Grille |  | Sq.mtr | 7.000 | 0.00 | 0.00
140 | 4.4 | EXTRUDED ALUMINIUM ROUND AIR DIFFUSER |  |  | 0.000 | 0.00 | 0.00
141 |  | Supply, Installation, Testing and Balancing of Powder coated aluminium supply air round diffuser complete with removable inner core as per approved shop drawing and specifications. The diffuser shall also be provided with Black painted GI opposed blade damper (OBD) of required sizes. Each diffuser shall have double inlet rings to connect flexible ducts. The diffuser shall be suitable for gypsum grid ceiling. The Colour shall be decided and approved by client and architect. |  |  | 0.000 | 0.00 | 0.00
142 |  | Make Cosmos Ruskin Titus Air Master |  |  | 0.000 | 0.00 | 0.00
143 |  | ROUND DIFFUSER FOR GYPSUM CEILING |  |  | 0.000 | 0.00 | 0.00
144 | a | Supply Air Diffuser with OBD - Neck Size 325Fmm |  | Nos. | 15.000 | 0.00 | 0.00
145 | b | Supply Air Diffuser with OBD - Neck Size 225Fmm |  | Nos. | 7.000 | 0.00 | 0.00
146 | c | Return Air Diffuser without OBD |  | Nos. | 3.000 | 0.00 | 0.00
147 | 4.5 | SS EXHAUST AND FRESH AIR GRILLES |  |  | 0.000 | 0.00 | 0.00
148 |  | SITC of 18G S.S 304 Grills adjustable Double Deflector With S.S Volume Control Dampers. Grills to be of Double Deflection Type for ease of deflection on all sides and to have necessary built in Dampers for adjustable nature. |  |  | 0.000 | 0.00 | 0.00
149 |  | Make Carryaire System Air Dynacraft Air Master |  |  | 0.000 | 0.00 | 0.00
150 | a | Linear Square Rectangular Grille |  | Sq.mtr | 1.000 | 0.00 | 0.00
151 | 4.6 | EXTRUDED ALUMINIUM LOUVER with BIRD SCREEN |  |  | 0.000 | 0.00 | 0.00
152 |  | SITC of Aluminium extruded powder coated Louver with four side flanges, wire mesh bird screen etc. |  | Sq.mtr | 0.000 | 0.00 | 0.00
153 | 4.7 | OPPOSED BLADE DAMPER |  |  | 0.000 | 0.00 | 0.00
154 |  | SITC of Aluminium Opposed blade dampers black powder coated vertical blades type for supply air collar. The damper should be gear operated type. |  | Sq.mtr | 2.000 | 0.00 | 0.00
155 |  | Make Cosmos, Air Master System Air |  |  | 0.000 | 0.00 | 0.00
156 | 4.8 | DOOR TRANSFER GRILLE |  |  | 0.000 | 0.00 | 0.00
157 |  | SITC of Aluminium extruded powder coated Door transfer grills. |  |  | 0.000 | 0.00 | 0.00
158 |  | Door transfer grille (Back to Back) |  | Sq.mtr | 1.000 | 0.00 | 0.00
159 |  | Make Cosmos, Air Master System Air |  |  | 0.000 | 0.00 | 0.00
160 | 4.9 | MULTI LEAF VOLUME CONTROL DAMPER |  |  | 0.000 | 0.00 | 0.00
161 |  | SITC of opposed blade aerofoil type 1.2 mm thick Anodized Aluminium volume control dampers for ducts shall be provided with concealed gears, plastic operator and quadrants for manual control of volume of air flow and for proper balancing of the air distribution system as per the approved shop drawings and specifications. |  | Sq.mtr | 5.000 | 0.00 | 0.00
162 |  | Make Cosmos, Air Master System Air |  |  | 0.000 | 0.00 | 0.00
163 | 4.10 | CURTAIN TYPE FIRE DAMPER |  |  | 0.000 | 0.00 | 0.00
164 |  | SITC of curtain type fire dampers consist of 16G GI frame, 20G GI interlocking blades secured with SS springs, blades outside airstream clamped with fusible link UL-555 listed with melting point 165 225°F, etc; as per the approved shop drawings and specifications. |  |  | 0.000 | 0.00 | 0.00
165 |  | Make Cosmos, Air Master System Air |  |  | 0.000 | 0.00 | 0.00
166 | a | Bare fire dampers |  | Sq.mtr | 0.000 | 0.00 | 0.00
167 | b | Fusible link as per specification UL 555 and CBRI approved |  | Nos. | 0.000 | 0.00 | 0.00
168 | 4.11 | DISC VALVE |  |  | 0.000 | 0.00 | 0.00
169 |  | SITC of Aluminium powder coated Disc valve suitable for exhausting toilet foul air, comprising of an adjustable centre cone and coupling sleeve made of Aluminium sheet duly epoxy painted with approved color. |  |  | 0.000 | 0.00 | 0.00
170 |  | Make Cosmos, Air Master System Air |  |  | 0.000 | 0.00 | 0.00
171 | a | 150mmF |  | Nos. | 0.000 | 0.00 | 0.00
172 | 4.12 | CANVAS CONNECTION |  |  | 0.000 | 0.00 | 0.00
173 |  | SITC of Flexible connections between mouth piece of Fan and initial piece of ducting with inspection zip. Flexible connections shall be double thickness non-flammable material (Fire retardant type). |  |  | 0.000 | 0.00 | 0.00
174 | a | For AHU |  | Nos | 2.000 | 0.00 | 0.00
175 | b | For Ventilation Fan |  | Nos | 4.000 | 0.00 | 0.00
176 |  | NOTES |  |  | 0.000 | 0.00 | 0.00
177 |  | The ducting support should be as per tender specification and additional supports are to be provided by Contractor as decided by Consultant. |  |  | 0.000 | 0.00 | 0.00
178 |  | Muslin cloth cover for all air outlets during construction. |  |  | 0.000 | 0.00 | 0.00
179 |  | Pressure testing of complete duct work as per DW SMACNA standard. |  |  | 0.000 | 0.00 | 0.00
180 |  | Silicon sealant for longitudinal transverse joints as per specification. |  |  | 0.000 | 0.00 | 0.00
181 |  | Diffusers grilles shall be powder coated as per color approved by Architect. |  |  | 0.000 | 0.00 | 0.00
182 |  | SUB-TOTAL |  |  | 0.000 | 0.00 | 0.00
183 | 5 | THERMAL ACOUSTIC INSULATION |  |  | 0.000 | 0.00 | 0.00
184 | 5.1 | THERMAL INSULATION |  |  | 0.000 | 0.00 | 0.00
185 |  | Supply fixing of Thermal insulation for supply air duct using 19mm thick class O BS 476 Part 6-7 FM Approved nitrile rubber elastomeric insulation thermal conductivity of 0.033 (W (M·K)) and water vapor permeance of 0.10 at 0°C for air conditioning ducting. Joints should be sealed with 50 mm wide 3 mm thick self adhesive tape. The duct shall be stick with recommended adhesive. |  | Sq.mtr | 350.000 | 0.00 | 0.00
186 |  | Make Armaflex K-flex |  |  | 0.000 | 0.00 | 0.00
187 | 5.2 | ACOUSTIC INSULATION |  |  | 0.000 | 0.00 | 0.00
188 |  | Supply fixing acoustic insulation for ducting using Class 1 closed cell elastomeric insulation of 10mm thick Nitrile rubber insulation adhesive, longitudinal transverse joints sealed with adhesive in neat clean manner. Material shall be processed Nitrile Rubber foam with anti-microbial protection. Insulation shall have thermal conductivity of 0.047 W (m.K) and density of 140 - 180 kg m³. |  | Sq.mtr | 30.000 | 0.00 | 0.00
189 |  | Make Armaflex K-flex |  |  | 0.000 | 0.00 | 0.00
190 | 5.3 | THERMAL INSULATION FOR KITCHEN DUCTS |  |  | 0.000 | 0.00 | 0.00
191 |  | SITC of Glass Fibre Blanket Insulation material bonded with Thrmosetting Resin, with factory applied laminated aluminium foil of 22 micrns with fibre glass backing. Nominal density 48 Kg CuM. Thermal conductivity, < 0.033 W m.K at 24 degreeC. All Insuation material and adhesives shall be as per Class I for surface spread and in accordance with BS 476, Class O for non-combustible grade. |  |  | 0.000 | 0.00 | 0.00
192 |  | Makes UP Twiga, Owens Corning, Supreme |  |  | 0.000 | 0.00 | 0.00
193 |  | 80 mm Thick |  | Sq.mtr | 150.000 | 0.00 | 0.00
194 |  | Note |  |  | 0.000 | 0.00 | 0.00
195 | a. | Insulation work to be coordinated with other agencies and repair to be included by contractor as per site requirement. |  |  | 0.000 | 0.00 | 0.00
196 | b. | Vendors to take care of the installation, if any damages takes place the vendor to repair or replace and hand over to clients in good and acceptable condition. |  |  | 0.000 | 0.00 | 0.00
197 | c. | Thermal insulation shall be internal for Elliptical Expossed ducting. |  |  | 0.000 | 0.00 | 0.00
198 |  | SUB-TOTAL |  |  | 0.000 | 0.00 | 0.00
199 | 6 | ELECTRICAL WORKS |  |  | 0.000 | 0.00 | 0.00
200 | 6.1 | STARTER PANEL |  |  | 0.000 | 0.00 | 0.00
201 |  | SITC of indoor outdoor, wall mounting type DOL Delta 3PH, 415V AC MOTOR STARTERS with VFD in CRCA Sheet Steel enclosure with necssary supporting brackets and required accessories, etc., The Enclosure shall be provided with knockouts suitable for cable termination at TOP BOTTOM for incoming and outgoing power cables of A2XFY type and size specified. The starters shall be complete with suitable MPCB MCCB, Contactor, Bi-metal O L relay with SPP, ON OFF Push buttons, on off trip indication Lamp, on off push button, phase indication Lamp. Selection of relay, contractor, MPCB MCCB etc. as per Type-2 Coordination. Starter panel shall be BMS compatible. Variable frequency drives shall be provided with necessary sensors and controllers complete with control wiring in all respect as required. VFDs shall be provided with necessary bypass arrangement inside electrical starter panels with IP-55 enclosure. |  |  | 0.000 | 0.00 | 0.00
202 |  | Suitable for Star Delta Panel with VFD |  |  | 0.000 | 0.00 | 0.00
203 | a | 11100 CFM Exhaust fan |  | No. | 0.000 | 0.00 | 0.00
204 | b | 8600 CFM Air-washer Fan |  | No. | 0.000 | 0.00 | 0.00
205 | c | 9.3 Tr 4300 CFM AHU |  | No. | 0.000 | 0.00 | 0.00
206 | 6.2 | ISOLATOR |  |  | 0.000 | 0.00 | 0.00
207 |  | S I of 32A, FP, 300mA ELMCB, in powder coated (IP66) sheet metal box for terminating power to equipment etc. |  | Nos. | 0.000 | 0.00 | 0.00
208 |  | S I of 25A, FP, 300mA ELMCB, in powder coated (IP66) sheet metal box for terminating power to equipment etc. |  | Nos. | 0.000 | 0.00 | 0.00
209 | 6.3 | POWER CABLING |  |  | 0.000 | 0.00 | 0.00
210 |  | Supply, handling, laying effecting proper connections testing and commissioning of following sizes of 1.1 KV grade XLPE insulated FRLS Aluminium Copper conductor cables laid over MS supports cable racks or fixing on walls including clamping the cable to supports in an approved manner as required complete with Copper earthing as specified for continuous earthing along with cable. All complete as required and as per final instruction as given by Owners Consultants and as per Technical specifications. Earthing shall be measured separately and shall be connected in two runs. Power to ELCB S be provided near each Fan ODU by electrical contractor. |  |  | 0.000 | 0.00 | 0.00
211 |  | Suitable Power Cable |  |  | 0.000 | 0.00 | 0.00
212 | a | 11100 CFM Exhaust fan |  | Rmt | 5.000 | 0.00 | 0.00
213 | b | 8600 CFM Air-washer Fan |  | Rmt | 5.000 | 0.00 | 0.00
214 | c | 5550 CFM Dry Scrubber |  | Rmt | 10.000 | 0.00 | 0.00
215 | d | 9.3 Tr 4300 CFM AHU |  | Rmt | 10.000 | 0.00 | 0.00
216 | e | Earthing |  |  | 0.000 | 0.00 | 0.00
217 |  | 8 SWG GI Earthing |  | Rmt | 40.000 | 0.00 | 0.00
218 | 6.4 | CABLE TERMINATION |  |  | 0.000 | 0.00 | 0.00
219 |  | Supply Making of Cable termination of armoured unarmoured cables 1.1 KV grade including installation of cable glands, cable lugs (Aluminium for A2XFY copper for 2XFY YY Double compression type), heat shrinkable sleeves on long ends, crimping paste etc. The work includes testing commissioning of cables, meggaring values submitting reports of tests. (One set includes termination of all cores of one end only). All crimping tools dies shall be arranged by contractor. |  |  | 0.000 | 0.00 | 0.00
220 |  | Suitable for |  |  | 0.000 | 0.00 | 0.00
221 | a | 11100 CFM Exhaust fan |  | Nos. | 2.000 | 0.00 | 0.00
222 | b | 8600 CFM Air-washer Fan |  | Nos. | 2.000 | 0.00 | 0.00
223 | c | 9.3 Tr 4300 CFM AHU |  | Nos. | 4.000 | 0.00 | 0.00
224 | 6.5 | CABLE TRAYS |  |  | 0.000 | 0.00 | 0.00
225 |  | Supplying Fixing of following sizes of GI cable tray duly painted perforated type of height 50mm along with necessary bends, reducers etc. anchored along the wall suspended from the ceiling with necessary MS supports. |  |  | 0.000 | 0.00 | 0.00
226 | a | 50mm wide x 1.6mm thick |  | Rmt | 30.000 | 0.00 | 0.00
227 | b | 100mm wide x 1.6mm thick |  | Rmt | 0.000 | 0.00 | 0.00