## Price Comparison
|  | RFQ No: R0235 COST COMPARISON REPORT | RFQ No: R0235 COST COMPARISON REPORT | RFQ No: R0235 COST COMPARISON REPORT | Comp. Date : 14/03/2024 | Comp. Date : 14/03/2024 | Comp. Date : 14/03/2024 | Vendor Name : PIONEER PROJECT SOLUTION (RV232410106) | [5 empty] | Vendor Name : COOL CARE ENTERPRISES (RV232410124) | [5 empty] | Vendor Name : ANJLE MEP PROJECT PVT LTD (T051996)
|  | RFQ No: R0235 COST COMPARISON REPORT | RFQ No: R0235 COST COMPARISON REPORT | RFQ No: R0235 COST COMPARISON REPORT | RFQ #: R0235 | RFQ #: R0235 | RFQ #: R0235 | Contact Name : Mohd Ashraf/Rayyan Javed | [5 empty] | Contact Name : Jasbir Singh | [5 empty] | Contact Name :
|  | RFQ No: R0235 COST COMPARISON REPORT | RFQ No: R0235 COST COMPARISON REPORT | RFQ No: R0235 COST COMPARISON REPORT | RFQ Date : 11/03/2024 16:28:21 | RFQ Date : 11/03/2024 16:28:21 | RFQ Date : 11/03/2024 16:28:21 | Vendor City : | [5 empty] | Vendor City : | [5 empty] | Vendor City :
|  | RFQ No: R0235 COST COMPARISON REPORT | RFQ No: R0235 COST COMPARISON REPORT | RFQ No: R0235 COST COMPARISON REPORT | BCD Date : | BCD Date : | BCD Date : | Telephone # : | [5 empty] | Telephone # : | [5 empty] | Telephone # :
|  | RFQ No: R0235 COST COMPARISON REPORT | RFQ No: R0235 COST COMPARISON REPORT | RFQ No: R0235 COST COMPARISON REPORT |  |  |  | Mobile # : | [5 empty] | Mobile # : | [5 empty] | Mobile # :
PR Number : TFS-2324-00034 | PR Number : TFS-2324-00034 | PR Number : TFS-2324-00034 | PR Number : TFS-2324-00034 | PR Number : TFS-2324-00034 | PR Number : TFS-2324-00034 | PR Number : TFS-2324-00034 | PR Number : TFS-2324-00034 | Email : projectspioneer@gmail.com | [5 empty] | Email : coolcareenterprises@gmail.com | [5 empty] | Email : anjlemepprojects@gmail.com
Package / RFQ Name : TFAS / RFQ / TFS-2324-00034 | Package / RFQ Name : TFAS / RFQ / TFS-2324-00034 | Package / RFQ Name : TFAS / RFQ / TFS-2324-00034 | Package / RFQ Name : TFAS / RFQ / TFS-2324-00034 | Package / RFQ Name : TFAS / RFQ / TFS-2324-00034 | Package / RFQ Name : TFAS / RFQ / TFS-2324-00034 | Package / RFQ Name : TFAS / RFQ / TFS-2324-00034 | Package / RFQ Name : TFAS / RFQ / TFS-2324-00034 | Round # : 5 (Auction) | [5 empty] | Round # : 5 (Auction) | [5 empty] | Round # : 5 (Auction)
Buyer : Jogeswar Sahu / Technical : / Approver : | Buyer : Jogeswar Sahu / Technical : / Approver : | Buyer : Jogeswar Sahu / Technical : / Approver : | Buyer : Jogeswar Sahu / Technical : / Approver : | Buyer : Jogeswar Sahu / Technical : / Approver : | Buyer : Jogeswar Sahu / Technical : / Approver : | Buyer : Jogeswar Sahu / Technical : / Approver : | Buyer : Jogeswar Sahu / Technical : / Approver : | Quotation Date : |  |  | Quotation Validity Date : |  |  | Quotation Date : |  |  | Quotation Validity Date : |  |  | Quotation Date : |  |  | Quotation Validity Date :
Comp. # : 5 | Comp. # : 5 | Comp. # : 5 | Comp. # : 5 | Comp. # : 5 | Currency :INR | Currency :INR | Currency :INR | Buyer Remark : | [5 empty] | Buyer Remark : . | [5 empty] | Buyer Remark :
Comp. # : 5 | Comp. # : 5 | Comp. # : 5 | Comp. # : 5 | Comp. # : 5 | BUDGET PRICE : | .00 |  | Quote Currency : INR | [5 empty] | Quote Currency : INR | [5 empty] | Quote Currency : INR
# | Item Code | Item Description | Unit | Qty | Last PO Details | Lowest Unit Rate | Lowest Vendor | First Bid | Disc % | GST % | Technical | Unit Price | Total | First Bid | Disc % | GST % | Technical | Unit Price | Total | First Bid | Disc % | GST % | Technical | Unit Price | Total
1 |  | LOW SIDE -AIR SCURBBER & AIR WASHER WITH DUCTING FOR BAR . | LOT | 1.00 |  | 653725.00 | COOL CARE ENTERPRISES | 754500.00 | 0.00 | 0.00 |  | 665,000.00 | 665,000.00 | 912850.00 | 0.00 | 0.00 |  | 653,725.00 | 653,725.00 | 1311450.00 | 0.00 | 0.00 |  | 1,311,450.00 | 1,311,450.00
Item Total | [8 empty] | .00 | .00 |  |  | 665,000.00 |  | .00 | .00 |  |  | 653,725.00 |  | .00 | .00 |  |  | 1,311,450.00
Discount Total Value | [7 empty] | Grand Dis. Amt | .00 |  |  |  | .00 | Grand Dis. Amt | .00 |  |  |  | .00 | Grand Dis. Amt | .00 |  |  |  | .00
GST Total Amount | [12 empty] | .00 | [5 empty] | .00 | [5 empty] | .00
Net Landed Cost | [11 empty] | INR | 665,000.00 |  |  |  |  | INR | 653,725.00 |  |  |  |  | INR | 1,311,450.00
Vendor Status | [7 empty] | Round # : 5 (Auction) | Round # : 5 (Auction)
Sr No. | Vendor Code | Vendor Name | [5 empty] | Status | Remarks
1 | T053007 | Kashyap Cooling point | [5 empty] | Participate
2 | T051996 | ANJLE MEP PROJECT PVT LTD | [5 empty] | Participate
3 | RV232410335 | Garg Brothers | [5 empty] | Not Participate
4 | RV232410333 | Daikin Airconditioning India Private Limited | [5 empty] | Participate
5 | RV232410124 | COOL CARE ENTERPRISES | [5 empty] | Participate
6 | RV232410106 | PIONEER PROJECT SOLUTION | [5 empty] | Participate

## BOQ Price Bid
|  | RFQ No: R0235 COST COMPARISON REPORT | RFQ No: R0235 COST COMPARISON REPORT | Comp. Date : 14/03/2024 | Comp. Date : 14/03/2024 | Comp. Date : 14/03/2024 | Vendor Name : PIONEER PROJECT SOLUTION | Vendor Name : PIONEER PROJECT SOLUTION | Vendor Name : COOL CARE ENTERPRISES | Vendor Name : COOL CARE ENTERPRISES | Vendor Name : ANJLE MEP PROJECT PVT LTD | Vendor Name : ANJLE MEP PROJECT PVT LTD
|  | RFQ No: R0235 COST COMPARISON REPORT | RFQ No: R0235 COST COMPARISON REPORT | RFQ #: R0235 | RFQ #: R0235 | RFQ #: R0235 | Contact Name : Mohd Ashraf/Rayyan Javed | Contact Name : Mohd Ashraf/Rayyan Javed | Contact Name : Jasbir Singh | Contact Name : Jasbir Singh | Contact Name : | Contact Name :
|  | RFQ No: R0235 COST COMPARISON REPORT | RFQ No: R0235 COST COMPARISON REPORT | RFQ Date : 11/03/2024 16:28:21 | RFQ Date : 11/03/2024 16:28:21 | RFQ Date : 11/03/2024 16:28:21 | Vendor City : | Vendor City : | Vendor City : | Vendor City : | Vendor City : | Vendor City :
|  | RFQ No: R0235 COST COMPARISON REPORT | RFQ No: R0235 COST COMPARISON REPORT | BCD Date : | BCD Date : | BCD Date : | Telephone # : | Telephone # : | Telephone # : | Telephone # : | Telephone # : | Telephone # :
|  | RFQ No: R0235 COST COMPARISON REPORT | RFQ No: R0235 COST COMPARISON REPORT |  |  |  | Mobile # : | Mobile # : | Mobile # : | Mobile # : | Mobile # : | Mobile # :
PR Number : TFS-2324-00034 | PR Number : TFS-2324-00034 | PR Number : TFS-2324-00034 | PR Number : TFS-2324-00034 | PR Number : TFS-2324-00034 | PR Number : TFS-2324-00034 | PR Number : TFS-2324-00034 | Email : projectspioneer@gmail.com | Email : projectspioneer@gmail.com | Email : coolcareenterprises@gmail.com | Email : coolcareenterprises@gmail.com | Email : anjlemepprojects@gmail.com | Email : anjlemepprojects@gmail.com
Package / RFQ Name : TFAS / RFQ / TFS-2324-00034 | Package / RFQ Name : TFAS / RFQ / TFS-2324-00034 | Package / RFQ Name : TFAS / RFQ / TFS-2324-00034 | Package / RFQ Name : TFAS / RFQ / TFS-2324-00034 | Package / RFQ Name : TFAS / RFQ / TFS-2324-00034 | Package / RFQ Name : TFAS / RFQ / TFS-2324-00034 | Package / RFQ Name : TFAS / RFQ / TFS-2324-00034 | Round # : 5 (Auction) | Round # : 5 (Auction) | Round # : 5 (Auction) | Round # : 5 (Auction) | Round # : 5 (Auction) | Round # : 5 (Auction)
Buyer : Jogeswar Sahu | Buyer : Jogeswar Sahu | Buyer : Jogeswar Sahu | Buyer : Jogeswar Sahu | Buyer : Jogeswar Sahu | Buyer : Jogeswar Sahu | Buyer : Jogeswar Sahu | Techanical Score : | Techanical Score : | Techanical Score : | Techanical Score : | Techanical Score : | Techanical Score :
Comp. # : 5 | Comp. # : 5 | Comp. # : 5 | Comp. # : 5 | Currency :INR | Currency :INR | Currency :INR | Quotation Date : | Quotation Date : | Quotation Date : | Quotation Date : | Quotation Date : | Quotation Date :
Comp. # : 5 | Comp. # : 5 | Comp. # : 5 | Comp. # : 5 | BUDGET PRICE :.00 | BUDGET PRICE :.00 | BUDGET PRICE :.00 | Quotation Validity Date : | Quotation Validity Date : | Quotation Validity Date : | Quotation Validity Date : | Quotation Validity Date : | Quotation Validity Date :
Sr No. | Item Code | Item Name | Item Description | UOM | Qty | Minimum Amount | Unit Price | Amount | Unit Price | Amount | Unit Price | Amount
1 |  | LOW SIDE -AIR SCURBBER & AIR WASHER WITH DUCTING FOR BAR . | LOW SIDE -AIR SCURBBER & AIR WASHER WITH DUCTING FOR BAR . | LOT | 1.000 |  |  | 754,500.00 |  | 653,725.00 |  | 1,311,450.00
1 |  | AIR SCRUBBER | AIR SCRUBBER
2 |  | Modular Double skin Floor mounted air scrubber units made of 23+2mm thick PUF insulated panels extruded aluminum hollow profiles with 0.8mm thick pre-coated GI Outer Sheet 0.8mm thick Plain GI (270gsm) inner sheet comprising of Intake section for duct connection, Al Wiremesh filter section, Wet section made of 20g SS Tank, Three Phase Pump (1w+1s), GI internal piping, Single Bank Spray Nozzles and 2bend PVC eliminators. Blower section with DIDW Aerofoil Backward Forward curved fans, drive set with V- belts, Spring type vibration isolators, wire guard on Fan section access door, fire retardant canvass connection at fan outlet, IE-2 motor (TEFC type suitable for VFD operation) LED lamps for blower section, limit switch for the fan section access door with a view port and damper at the outlet of unit. All dampers shall be low leakage aluminum aerofoil design and suitable for manual motorised operation. Units exposed to open sky shall have weather proof canopy. The End Plates Casing blank offs of Eliminators shall also be made of SS. | Modular Double skin Floor mounted air scrubber units made of 23+2mm thick PUF insulated panels extruded aluminum hollow profiles with 0.8mm thick pre-coated GI Outer Sheet 0.8mm thick Plain GI (270gsm) inner sheet comprising of Intake section for duct connection, Al Wiremesh filter section, Wet section made of 20g SS Tank, Three Phase Pump (1w+1s), GI internal piping, Single Bank Spray Nozzles and 2bend PVC eliminators. Blower section with DIDW Aerofoil Backward Forward curved fans, drive set with V- belts, Spring type vibration isolators, wire guard on Fan section access door, fire retardant canvass connection at fan outlet, IE-2 motor (TEFC type suitable for VFD operation) LED lamps for blower section, limit switch for the fan section access door with a view port and damper at the outlet of unit. All dampers shall be low leakage aluminum aerofoil design and suitable for manual motorised operation. Units exposed to open sky shall have weather proof canopy. The End Plates Casing blank offs of Eliminators shall also be made of SS.
3 |  | 8400 CFM (65mm of wg Total St. Pressure) | 8400 CFM (65mm of wg Total St. Pressure) | No. | 1.000 | 175,000.00 | 235000.00 | 235,000.00 | 175000.00 | 175,000.00 | 640000.00 | 640,000.00
4 |  | AIR WASHER | AIR WASHER
5 |  | Modular Double skin Floor mounted air washer units made of 23+2mm thick PUF insulated panels extruded aluminum hollow profiles with 0.8mm thick pre-coated GI Outer Sheet 0.8mm thick Plain GI (270gsm) inner sheet comprising of Al Wiremesh filter section, Wet section made of 20g SS Tank, Single Phase Pump (1w+1s), PVC internal piping, Distribution system, 200mm deep Cellulose Pads 2 bend PVC eliminators. Blower section with DIDW Aerofoil Backward Forward curved fans, drive set with V- belts, Spring type vibration isolators, wire guard on Fan section access door, fire retardant canvass connection at fan outlet, IE-2 motor (TEFC type suitable for VFD operation) LED lamps for blower section, limit switch for the fan section access door with a view port and damper at the outlet of unit. All dampers shall be low leakage aluminum aerofoil design and suitable for manual motorised operation. Units exposed to open sky shall have weather proof canopy. The End Plates Casing blank offs of Pads Eliminators shall also be made of SS. | Modular Double skin Floor mounted air washer units made of 23+2mm thick PUF insulated panels extruded aluminum hollow profiles with 0.8mm thick pre-coated GI Outer Sheet 0.8mm thick Plain GI (270gsm) inner sheet comprising of Al Wiremesh filter section, Wet section made of 20g SS Tank, Single Phase Pump (1w+1s), PVC internal piping, Distribution system, 200mm deep Cellulose Pads 2 bend PVC eliminators. Blower section with DIDW Aerofoil Backward Forward curved fans, drive set with V- belts, Spring type vibration isolators, wire guard on Fan section access door, fire retardant canvass connection at fan outlet, IE-2 motor (TEFC type suitable for VFD operation) LED lamps for blower section, limit switch for the fan section access door with a view port and damper at the outlet of unit. All dampers shall be low leakage aluminum aerofoil design and suitable for manual motorised operation. Units exposed to open sky shall have weather proof canopy. The End Plates Casing blank offs of Pads Eliminators shall also be made of SS.
6 |  | 7500 CFM (50mm of wg Total St. Pressure) | 7500 CFM (50mm of wg Total St. Pressure) | No. | 1.000 | 163,000.00 | 195000.00 | 195,000.00 | 163000.00 | 163,000.00 | 245000.00 | 245,000.00
7 |  | Supplying, installing, testing and commissioning of INLINE FANS suitable for installing in any position in vertical or horizontal ducts. The casing shall be double skin, internally acoustically lined and constructed of galvanised steel. The fan shall be DIDW with forward curve impeller fitted with maintenance free external rotor motor. The motor shall be suitable for 220±10% volt single phase 50 cycles AC supply. All units shall be complete with duct flexible connector and volume control damper and static pressure or to suit the system, shall be as follows | Supplying, installing, testing and commissioning of INLINE FANS suitable for installing in any position in vertical or horizontal ducts. The casing shall be double skin, internally acoustically lined and constructed of galvanised steel. The fan shall be DIDW with forward curve impeller fitted with maintenance free external rotor motor. The motor shall be suitable for 220±10% volt single phase 50 cycles AC supply. All units shall be complete with duct flexible connector and volume control damper and static pressure or to suit the system, shall be as follows
8 |  | Capacity 500 CFM Static Pressure 15 mmwg | Capacity 500 CFM Static Pressure 15 mmwg | No. | 1.000 | 10,500.00 | 10500.00 | 10,500.00 | 10500.00 | 10,500.00 | 22500.00 | 22,500.00
9 |  | Capacity 1000 CFM Static Pressure 15 mmwg | Capacity 1000 CFM Static Pressure 15 mmwg | No. | 1.000 | 16,000.00 | 16500.00 | 16,500.00 | 16000.00 | 16,000.00 | 32500.00 | 32,500.00
10 |  | AIR DISTRIBUTION | AIR DISTRIBUTION
11 |  | (FOR FACTORY FABRICATED DUCTS AS PER “SMACNA” STANDARDS SPECIFICTIONS) | (FOR FACTORY FABRICATED DUCTS AS PER “SMACNA” STANDARDS SPECIFICTIONS)
12 |  | Supply, Fabrication, installation and testing of factory fabricated sheet metal ducts with sleeve joints and supports complete with the approved shop drawings and as required by the specifications and hanging of the ducts to be done by thread wire on metal cushion with gripple support. | Supply, Fabrication, installation and testing of factory fabricated sheet metal ducts with sleeve joints and supports complete with the approved shop drawings and as required by the specifications and hanging of the ducts to be done by thread wire on metal cushion with gripple support.
13 |  | 18 G sheet | 18 G sheet | sq.m | 35.000 | 49,875.00 | 1450.00 | 50,750.00 | 1425.00 | 49,875.00 | 2050.00 | 71,750.00
14 |  | 20G sheet | 20G sheet | sq.m | 5.000 | 6,200.00 | 1250.00 | 6,250.00 | 1240.00 | 6,200.00 | 1650.00 | 8,250.00
15 |  | 22G sheet | 22G sheet | sq.m | 5.000 | 5,750.00 | 1150.00 | 5,750.00 | 1150.00 | 5,750.00 | 1450.00 | 7,250.00
16 |  | 24G sheet | 24G sheet | sq.m | 50.000 | 50,000.00 | 1050.00 | 52,500.00 | 1000.00 | 50,000.00 | 1250.00 | 62,500.00
17 |  | 26G sheet | 26G sheet | sq.m | 35.000 | 33,250.00 | 950.00 | 33,250.00 | 950.00 | 33,250.00 | 1150.00 | 40,250.00
18 |  | Supplying and erecting GI sheet of fabricated at site and mentioned guage to be used for fabrication of ducting complete with neoprene rubber garkets, elbows, splitter dampers, vanes, hangers, supports etc. as per approved drawings and specifications of following sheet thickness complete as required | Supplying and erecting GI sheet of fabricated at site and mentioned guage to be used for fabrication of ducting complete with neoprene rubber garkets, elbows, splitter dampers, vanes, hangers, supports etc. as per approved drawings and specifications of following sheet thickness complete as required
19 |  | 18 G sheet | 18 G sheet | sq.m | 5.000 | 7,000.00 | 1450.00 | 7,250.00 | 1400.00 | 7,000.00 | 1850.00 | 9,250.00
20 |  | 20G sheet | 20G sheet | sq.m | 5.000 | 6,000.00 | 1250.00 | 6,250.00 | 1200.00 | 6,000.00 | 1550.00 | 7,750.00
21 |  | 22G sheet | 22G sheet | sq.m | 5.000 | 5,750.00 | 1150.00 | 5,750.00 | 1150.00 | 5,750.00 | 1350.00 | 6,750.00
22 |  | 24G sheet | 24G sheet | sq.m | 5.000 | 5,100.00 | 1050.00 | 5,250.00 | 1020.00 | 5,100.00 | 1150.00 | 5,750.00
23 |  | Supply, installation, testing and balancing of powder coated Extruded Aluminium Supply air Grilles with volume control dampers in accordance with the approved shop drawings and specifications. (Minimum Chargable area would be 0.1 Sqm Per Pc) | Supply, installation, testing and balancing of powder coated Extruded Aluminium Supply air Grilles with volume control dampers in accordance with the approved shop drawings and specifications. (Minimum Chargable area would be 0.1 Sqm Per Pc) | SQMT | 1.000 | 9,000.00 | 9000.00 | 9,000.00 | 9000.00 | 9,000.00 | 10500.00 | 10,500.00
24 |  | Supplying fixing of opposed blade volume control dampers in supply air duct collars as per approved drawings and specifications. Volume control damper shall be provided at the junction of each branch duct with main duct. Dampers shall be 2 gauge heavier than the gauge of large duct but should not be less than 20 gauge, and shall be rigid in construction so as not to flutter with the passage of air. | Supplying fixing of opposed blade volume control dampers in supply air duct collars as per approved drawings and specifications. Volume control damper shall be provided at the junction of each branch duct with main duct. Dampers shall be 2 gauge heavier than the gauge of large duct but should not be less than 20 gauge, and shall be rigid in construction so as not to flutter with the passage of air. | SQMT | 1.000 | 6,700.00 | 8500.00 | 8,500.00 | 6700.00 | 6,700.00 | 6750.00 | 6,750.00
25 |  | Supply, fabrication, installation and testing the flexible connections constructed of fire resistance flexible double canvas sleeve as per the approved shop drawings. | Supply, fabrication, installation and testing the flexible connections constructed of fire resistance flexible double canvas sleeve as per the approved shop drawings. | Nos. | 2.000 | 4,600.00 | 2500.00 | 5,000.00 | 2300.00 | 4,600.00 | 2850.00 | 5,700.00
26 |  | Supply, installation, testing and balancing of Powder coated Anodised extruded aluminium construction exhaust air louvers with bird screen for exhaust air as per specifications and approved shop drawings. (Minimum Chargable area would be 0.1 Sqm Per Pc) | Supply, installation, testing and balancing of Powder coated Anodised extruded aluminium construction exhaust air louvers with bird screen for exhaust air as per specifications and approved shop drawings. (Minimum Chargable area would be 0.1 Sqm Per Pc) | SQMT | 0.000 | .00 | 0.00 | .00 | 0.00 | .00 | 12500.00 | .00
27 |  | Supply, installation, testing and balancing of Powder coated Anodised extruded aluminium construction. inlet air louvers with bird screen and volume damper for fresh air as per specifications and approved shop drawings. | Supply, installation, testing and balancing of Powder coated Anodised extruded aluminium construction. inlet air louvers with bird screen and volume damper for fresh air as per specifications and approved shop drawings. | SQMT | 0.000 | .00 | 0.00 | .00 | 0.00 | .00 | 0.00 | .00
28 |  | Supply, installation, testing and balancing of powder coated Extruded Aluminium exhaust air Grilles with volume control dampers in accordance with the approved shop drawings and specifications. (Minimum Chargable area would be 0.1 Sqm Per Pc) | Supply, installation, testing and balancing of powder coated Extruded Aluminium exhaust air Grilles with volume control dampers in accordance with the approved shop drawings and specifications. (Minimum Chargable area would be 0.1 Sqm Per Pc) | SQMT | 2.000 | 18,000.00 | 9500.00 | 19,000.00 | 9000.00 | 18,000.00 | 10500.00 | 21,000.00
29 |  | THERMAL INSULATION | THERMAL INSULATION
30 |  | THERMAL INSULATION FOR KITCHEN DUCTS | THERMAL INSULATION FOR KITCHEN DUCTS
31 |  | SITC of Glass Fibre Blanket Insulation material bonded with Thrmosetting Resin, with factory applied laminated aluminium foil of 22 micrns with fibre glass backing. Nominal density 48 Kg CuM. Thermal conductivity, < 0.033 W m.K at 24 degreeC. All Insuation material and adhesives shall be as per Class I for surface spread and in accordance with BS 476, Class O for non-combustible grade. | SITC of Glass Fibre Blanket Insulation material bonded with Thrmosetting Resin, with factory applied laminated aluminium foil of 22 micrns with fibre glass backing. Nominal density 48 Kg CuM. Thermal conductivity, < 0.033 W m.K at 24 degreeC. All Insuation material and adhesives shall be as per Class I for surface spread and in accordance with BS 476, Class O for non-combustible grade.
32 |  | 80 mm Thick | 80 mm Thick | sq.m | 40.000 | 38,000.00 | 950.00 | 38,000.00 | 950.00 | 38,000.00 | 1250.00 | 50,000.00
33 |  | ELECTRICAL INSTALLATION | ELECTRICAL INSTALLATION
34 |  | CONTROL PANEL FOR AHU Air washer Scrubber (WITH DOL SD STARTER) | CONTROL PANEL FOR AHU Air washer Scrubber (WITH DOL SD STARTER)
35 |  | Design, manufacture, supply, installation, testing and commissioning of the following cubicle type, dead front, sheet steel, wall mounted control panels including anchoring into the wall, wiring, incoming, earthing terminating into MCCB in each panel shall be provided by the electrical contractor. | Design, manufacture, supply, installation, testing and commissioning of the following cubicle type, dead front, sheet steel, wall mounted control panels including anchoring into the wall, wiring, incoming, earthing terminating into MCCB in each panel shall be provided by the electrical contractor.
36 |  | All internal wiring power cabling and copper earthing of air handling unit motors from the panel shall be included. | All internal wiring power cabling and copper earthing of air handling unit motors from the panel shall be included.
37 |  | All outgoing shall be provided with Stop Manual Auto selector switch to facilitate operation through BAS. All starters shall be provided with potential free Contact for Connections to Building Automation System. | All outgoing shall be provided with Stop Manual Auto selector switch to facilitate operation through BAS. All starters shall be provided with potential free Contact for Connections to Building Automation System.
38 |  | The panel shall include the following components and accessories. | The panel shall include the following components and accessories.
39 |  | MCCB as per the ratings given below, suitable for motor duty and able to withstand fault level of 20 KA. | MCCB as per the ratings given below, suitable for motor duty and able to withstand fault level of 20 KA.
40 |  | DOL SD starter as per HP ratings | DOL SD starter as per HP ratings
41 |  | Terminal block for power distribution. | Terminal block for power distribution.
42 |  | Contactor, over load relay with built in single phasing protection. | Contactor, over load relay with built in single phasing protection.
43 |  | Phase indicating lights and indicating light for ON status. | Phase indicating lights and indicating light for ON status.
44 |  | Digital voltmeter and digital ammeter with selector switches. | Digital voltmeter and digital ammeter with selector switches.
45 |  | Time delay relay for delayed automatic restart of air handling unit motor. | Time delay relay for delayed automatic restart of air handling unit motor.
46 |  | For on off remote and local operation, 3 pole single throw switch shall be provided in each AHU panel to facilitate override of the automatic operation. | For on off remote and local operation, 3 pole single throw switch shall be provided in each AHU panel to facilitate override of the automatic operation.
47 |  | All starters shall be provided with suitable potential free contract for connections to the Building Automation System. | All starters shall be provided with suitable potential free contract for connections to the Building Automation System.
48 |  | The number of AHU control panels shall be as follows. | The number of AHU control panels shall be as follows.
49 |  | 5 HP DOL Starter | 5 HP DOL Starter | No. | 1.000 | 22,000.00 | 22500.00 | 22,500.00 | 22000.00 | 22,000.00 | 25500.00 | 25,500.00
50 |  | 7.5 HP DOL Starter | 7.5 HP DOL Starter | No. | 1.000 | 22,000.00 | 22500.00 | 22,500.00 | 22000.00 | 22,000.00 | 32500.00 | 32,500.00

## Technical Score Detail
|  | RFQ No: R0235 COST COMPARISON REPORT | RFQ No: R0235 COST COMPARISON REPORT | RFQ No: R0235 COST COMPARISON REPORT | Comp. Date : 14/03/2024 | Comp. Date : 14/03/2024 | Comp. Date : 14/03/2024 | Vendor Name : PIONEER PROJECT SOLUTION |  | Vendor Name : COOL CARE ENTERPRISES |  | Vendor Name : ANJLE MEP PROJECT PVT LTD
|  | RFQ No: R0235 COST COMPARISON REPORT | RFQ No: R0235 COST COMPARISON REPORT | RFQ No: R0235 COST COMPARISON REPORT | RFQ #: R0235 | RFQ #: R0235 | RFQ #: R0235 | Contact Name : Mohd Ashraf/Rayyan Javed |  | Contact Name : Jasbir Singh |  | Contact Name :
|  | RFQ No: R0235 COST COMPARISON REPORT | RFQ No: R0235 COST COMPARISON REPORT | RFQ No: R0235 COST COMPARISON REPORT | RFQ Date : 11/03/2024 16:28:21 | RFQ Date : 11/03/2024 16:28:21 | RFQ Date : 11/03/2024 16:28:21 | Vendor City : |  | Vendor City : |  | Vendor City :
|  | RFQ No: R0235 COST COMPARISON REPORT | RFQ No: R0235 COST COMPARISON REPORT | RFQ No: R0235 COST COMPARISON REPORT | BCD Date : | BCD Date : | BCD Date : | Telephone # : |  | Telephone # : |  | Telephone # :
|  | RFQ No: R0235 COST COMPARISON REPORT | RFQ No: R0235 COST COMPARISON REPORT | RFQ No: R0235 COST COMPARISON REPORT |  |  |  | Mobile # : |  | Mobile # : |  | Mobile # :
PR Number : TFS-2324-00034 | PR Number : TFS-2324-00034 | PR Number : TFS-2324-00034 | PR Number : TFS-2324-00034 | PR Number : TFS-2324-00034 | PR Number : TFS-2324-00034 | PR Number : TFS-2324-00034 | PR Number : TFS-2324-00034 | Email : projectspioneer@gmail.com |  | Email : coolcareenterprises@gmail.com |  | Email : anjlemepprojects@gmail.com
Package / RFQ Name : TFAS / RFQ / TFS-2324-00034 | Package / RFQ Name : TFAS / RFQ / TFS-2324-00034 | Package / RFQ Name : TFAS / RFQ / TFS-2324-00034 | Package / RFQ Name : TFAS / RFQ / TFS-2324-00034 | Package / RFQ Name : TFAS / RFQ / TFS-2324-00034 | Package / RFQ Name : TFAS / RFQ / TFS-2324-00034 | Package / RFQ Name : TFAS / RFQ / TFS-2324-00034 | Package / RFQ Name : TFAS / RFQ / TFS-2324-00034 | Round # : 5 (Auction) |  | Round # : 5 (Auction) |  | Round # : 5 (Auction)
Buyer : Jogeswar Sahu | Buyer : Jogeswar Sahu | Buyer : Jogeswar Sahu | Buyer : Jogeswar Sahu | Buyer : Jogeswar Sahu | Buyer : Jogeswar Sahu | Buyer : Jogeswar Sahu | Buyer : Jogeswar Sahu | Quotation Date : |  | Quotation Date : |  | Quotation Date :
Comp. # : 5 | Comp. # : 5 | Comp. # : 5 | Comp. # : 5 | Comp. # : 5 | Currency :INR | Currency :INR | Currency :INR | Quotation Validity Date : |  | Quotation Validity Date : |  | Quotation Validity Date :
Comp. # : 5 | Comp. # : 5 | Comp. # : 5 | Comp. # : 5 | Comp. # : 5 | BUDGET PRICE : | .00 |  | Quote Currency : |  | Quote Currency : |  | Quote Currency :
# | Item Code | Item Description | Last PO Details | Unit | Qty | Last PO Unit Rate | Last PO Total Value | Score | Justification | Score | Justification | Score | Justification
1 |  | LOW SIDE -AIR SCURBBER & AIR WASHER WITH DUCTING FOR BAR . |  | LOT | 1.000 | 0.00 | 0.00
2 |  | AIR SCRUBBER |  |  | 0.000 | 0.00 | 0.00
3 |  | Modular Double skin Floor mounted air scrubber units made of 23+2mm thick PUF insulated panels extruded aluminum hollow profiles with 0.8mm thick pre-coated GI Outer Sheet 0.8mm thick Plain GI (270gsm) inner sheet comprising of Intake section for duct connection, Al Wiremesh filter section, Wet section made of 20g SS Tank, Three Phase Pump (1w+1s), GI internal piping, Single Bank Spray Nozzles and 2bend PVC eliminators. Blower section with DIDW Aerofoil Backward Forward curved fans, drive set with V- belts, Spring type vibration isolators, wire guard on Fan section access door, fire retardant canvass connection at fan outlet, IE-2 motor (TEFC type suitable for VFD operation) LED lamps for blower section, limit switch for the fan section access door with a view port and damper at the outlet of unit. All dampers shall be low leakage aluminum aerofoil design and suitable for manual motorised operation. Units exposed to open sky shall have weather proof canopy. The End Plates Casing blank offs of Eliminators shall also be made of SS. |  |  | 0.000 | 0.00 | 0.00
4 |  | 8400 CFM (65mm of wg Total St. Pressure) |  | No. | 1.000 | 0.00 | 0.00
5 |  | AIR WASHER |  |  | 0.000 | 0.00 | 0.00
6 |  | Modular Double skin Floor mounted air washer units made of 23+2mm thick PUF insulated panels extruded aluminum hollow profiles with 0.8mm thick pre-coated GI Outer Sheet 0.8mm thick Plain GI (270gsm) inner sheet comprising of Al Wiremesh filter section, Wet section made of 20g SS Tank, Single Phase Pump (1w+1s), PVC internal piping, Distribution system, 200mm deep Cellulose Pads 2 bend PVC eliminators. Blower section with DIDW Aerofoil Backward Forward curved fans, drive set with V- belts, Spring type vibration isolators, wire guard on Fan section access door, fire retardant canvass connection at fan outlet, IE-2 motor (TEFC type suitable for VFD operation) LED lamps for blower section, limit switch for the fan section access door with a view port and damper at the outlet of unit. All dampers shall be low leakage aluminum aerofoil design and suitable for manual motorised operation. Units exposed to open sky shall have weather proof canopy. The End Plates Casing blank offs of Pads Eliminators shall also be made of SS. |  |  | 0.000 | 0.00 | 0.00
7 |  | 7500 CFM (50mm of wg Total St. Pressure) |  | No. | 1.000 | 0.00 | 0.00
8 |  | Supplying, installing, testing and commissioning of INLINE FANS suitable for installing in any position in vertical or horizontal ducts. The casing shall be double skin, internally acoustically lined and constructed of galvanised steel. The fan shall be DIDW with forward curve impeller fitted with maintenance free external rotor motor. The motor shall be suitable for 220±10% volt single phase 50 cycles AC supply. All units shall be complete with duct flexible connector and volume control damper and static pressure or to suit the system, shall be as follows |  |  | 0.000 | 0.00 | 0.00
9 |  | Capacity 500 CFM Static Pressure 15 mmwg |  | No. | 1.000 | 0.00 | 0.00
10 |  | Capacity 1000 CFM Static Pressure 15 mmwg |  | No. | 1.000 | 0.00 | 0.00
11 |  | AIR DISTRIBUTION |  |  | 0.000 | 0.00 | 0.00
12 |  | (FOR FACTORY FABRICATED DUCTS AS PER “SMACNA” STANDARDS SPECIFICTIONS) |  |  | 0.000 | 0.00 | 0.00
13 |  | Supply, Fabrication, installation and testing of factory fabricated sheet metal ducts with sleeve joints and supports complete with the approved shop drawings and as required by the specifications and hanging of the ducts to be done by thread wire on metal cushion with gripple support. |  |  | 0.000 | 0.00 | 0.00
14 |  | 18 G sheet |  | sq.m | 35.000 | 0.00 | 0.00
15 |  | 20G sheet |  | sq.m | 5.000 | 0.00 | 0.00
16 |  | 22G sheet |  | sq.m | 5.000 | 0.00 | 0.00
17 |  | 24G sheet |  | sq.m | 50.000 | 0.00 | 0.00
18 |  | 26G sheet |  | sq.m | 35.000 | 0.00 | 0.00
19 |  | Supplying and erecting GI sheet of fabricated at site and mentioned guage to be used for fabrication of ducting complete with neoprene rubber garkets, elbows, splitter dampers, vanes, hangers, supports etc. as per approved drawings and specifications of following sheet thickness complete as required |  |  | 0.000 | 0.00 | 0.00
20 |  | 18 G sheet |  | sq.m | 5.000 | 0.00 | 0.00
21 |  | 20G sheet |  | sq.m | 5.000 | 0.00 | 0.00
22 |  | 22G sheet |  | sq.m | 5.000 | 0.00 | 0.00
23 |  | 24G sheet |  | sq.m | 5.000 | 0.00 | 0.00
24 |  | Supply, installation, testing and balancing of powder coated Extruded Aluminium Supply air Grilles with volume control dampers in accordance with the approved shop drawings and specifications. (Minimum Chargable area would be 0.1 Sqm Per Pc) |  | SQMT | 1.000 | 0.00 | 0.00
25 |  | Supplying fixing of opposed blade volume control dampers in supply air duct collars as per approved drawings and specifications. Volume control damper shall be provided at the junction of each branch duct with main duct. Dampers shall be 2 gauge heavier than the gauge of large duct but should not be less than 20 gauge, and shall be rigid in construction so as not to flutter with the passage of air. |  | SQMT | 1.000 | 0.00 | 0.00
26 |  | Supply, fabrication, installation and testing the flexible connections constructed of fire resistance flexible double canvas sleeve as per the approved shop drawings. |  | Nos. | 2.000 | 0.00 | 0.00
27 |  | Supply, installation, testing and balancing of Powder coated Anodised extruded aluminium construction exhaust air louvers with bird screen for exhaust air as per specifications and approved shop drawings. (Minimum Chargable area would be 0.1 Sqm Per Pc) |  | SQMT | 0.000 | 0.00 | 0.00
28 |  | Supply, installation, testing and balancing of Powder coated Anodised extruded aluminium construction. inlet air louvers with bird screen and volume damper for fresh air as per specifications and approved shop drawings. |  | SQMT | 0.000 | 0.00 | 0.00
29 |  | Supply, installation, testing and balancing of powder coated Extruded Aluminium exhaust air Grilles with volume control dampers in accordance with the approved shop drawings and specifications. (Minimum Chargable area would be 0.1 Sqm Per Pc) |  | SQMT | 2.000 | 0.00 | 0.00
30 |  | THERMAL INSULATION |  |  | 0.000 | 0.00 | 0.00
31 |  | THERMAL INSULATION FOR KITCHEN DUCTS |  |  | 0.000 | 0.00 | 0.00
32 |  | SITC of Glass Fibre Blanket Insulation material bonded with Thrmosetting Resin, with factory applied laminated aluminium foil of 22 micrns with fibre glass backing. Nominal density 48 Kg CuM. Thermal conductivity, < 0.033 W m.K at 24 degreeC. All Insuation material and adhesives shall be as per Class I for surface spread and in accordance with BS 476, Class O for non-combustible grade. |  |  | 0.000 | 0.00 | 0.00
33 |  | 80 mm Thick |  | sq.m | 40.000 | 0.00 | 0.00
34 |  | ELECTRICAL INSTALLATION |  |  | 0.000 | 0.00 | 0.00
35 |  | CONTROL PANEL FOR AHU Air washer Scrubber (WITH DOL SD STARTER) |  |  | 0.000 | 0.00 | 0.00
36 |  | Design, manufacture, supply, installation, testing and commissioning of the following cubicle type, dead front, sheet steel, wall mounted control panels including anchoring into the wall, wiring, incoming, earthing terminating into MCCB in each panel shall be provided by the electrical contractor. |  |  | 0.000 | 0.00 | 0.00
37 |  | All internal wiring power cabling and copper earthing of air handling unit motors from the panel shall be included. |  |  | 0.000 | 0.00 | 0.00
38 |  | All outgoing shall be provided with Stop Manual Auto selector switch to facilitate operation through BAS. All starters shall be provided with potential free Contact for Connections to Building Automation System. |  |  | 0.000 | 0.00 | 0.00
39 |  | The panel shall include the following components and accessories. |  |  | 0.000 | 0.00 | 0.00
40 |  | MCCB as per the ratings given below, suitable for motor duty and able to withstand fault level of 20 KA. |  |  | 0.000 | 0.00 | 0.00
41 |  | DOL SD starter as per HP ratings |  |  | 0.000 | 0.00 | 0.00
42 |  | Terminal block for power distribution. |  |  | 0.000 | 0.00 | 0.00
43 |  | Contactor, over load relay with built in single phasing protection. |  |  | 0.000 | 0.00 | 0.00
44 |  | Phase indicating lights and indicating light for ON status. |  |  | 0.000 | 0.00 | 0.00
45 |  | Digital voltmeter and digital ammeter with selector switches. |  |  | 0.000 | 0.00 | 0.00
46 |  | Time delay relay for delayed automatic restart of air handling unit motor. |  |  | 0.000 | 0.00 | 0.00
47 |  | For on off remote and local operation, 3 pole single throw switch shall be provided in each AHU panel to facilitate override of the automatic operation. |  |  | 0.000 | 0.00 | 0.00
48 |  | All starters shall be provided with suitable potential free contract for connections to the Building Automation System. |  |  | 0.000 | 0.00 | 0.00
49 |  | The number of AHU control panels shall be as follows. |  |  | 0.000 | 0.00 | 0.00
50 |  | 5 HP DOL Starter |  | No. | 1.000 | 0.00 | 0.00
51 |  | 7.5 HP DOL Starter |  | No. | 1.000 | 0.00 | 0.00